## Slide 1
Regulation Bias Analysis Post SCR-773
Dec 2019
ERCOT
Operations Planning
PDCWG | January 14th, 2020

## Slide 2
Discussion Points
Current GTBD Parameters & References
Metric to measure Regulation bias and performance
Regulation Deployed comparison for last three months.
Total Regulation (net) Deployed Comparison
Regulation Deployed 15-minute interval comparison by each hour for 2017, 2018, and 2019 months
Regulation Exhaustion Rate
Regulation bias for consecutive 5-min SCED intervals
Time Error & Contributing Factors
Summary

## Slide 3: Current GTBD Parameters
Notes: 3/12/18 – Integral ACE Time Constant Changed from 60 min to 45 min
5/17/18 - K4 Changed from 0.3 to 0.2 and K5 Changed from 0.4 to 0.5
12/4/18 - K6 Changed from 0 to 0.5
2/12/19 - K6 Changed from 0.5 to 1
4/01/19 - K5 changed from 0.5 to 0.4 and Max. Integral ACE Feedback changed from 250 to 150
4/24/19 - Max. Integral ACE Feedback changed from 150 to 160. PWRR Threshold changed from 20 to 25.
5/22/19 – K5 changed from 0.4 to 0.5 Max. Integral ACE Feedback changed from 160 to 200. PWRR Threshold changed from 25 to 30.

## Slide 4: Projected Wind Ramp Rate MAE

## Slide 5: Projected Wind Ramp Rate Error

## Slide 6: References
 | Hours |  |  |  | 
 |  | Dec-17 | Dec-18 | Dec-19 | 
 | Peak | 10, 11, 18, 19, 20, 21 | 9, 10, 11, 18, 19, 20 | 8, 9, 10, 11, 18, 19 | 
 | Off-Peak | 1, 2, 3, 4, 5, 6 | 1, 2, 3, 4, 5, 24 | 1, 2, 3, 4, 5, 24 | 
 | Up-Ramp | 5, 6, 7, 9, 17, 18 | 5, 6, 7, 8, 17, 18 | 4, 5, 6, 7, 17, 18 | 
 | Down-Ramp | 1, 20, 21, 22, 23, 24 | 1, 12, 21, 22, 23, 24 | 12, 20, 21, 22, 23, 24 | 

## Slide 7
Metrics to Measure SCR-773 Performance
Trend and monitor the regulation deployed by hour.
Set target of 50 MW for total regulation deployed by hour for peak hours.
Set target of 85% for the number of intervals where regulation deployment was both up and down for peak hours.
Track the Regulation exhaustion rate for all hours (not to exceed 5%).
Using a 50MW filter, target 15 occurrences or less per month for regulation bias of six or more consecutive 5 minute intervals for peak hours.

## Slide 8: Total Regulation Deployed Comparison
Total regulation deployed for the last three months.

## Slide 9: Total Regulation Deployed Comparison - Monthly

## Slide 10: Metric 1: Regulation Deployed Comparisons
Trend and monitor the regulation deployed by hour.

## Slide 11: Regulation Deployed Comparison
 | Regulation Performance |  |  |  |  | 
 |  |  | Dec-17 | Dec-18 | Dec-19 | 
 | All | REGUP | 51 | 43 | 46 | 
 |  | REGDN | 60 | 62 | 61 | 
 |  | TOTAL | -10 | -19 | -14 | 
 | Peak | REGUP | 52 | 42 | 53 | 
 |  | REGDN | 64 | 67 | 73 | 
 |  | TOTAL | -12 | -25 | -20 | 
 | Off-Peak | REGUP | 52 | 40 | 38 | 
 |  | REGDN | 52 | 55 | 52 | 
 |  | TOTAL | 0 | -15 | -14 | 
 | Up-Ramp | REGUP | 86 | 67 | 86 | 
 |  | REGDN | 45 | 55 | 37 | 
 |  | TOTAL | 41 | 12 | 48 | 
 | Down-Ramp | REGUP | 36 | 34 | 28 | 
 |  | REGDN | 73 | 75 | 70 | 
 |  | TOTAL | -37 | -41 | -42 | 

## Slide 12: Regulation Deployed Comparison

## Slide 13: Regulation Deployed Comparison

## Slide 14: Metric 2: Total Regulation Deployed Comparisons
Set target of 50MW for total regulation deployed by hour for peak hours.

## Slide 15: Total Regulation Deployed Comparison

## Slide 16: Metric 3: 15-min Intervals Where Both REGUP/REGDN Were Deployed
Set target of 85% for the number of intervals where regulation deployment was both up and down.

## Slide 17: “Zero” Crossing Regulation
 | Zero-Crossing Regulation |  |  |  | 
 | HE | Dec-17 | Dec-18 | Dec-19 | 
 | 1 | 78.23% | 78.23% | 89.52% | 
 | 2 | 75.81% | 84.68% | 88.71% | 
 | 3 | 75.81% | 82.26% | 89.52% | 
 | 4 | 86.29% | 77.42% | 91.94% | 
 | 5 | 75.81% | 82.26% | 91.94% | 
 | 6 | 75.00% | 80.65% | 83.87% | 
 | 7 | 66.13% | 79.84% | 87.90% | 
 | 8 | 78.23% | 79.84% | 78.23% | 
 | 9 | 69.35% | 75.81% | 66.94% | 
 | 10 | 78.23% | 67.74% | 80.65% | 
 | 11 | 63.71% | 70.97% | 75.00% | 
 | 12 | 62.90% | 78.23% | 83.06% | 
 | 13 | 63.71% | 81.45% | 89.52% | 
 | 14 | 74.19% | 85.48% | 85.48% | 
 | 15 | 70.16% | 79.84% | 91.94% | 
 | 16 | 75.00% | 82.11% | 85.48% | 
 | 17 | 60.48% | 79.03% | 67.74% | 
 | 18 | 68.55% | 76.61% | 62.90% | 
 | 19 | 56.45% | 62.90% | 67.74% | 
 | 20 | 71.77% | 82.26% | 78.23% | 
 | 21 | 72.58% | 75.00% | 90.32% | 
 | 22 | 71.77% | 75.00% | 85.48% | 
 | 23 | 79.84% | 79.84% | 87.90% | 
 | 24 | 78.23% | 81.45% | 83.87% | 

## Slide 18: “Zero” Crossing Regulation
 |  | Dec-17 | Dec-18 | Dec-19 | 
 | All | 72.01% | 78.29% | 82.66% | 
 | Peak | 68.55% | 72.72% | 71.91% | 
 | Off-Peak | 77.82% | 81.05% | 89.25% | 
 | Up-Ramp | 69.22% | 79.70% | 81.05% | 
 | Down-Ramp | 75.40% | 77.96% | 84.81% | 

## Slide 19: Metric 4: Regulation Exhaustion Rate
Track the regulation exhaustion rate for all hours (not to exceed 5%.)

## Slide 20: Regulation Exhaustion Rate
Regulation-Up |  |  | 
 | Dec-17 | Dec-18 | Dec-19
All Hours Average | 3.09% | 2.96% | 2.13%

## Slide 21: Regulation Exhaustion Rate
Regulation-Down |  |  | 
 | Dec-17 | Dec-18 | Dec-19
All Hours Average | 4.40% | 4.41% | 3.64%

## Slide 22: Metric 5: Stats on REGUP Bias for Consecutive 5-min Intervals
Using a 50MW filter, target 15 occurrences or less per month for regulation bias of six or more consecutive 5-minute intervals for peak hours.

## Slide 23: Regulation Bias for Consecutive SCED Intervals
Regulation-Up |  |  | 
 | Dec-17 | Dec-18 | Dec-19
All | 111 | 65 | 61
Peak | 27 | 25 | 28

## Slide 24: Regulation Bias for Consecutive SCED Intervals
Regulation-Down |  |  | 
 | Dec-17 | Dec-18 | Dec-19
All | 128 | 123 | 91
Peak | 39 | 37 | 41

## Slide 25: Time Error and Contributing Factors
Accumulated Time Error, Load and Wind Ramp, PWRR Error, Start-Up/Shut-Down Hours, STLF Error, and Expected Generation Deviation.

## Slide 26: Time Error Accumulation

## Slide 27: Load Profile

## Slide 28: Net Load Profile

## Slide 29: Load Ramp

## Slide 30: Wind Profile

## Slide 31: Start-Up & Shut-Down Hours

## Slide 32: Short-Term Load Forecast Error

## Slide 33: STLF Error Chart
Notes: Min,Max, 10th, 90th percentile
15 minute intervals

## Slide 34: Expected Generation Deviation

## Slide 35: Expected Generation Deviation

## Slide 36: Expected Generation Deviation

## Slide 37: Questions?
Thank you!