## Sheet1
TDSP comments |  | ERCOT Comments
1 | Clarify DSP authority to require DGR to follow DSP voltage requirements | agreed
2 | Clarify language on outage notifications. | agreed
| a. There are no notification timelines specified, either for the DSP notification to the DGR, or for the DGR notification to ERCOT. Is this preferred? | tbd
| b. Will the DSP be responsible for notifying the DGR directly for any planned transmission outages that affect the DGR (vs normal entry into the ERCOT Outage Scheduler only)? | not anticipated.
| c. ERCOT’s Nov 5 workshop slide 7 states the DSP must notify the Resource Entity for the DGR. Should the DSP be notifying the DGR’s QSE? | agreed
3 | Confirm reconfiguring feeder notifications are not required if path is not impacted for DGR | agreed
a. Normal construction for new customers may only affect a portion of load on the feeder and not the DGR itself (i.e., construction is not altering the electrical path to the DGR).
b. We support ERCOT’s proposed Protocol 3.8.7(3) in which reconfiguration of a feeder altering the electrical path to the DGR would only be subject to notification if the reconfiguration will be more than 60 days in duration.
4 | Support idea of PGRR for process
| a. ERCOT should define the minimum requirements the DGR must meet for the process to begin, a defined set (with some initial flexibility) of DSP-performed studies, and defined timelines. | To be discussed at 12/11 meeting
| b. There is a learning curve (planning and operational) involved with DGRs; study requirements are going to evolve and improve over time. DSPs may potentially add studies that are not contemplated now, or may waive studies that are not needed. | noted
| c. It would be useful for ERCOT to require the DGR to specify which types of AS it will provide, so this can be considered in the DSP studies. Some types of AS may have more significant impacts on the distribution system (e.g., FRRS) and therefore require more extensive studies, while other types of AS may have a lesser impact and are less study-intensive. | To be discussed at 12/11 meeting
| d. If the DGR elects to provide additional types of AS, it must notify ERCOT and the DSP, either of which may require additional studies prior to the DGR offering the new AS. | To be discussed at 12/11 meeting
| e Planning for the long term risks and benefits of DGR and their cumulative impacts on the utility system needs to be incorporated into ERCOT Protocols and Guides, and TDSP procedures. | ERCOT acknowledges this may be a future need.
I Example: Transmission contingencies that cause DGR to react, or other conditions that require technical studies and coordination across the T&D boundary.
5 | ERCOT system doesn’t include Distribution will need to add in that if we intend to include it.
| a. Protocol Section 2 definition: “The interconnected power system that is under the jurisdiction of the PUCT and that is not synchronously interconnected with either the Eastern Interconnection or the Western Electricity Coordinating Council.” | To be discussed at 12/11 meeting
| b. Where the word “transmission” before the term “ERCOT system” was struck in ERCOT’s proposed Protocol changes for DGR (for example, 3.10.7.2(1)), we suggest the following: “ERCOT system or the distribution system”. | To be discussed at 12/11 meeting
6 | Protocol 3.10.7.2(3), at the end of the long first sentence “Each Resource Entity representing a Distribution Generation Resource…and any additional information and telemetry as required by ERCOT,” please add “and the interconnecting DSP”. | agreed
7 | If the desired completion of the protocol changes is summer/fall 2020 and the expected certifications for UL 1741-2020 will not be available until fall 2020 or winter 2020/2021, who is liable for any failed operation during the time the DGR is not certified to operate in the stated ranges of voltage and frequency set points? | ERCOTs understanding is the owner of the equipment is liable.
b. Although the DSP may be able to test for DGR functionality in the stated ranges, this should not be taken as a certification in any way that a DGR will always operate as desired in the tested range.
8 | It is understood that the desire is to have a DGR remain off any load shed feeders for the lifetime of a project. | may need to be addressed in a future NPRR
| a. Does this also include Remedial Action Schemes for transmission lines? | may need to be addressed in a future NOGRR
| b. If a DGR is temporarily moved to another feeder, does the alternate feeder (attached to the same bus) have to be a non-load shed feeder for the DGR to remain in operation | agreed
Example: Feeder breaker maintenance
We propose the DGR should be allowed to be moved to a load shed feeder if it resides there for less than 30 days.
c. Long term, if DGRs proliferate it will be impractical to completely prohibit them from residing on load shed feeders. If a DGR connects to a feeder that becomes a load shed feeder in the future, the DSP would notify the DGR, and it can become SODG.
| d. Impacts to load shed considerations needs further vetting, not only due to the anticipated proliferation of DGRs but what are considered as critical loads may also need to be reviewed. | may need to be addressed in a future NPRR
9 | We propose that ERCOT establish a minimum size for DGRs of 2MW. | ERCOT proposes 1 MW threshold and there is at least 1 project submittal for less than 2 MW
TDSP comments 1/06/2020
10 | Suggest removing reference to Open Access in business case since that is a Transmission level concept.
11 | Business case referencing July 2019 seems outdated | agreed
12 | Clarify that a facility cannot be both DGR and DESR? | No, Resource must be either DGR or DESR not both
13 | Proposes a 10 MW upper threshold for DGR | ERCOT does not have justification to limit the upper size of a DGR
14 | Clarification for language change for "Resource Node" | General cleanup since the Resource Nodes are assigned per new OBD.
15 | In the event of conflicting emergencies, the DSP should have default operating priority over Load shed/disconnecting DGR. | agreed
16 | Clarify Load Shed terminology | agreed
17 | Review of Frequency Trip settings still in progress. Should Frequency Trip settings be modified in addition to VRT. | to be discussed
TAEBA comments
1 | While ERCOT’s commitment to work efficiently and quickly on the issues raised by the DGR Market Notice is helpful, it still leaves prospective DGR installers, owners, and operators without the certainty they need to make business decisions. | agreed
2 | We therefore agree with ERCOT’s proposal to continue to work through these issues through workshops to allow for a more nimble, accelerated process, and we further encourage ERCOT to explore ways to expedite the development and approval of the relevant Nodal Protocol Revision Request (NPRR), Planning Guide Revision Request (PGRR), and Nodal Operating Guide Revision Request (NOGRR).
KCE Comments
1 | AVR needs to be coordinated with DSP
2 | Given that it is infeasible for KCE to achieve the proposed VRT requirements, and inverters that can do so are not yet commercially-available, KCE respectfully recommends that ERCOT pursue one of the following options: | ERCOT proposes revised settings that commercially available equipment can meet.
| a. Grandfather in DGR projects installed prior to the commercial availability of inverters that can meet the proposed VRT requirements by allowing such projects to meet the current VRT requirements of NERC PRC-024-2; or | waiting on proposed language from MKT.
b. Revise the proposed UV1 Minimum Ride-Through time down from 21 seconds to five seconds (in conformance with the current VRT requirements of NERC PRC-024-2.)
| Notwithstanding the foregoing, a DGR utilizing inverter-based generation that is not physically or technically capable of complying with the VRT requirements presented in this Section may apply for an exemption prior to [date of NPRR approval] and upon receiving ERCOT approval shall not be required to meet the VRT requirements presented in this Section. | Would like to review proposed approach on grandfathering
Shell comments
1 | Clarify the registration requirements for >1MW and <10 MW. | agreed
GlidePath Comments
1 | AVR needs to be coordinated with DSP | agreed
2 | GlidePath also feels that inverters that can meet the proposed ride-through requirements are not yet commercially-available, so GlidePath respectfully recommends that ERCOT pursue one of the following options: | ERCOT proposes revised settings that commercially available equipment can meet.
a. Grandfather in DGR projects installed prior to the commercial availability of inverters that can meet the proposed VRT requirements by allowing such projects to meet the current VRT requirements; or
b. Revise the proposed UV1 Minimum Ride-Through time down from 21 seconds to five seconds (in conformance with the current VRT requirements.)
| c. GlidePath also requests waiving VRT requirements if it would result in distribution upgrades or If DSP refuses to comply | Required to qualify as DGR
3 | DSP outage notifications in NPRR 3.1.6.13 does not adequately protect the DGR from the potential of improper notification so GlidePath proposes the following additions: | This should be part of the DSP-DGR/RE agreement. Not an ERCOT issue
a. DSP outage notifications need to mirror TSP obligations to transmission connected Resources.
b. If DSP outage notifications is not communicated in a timely manner, the DGR should be relieved of DAM oblications and the DSP should be penalized.
c. GlidePath also suggests rewording proposed language to "A DSP must notify the Resource Entity for a DGR if the DSP intends to take an outage on any distribution facility that will materially impact the operation of a DGR and indicate the impact the outage is expected to have on the operation of the DGR. The Resource Entity for the DGR shall adjust their market offers or bidding parameters or submit a Planned or Maintenance Resource Outage, as appropriate, to reflect the unavailability of the Resource due to the DSP outage.”
ERCOT agrees and language either has been or needs to be revised to reflect (if necessary)
Either further clarification is needed, or ERCOT disagrees - Item needs to be resolved.
A comment or observation. There don’t seem to be any language changes needed to be resolved, but may require future action