## Slide 1
Meter Working Group
February 12, 2020

## Slide 2: Anti-Trust Admonition
  Antitrust Admonition
  To avoid raising concerns about antitrust liability, participants in ERCOT activities should refrain from proposing any action or measure that would exceed ERCOT’s authority under federal or state law. For additional information, stakeholders should consult the Statement of Position on Antitrust Issues for Members of ERCOT Committees, Subcommittees, and Working Groups, which is posted on the ERCOT website. http://www.ercot.com/about/governance/index.html
Disclaimer
All presentations and materials submitted by Market Participants or any other Entity to ERCOT staff for this meeting are received and posted with the acknowledgement that the information will
be considered public in accordance with the ERCOT Websites Content Management Operating Procedure.

## Slide 3: Attendance Roll-call and Introductions
  Brief introduction of those present and those participating via WebEx

## Slide 4: Selection of Chair/Vice-chair
  Selection of MWG Chair and Vice-Chair for the next year

## Slide 5: Point of Interconnection Discussion Update
ERCOT NPRR to clarify Point of Interconnection (POI) is in the final internal review stage
POI as used in Protocols
  Creates uncertainty and ambiguity in regards to the location of the POI
  Uses one term to define separate and distinct points of measurement
    EPS Meter location for energy settlement
    Telemetry location for generator performance

## Slide 6: Point of Interconnection Defined
NPRR proposes changing the definition of POI
  From: The voltage level and substation where a Generation Entity’s interconnection Facilities connect to the Transmission Facilities as reflected in the Standard Generation Interconnection Agreement (SGIA) between a Generation Entity and a Transmission Service Provider (TSP) or the voltage level and substation where Load interconnects to the TSP Facilities.
  To: Any physical location where a Generation Entity’s Facilities electrically connect to the Transmission Service Provider’s (TSP’s) Facilities.

## Slide 7: Point of Interconnection Bus
NPRR proposes creation of a new defined term - Point of Interconnection Bus (POIB)
  For each TSP substation to which a Generation Resource interconnects, the Electrical Bus at that substation that is electrically closest to the Generation Resource’s POI, or any electrically equivalent Electrical Bus in that substation.

## Slide 8: Line Loss Compensation Survey Results
  9 TDSPs out of 22 provided a response (40.9%)
  5 of the responses stated that their company did not use line loss and therefore elected to not provide a recommendation
  Some responses included multiple options, all options are included below
    2 responses supported the concept of not programming line loss when there would be no observable impact to meter testing.
      Previous ERCOT calculation of % Watt Cu less than 0.001% to not be observed on meter test report when using 5 test amps. (see key document Line Loss Compensation References Item A)
    1 response recommended only programming when % Watt Cu was 0.05% or greater (see key document Line Loss Compensation References Item B)
    1 response recommended creating a reference table of line types, voltages and length which would indicate when loss compensation was required
    1 response recommended programming for line loss to prevent exceeding a maximum metering error of 0.47% (see key document Line Loss Compensation References Item C)
    1 response recommended programming for line loss only when the distance exceeds 600 yards (see key document Line Loss Compensation References Item D)
    1 response recommend keeping the current protocol where any difference from the POI should be calculated and compensated (see key document Line Loss Compensation References Item E)

## Slide 9: Line Loss Compensation Discussion
What path forward should be taken by the Meter Working Group?

## Slide 10: Throw Over Scheme Discussion
Possible permutations for Throw Over schemes are numerous dependent on substation design
There are two basic design schemes currently in use for VT throw overs:
  Method 1: Both primary and backup meter are always powered from the same VTs
  Method 2: Primary and backup meter are normally powered from alternate VTs
Abnormal grid configurations are more likely to result in metering errors when method 1 is utilized
Should the meter working group pursue language minimize the chance of metering errors?
NUMBER OF TDSPs UTILIZING THROW-OVER SCHEME | 11
NUMBER OF SITES WITH THROW-OVER SCHEMES | 44
NUMBER OF EPS METER POINTS | 120
% IN COMPARISON TO TOTAL SITES | Less than 10% (9.3%)
VOLTAGE LEVEL INSTALLED | 69 kV, 138 kV, 345 kV
SUBSTATION BUS SCHEMES | Breaker-and-a-Half; Double-Breaker

## Slide 11: Instrument Transformer Nameplate Requirements
Review draft language (key document 8)
  As presented at the Aug 2019 meeting

## Slide 12: Isolatable Voltage Transformers
Issue identified over the last year across more than one TDSP
Configurations where the voltage transformer can be de-energized while there is still current flow through the CT.
  Observed when there are switches/breakers between the CT and VT
  Line being metered has >1 flow path inside substation with the CTs on the line and the VTs not co-located.

## Slide 13: Reports on EPS Activities
See key document 10, Reports on EPS meter activities Feb2020

## Slide 14: Changes in EPS database
Recent deployment of EPS database enhancements will result in some notable changes to TDSPs.
  Follow-up emails requests for certification and test documents will include a follow up number at the end of the subject line, i.e. “3rd follow up”
  Process 000 changes include:
    Site Name will now be listed on all notifications
    Open 6-hour and 12-hour notices will now include a note to notify TDSP if one of the two meters had read. The note will indicate which meter read and will be updated daily until the notice is closed.
    A 12-hour notice that is becoming a 6-hour notice will have conversion emails sent, i.e. “12-hour Conversion Cancellation” will be different than normal Cancellations.

## Slide 15: NPRR949 Implementation
  As a reminder, NPRR949 was approved 8/13/2019. Protocol 10.12.1 will be updated effective 1/1/2023. See updated language below.
[NPRR949: Replace Section 10.12.1 above with the following on January 1, 2023:] 10.12.1 ERCOT Acquisition of ERCOT-Polled Settlement (EPS) Meter Data (1) ERCOT shall acquire ERCOT-Polled Settlement (EPS) Meter data via the following communication links: (a) ERCOT private communication network established by ERCOT for ERCOT Real-Time metered Entities; or (b) Other ERCOT-approved communication technology provided by the Transmission Service Provider (TSP) or Distribution Service Provider (DSP).
10.12.1 ERCOT Acquisition of Meter Data
(1) ERCOT shall acquire meter data via the following communication links:
(a) ERCOT private communication network established by ERCOT for ERCOT Real-Time metered Entities; and
(b) Standard voice telephone circuit or other ERCOT-approved communication technology provided by the Transmission Service Provider (TSP) or Distribution Service Provider (DSP) for ERCOT-Polled Settlement (EPS) Meters.

## Slide 16: New or Other Business Items
  Request for any new or other business items

## Slide 17: Meeting Summary and Closing Remarks
  Thank you for your attendance and participation
  Notes from this meeting will be posted on the ERCOT website under the key documents for this meeting.
    http://www.ercot.com/calendar/2020/2/12/196908-MWG