## Slide 1
ERCOT Frequency Control Report
January 2020
ERCOT
Operations Planning
PDCWG | February 12th, 2020

## Slide 2: Summary of January 2020
CPS1: 174.68%
Current CPS1 12-Month Rolling Average: 174.83%
4 BAAL Exceedances
1 hourly CPS1 score below 100%
BAAL-003 Events have updated through 2019
2018 BAAL-003 FRM Performance: -843.17
2020 RMS1 Statistics
  Mean: 15.07 mHz
  Min: 13.56 mHz
  Max: 16.6 mHz
Energy Statistics
  Total Energy: 28,969,595 MWh
  Wind Energy: 7,474,690 MWh
  Percent Energy from Wind: 25.80%
  Solar Energy: 336,423 MWh
  Percent Energy from Solar: 1.16%
Minimum System Inertia
  Mean: 183,800
  Max: 244,162 on Jan 30th
  Min: 143,088 on Jan 9th

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
Jan-20 CPS1 (%): 174.68
Notes: Outliers:
1/11/2020 10:00 61.2%:
Large deviation generation from wind, significant ramp down during the hour ~54MW/min

## Slide 5: BAAL Exceedances & Violations
There were 4 BAAL exceedances in Jan
Notes: BAAL Exceedances related to the two FMEs on 1/1/2020 and 1/17/2020

## Slide 6: 15-Minute Average CPS1%
Jan-20 CPS1 (%): 174.68

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 174.83%

## Slide 8: Daily RMS1 of ERCOT Frequency by Year
Notes:   Mean: 15.00 mHz

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month
Notes: Mean: 15.07 mHz
Min: 13.6 mHz
Max: 16.6 mHz

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2018 BAL-003 Selected Events – Update
Notes: BAL-003

## Slide 19: Op. Year 2018 BAL-003 FRM Performance - Update
Notes: OP2018: FRO = -381.0, FRM_median = -843.17, FRM_average = -959.7
OP2019: FRO = -381.0
OP2020: FRO = -425.0, FRM_median = -811.14, FRM_average = -892.5

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 28,969,595 MWh

## Slide 22: Total Energy from Wind Generation
Notes: 7,474,690 MWh

## Slide 23: % Energy from Wind Generation
Notes: 25.80%

## Slide 24: Total Energy From Solar Generation
Notes: 336,423 MWh

## Slide 25: % Energy from Solar Generation
Notes: 1.16%
- Less overall Load compared to last 3 years

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia = 143,088 MW*s on 1/9/2020
Previous Minimum was 128,759 MW*s on 11/18/2018.
Data:
Mean: 183,800
Max: 244,162 on Jan 30th
Min: 143,088 on Jan 9th

## Slide 28: Questions?
Thank you!