## Slide 1
Regulation Bias Analysis Post SCR-773
Jan 2020
ERCOT
Operations Planning
PDCWG | February 12th, 2020

## Slide 2
Discussion Points
Current GTBD Parameters & References
Metric to measure Regulation bias and performance
Regulation Deployed comparison for last three months.
Total Regulation (net) Deployed Comparison
Regulation Deployed 15-minute interval comparison by each hour for 2017, 2018, and 2019 months
Regulation Exhaustion Rate
Regulation bias for consecutive 5-min SCED intervals
Time Error & Contributing Factors
Summary

## Slide 3: Current GTBD Parameters
Notes: 3/12/18 – Integral ACE Time Constant Changed from 60 min to 45 min
5/17/18 - K4 Changed from 0.3 to 0.2 and K5 Changed from 0.4 to 0.5
12/4/18 - K6 Changed from 0 to 0.5
2/12/19 - K6 Changed from 0.5 to 1
4/01/19 - K5 changed from 0.5 to 0.4 and Max. Integral ACE Feedback changed from 250 to 150
4/24/19 - Max. Integral ACE Feedback changed from 150 to 160. PWRR Threshold changed from 20 to 25.
5/22/19 – K5 changed from 0.4 to 0.5 Max. Integral ACE Feedback changed from 160 to 200. PWRR Threshold changed from 25 to 30.

## Slide 4: Projected Wind Ramp Rate MAE

## Slide 5: Projected Wind Ramp Rate Error

## Slide 6: References
 | Hours |  |  |  | 
 |  | Jan-18 | Jan-19 | Jan-20 | 
 | Peak | 8, 9, 10, 18, 19, 20 | 8, 9, 10, 18, 19, 20 | 8, 9, 10, 18, 19, 20 | 
 | Off-Peak | 1, 2, 3, 4, 5, 24 | 1, 2, 3, 4, 5, 24 | 1, 2, 3, 4, 5, 24 | 
 | Up-Ramp | 4, 5, 6, 7, 17, 18 | 4, 5, 6, 7, 17, 18 | 4, 5, 6, 7, 17, 18 | 
 | Down-Ramp | 11, 20, 21, 22, 23, 24 | 11, 20, 21, 22, 23, 24 | 11, 20, 21, 22, 23, 24 | 

## Slide 7
Metrics to Measure SCR-773 Performance
Trend and monitor the regulation deployed by hour.
Set target of 50 MW for total regulation deployed by hour for peak hours.
Set target of 85% for the number of intervals where regulation deployment was both up and down for peak hours.
Track the Regulation exhaustion rate for all hours (not to exceed 5%).
Using a 50MW filter, target 15 occurrences or less per month for regulation bias of six or more consecutive 5 minute intervals for peak hours.

## Slide 8: Total Regulation Deployed Comparison
Total regulation deployed for the last three months.

## Slide 9: Total Regulation Deployed Comparison - Monthly

## Slide 10: Metric 1: Regulation Deployed Comparisons
Trend and monitor the regulation deployed by hour.

## Slide 11: Regulation Deployed Comparison

## Slide 12: Regulation Deployed Comparison

## Slide 13: Regulation Deployed Comparison

## Slide 14: Metric 2: Total Regulation Deployed Comparisons
Set target of 50MW for total regulation deployed by hour for peak hours.

## Slide 15: Total Regulation Deployed Comparison

## Slide 16: Metric 3: 15-min Intervals Where Both REGUP/REGDN Were Deployed
Set target of 85% for the number of intervals where regulation deployment was both up and down.

## Slide 17: “Zero” Crossing Regulation
 | Zero-Crossing Regulation |  |  |  | 
 | HE | Jan-18 | Jan-19 | Jan-20 | 
 | 1 | 75.81% | 79.03% | 86.29% | 
 | 2 | 72.58% | 77.42% | 80.65% | 
 | 3 | 75.81% | 75.00% | 81.45% | 
 | 4 | 74.19% | 82.26% | 88.71% | 
 | 5 | 74.19% | 81.45% | 91.13% | 
 | 6 | 66.94% | 84.68% | 87.90% | 
 | 7 | 83.87% | 87.10% | 87.90% | 
 | 8 | 70.97% | 75.00% | 81.45% | 
 | 9 | 57.26% | 68.55% | 83.06% | 
 | 10 | 72.58% | 74.19% | 79.03% | 
 | 11 | 65.32% | 74.19% | 76.61% | 
 | 12 | 74.19% | 76.61% | 85.48% | 
 | 13 | 71.77% | 79.03% | 83.87% | 
 | 14 | 64.52% | 71.77% | 83.06% | 
 | 15 | 71.77% | 74.19% | 87.10% | 
 | 16 | 73.39% | 87.90% | 87.90% | 
 | 17 | 72.58% | 85.48% | 84.68% | 
 | 18 | 58.06% | 64.52% | 70.97% | 
 | 19 | 45.97% | 65.32% | 70.16% | 
 | 20 | 54.03% | 66.13% | 80.65% | 
 | 21 | 76.61% | 86.29% | 78.23% | 
 | 22 | 73.39% | 78.23% | 85.48% | 
 | 23 | 78.23% | 83.06% | 83.87% | 
 | 24 | 83.87% | 92.74% | 89.52% | 

## Slide 18: “Zero” Crossing Regulation
 |  | Jan-18 | Jan-19 | Jan-20 | 
 | All | 70.33% | 77.92% | 83.13% | 
 | Peak | 65.99% | 70.56% | 77.55% | 
 | Off-Peak | 76.08% | 81.32% | 86.29% | 
 | Up-Ramp | 71.64% | 80.91% | 85.22% | 
 | Down-Ramp | 74.46% | 80.65% | 82.39% | 

## Slide 19: Metric 4: Regulation Exhaustion Rate
Track the regulation exhaustion rate for all hours (not to exceed 5%.)

## Slide 20: Regulation Exhaustion Rate
Regulation-Up |  |  | 
 | Jan-18 | Jan-19 | Jan-20
All Hours Average | 2.88% | 2.31% | 2.24%

## Slide 21: Regulation Exhaustion Rate
Regulation-Down |  |  | 
 | Jan-18 | Jan-19 | Jan-20
All Hours Average | 4.42% | 4.07% | 4.54%

## Slide 22: Metric 5: Stats on REGUP Bias for Consecutive 5-min Intervals
Using a 50MW filter, target 15 occurrences or less per month for regulation bias of six or more consecutive 5-minute intervals for peak hours.

## Slide 23: Regulation Bias for Consecutive SCED Intervals
Regulation-Up |  |  | 
 | Jan-18 | Jan-19 | Jan-20
All | 98 | 60 | 55
Peak | 30 | 17 | 30

## Slide 24: Regulation Bias for Consecutive SCED Intervals
Regulation-Down |  |  | 
 | Jan-18 | Jan-19 | Jan-20
All | 126 | 113 | 99
Peak | 33 | 42 | 30

## Slide 25: Time Error and Contributing Factors
Accumulated Time Error, Load and Wind Ramp, PWRR Error, Start-Up/Shut-Down Hours, STLF Error, and Expected Generation Deviation.

## Slide 26: Time Error Accumulation

## Slide 27: Load Profile

## Slide 28: Net Load Profile

## Slide 29: Load Ramp

## Slide 30: Wind Profile

## Slide 31: Start-Up & Shut-Down Hours

## Slide 32: Short-Term Load Forecast Error

## Slide 33: STLF Error Chart
Notes: Min,Max, 10th, 90th percentile
15 minute intervals

## Slide 34: Expected Generation Deviation
Expected Generation Deviation |  |  | 
 | Jan-18 | Jan-19 | Jan-20
All Hours Average | -23.83 | -11.75 | -18.90

## Slide 35: Expected Generation Deviation

## Slide 36: Expected Generation Deviation

## Slide 37: Questions?
Thank you!