## Slide 1
PDCWG Report to ROS
Chair: Chad Mulholland, NRG
Vice Chair: Jimmy Jackson, CPS
ROS
March 5th, 2020

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
  BAL-001-TRE-1 FMEs & IMFR
    3 FMEs in the month of January
  Frequency Control Report

## Slide 3: Meeting Minutes
PDCWG Meeting 2/12/2020
  NPRR 863 and 960 Phase 1 Implementation Details (FFR)
    Review of ERCOT Webex from January
    NPRR 863 takes effect March 1, 2020
  Battery & Energy Storage Integration
    Discussed NOGRR 204, NPRR 989, and NPRR 987
  Regulation & Frequency Control Reports

## Slide 4: Frequency Measurable Events Performance

## Slide 5: Frequency Measurable Events
There were 3 FMEs in December
  1/1/2020 12:53:12
    Loss of 1,210 MW
    Interconnection Frequency Response: 1,169 MW/0.1 Hz
    7 of 41 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    6 of 41 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 6: Frequency Measurable Events
  1/10/2020 20:54:10
    Loss of 773 MW
    Interconnection Frequency Response: 1,247 MW/0.1 Hz
    12 of 63 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    11 of 63 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.
  1/17/2020 10:01:06
    Loss of 663 MW
    Interconnection Frequency Response: 539 MW/0.1 Hz
    5 of 24 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    4 of 24 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 7: Interconnection Minimum Frequency Response (IMFR) Performance
IMFR Performance currently 939.60 MW/0.1Hz
Frequency Response Obligation (FRO): 425 MW/0.1 Hz

## Slide 8: Frequency Control Report
November 2019

## Slide 9: CPS1 Performance

## Slide 10: RMS1 Performance of ERCOT Frequency

## Slide 11: Frequency Profile Analysis

## Slide 12: Time Error Corrections

## Slide 13: ERCOT Total Energy

## Slide 14: ERCOT Total Energy from Wind Generation

## Slide 15: ERCOT % Energy from Wind Generation

## Slide 16: ERCOT Total Energy from Solar Generation

## Slide 17: ERCOT % Energy from Solar Generation

## Slide 18
Questions?