## Slide 1
EPRI released version 1.0 of GIC Harmonics Assessment tool.
  Tool is capable of extensive system modeling
  Capable of accurate representation of saturated transformers
  Has a built-in converter.
  Tool includes 3-bus test case
EPRI updated assessment guide: GMD harmonic impacts and asset withstand capabilities.
  Updated generator harmonics impact chapter (harmonic impact, screening criteria, detail case study, and generator protection guidance).
EPRI performed thermal impact screening on 42 additional transformers (different core design, winding geometry, voltage levels…etc) and released Transformer Thermal Impact Assessments for DC Withstand Capability.
EPRI now have 6 sites to monitor on-line the impacts of vibration, harmonics and thermal behavior on transformers. EPRI will continue to monitor these transformers
Department of Energy (DOE) GIC pilot program Phase 2 - mitigate the effect of GICs
  Testing and evaluation of mitigation technologies and study the effectiveness in reducing GIC impacts
  Western Area Power Administration (WAPA) and Tennessee Valley Authority (TVA) are participants
GMDTF February 20, 2020 – Salt Lake City
Notes: EPRI added 84 additional models to the thermal impact screening tool.

## Slide 2
NERC GMD Data Portal update
  Device information may be entered manually or through a file in excel or CSV format.
  Event data may be submitted in Excel or CSV formats
  Event information will be posted on the NERC website
  Email address is being created
  Everyone providing data will be required to have a NERC portal account
GMD studies
  Southern California Edison: No GIC flows for Benchmark above 75 A/Phase, 2-500kV transformers above 85 A/Phase for supplemental
  MISO: 16 transformers above 75 A/Phase and 9 transformers above 85 A/Phase
PSSE added non-uniform E-field option. PSSE can import the latest USGS Efield Grid data from the cloud or you can import your own data.
Texas A&M completed installing 6 magnetometers in December 2019
Dominion will perform GIC field test on a 500kV switch
  The station has two 500/230kV single phase core type autos.
  The maximum injected phase DC current is 50 A.
  Data will be collected to improve existing transformers thermal and harmonic models.
Notes: PSSE: Branch induced voltage is calculated with adaptive nearest neighbor algorithm.