## Summary
Release Date: March 5, 2020
FINAL
Seasonal Assessment of Resource Adequacy for the ERCOT Region (SARA)
Spring 2020
SUMMARY
The ERCOT region is expected to have sufficient installed generating capacity to serve forecasted peak demands in the upcoming spring season (March - May 2020).
The final SARA report reflects a spring 2020 peak forecast of 64,233 MW based on current expectations for average weather.
An additional 3,828 MW of new planned capacity is expected to be available at the start of the spring season, including 42 MW of battery storage. Of that, 1,669 MW are expected to be available during spring peak load hours, with gas-fired units contributing 96 MW, wind contributing 1,238 MW, and solar contributing 335 MW.
The report also includes a forecast of 11,238 MW of unit outages based on historical outage data from the past three spring seasons (starting with 2017), and assumes the high likelihood that the spring peak demand will occur in May.
While a significant amount of unit maintenance is conducted during the spring season, much of this maintenance is completed prior to the onset of hotter temperatures/higher electricity demand in late May.
The extreme scenario in this report assumes an extreme April peak demand coinciding with average April generation outages occurring during the peak hours of each weekday.

## Scenarios
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Spring 2020 - Final
Release Date: March 5, 2020
Forecasted Capacity and Demand
| Operational Resources (thermal and hydro), MW | 66524.3 | Based on current Seasonal Maximum Sustainable Limits reported through the unit registration process
| Switchable Capacity Total, MW | 3691 | Installed capacity of units that can interconnect with other Regions and are available to ERCOT
| Less Switchable Capacity Unavailable to ERCOT, MW | -868 | Based on survey responses of Switchable Resource owners
| Available Mothballed Capacity, MW | 0 | Based on seasonal Mothball units plus Probability of Return responses of Mothball Resource owners
| Capacity from Private Use Networks, MW | 3057 | Average grid injection during the top 20 spring peak load hours over the last three years, plus the forecasted net change in generation capacity available to the ERCOT grid pursuant to Nodal Protocol Section 10.3.2.4.
| Coastal Wind, Peak Average Capacity Contribution, MW | 2171.664 | Based on 66% of installed capacity for coastal wind resources (spring season) per ERCOT Nodal Protocols Section 3.2.6.2.2
| Panhandle Wind, Peak Average Capacity Contribution, MW | 1587.132 | Based on 36% of installed capacity for panhandle wind resources (spring season) per ERCOT Nodal Protocols Section 3.2.6.2.2
| Other Wind, Peak Average Capacity Contribution, MW | 5496.338 | Based on 34% of installed capacity for other wind resources (spring season) per ERCOT Nodal Protocols Section 3.2.6.2.2
| Solar Utility-Scale, Peak Average Capacity Contribution, MW | 1409.322 | Based on 62% of rated capacity for solar resources (spring season) per Nodal Protocols Section 3.2.6.2.2
| Storage, Peak Average Capacity Contribution, MW | 0 | Based on 0% of rated capacity (spring season); resources assumed to provide regulation reserves rather than sustained capacity available to meet peak loads
| RMR Capacity to be under Contract | 0
| Capacity Pending Retirement, MW | 0 | Announced retired capacity that is undergoing ERCOT grid reliability reviews pursuant to Nodal Protocol Section 3.14.1.2
| Non-Synchronous Ties, Capacity Contribution, MW | 837.5 | Based on import flows during most recent Energy Emergency Alert (EEA) intervals for the winter season. (Used as a proxy for the spring season due to lack of EEA intervals.)
| Planned Thermal Resources with Signed IA, Air Permits and Water Rights, MW | 96 | Based on in-service dates provided by developers
| Planned Coastal Wind with Signed IA, Peak Average Capacity Contribution, MW | 344.586 | Based on in-service dates provided by developers and 66% spring capacity contribution for coastal wind resources
| Planned Panhandle Wind with Signed IA, Peak Average Capacity Contribution, MW | 0 | Based on in-service dates provided by developers and 36% spring capacity contribution for panhandle wind resources
| Planned Other Wind with Signed IA, Peak Average Capacity Contribution, MW | 893.214 | Based on in-service dates provided by developers and 34% spring capacity contribution for other wind resources
| Planned Solar Utility-Scale, Peak Average Capacity Contribution, MW | 335.296 | Based on in-service dates provided by developers and 62% spring capacity contribution for solar resources
| Planned Storage, Peak Average Capacity Contribution, MW | 0 | Based on in-service dates provided by developers and 0% spring capacity contribution for storage resources
[a] Total Resources, MW |  | 85575.352
[b] Peak Demand, MW |  | 64233 | May peak forecast is based on average weather conditions at time of peak from 2003 – 2017
[c] Reserve Capacity [a - b], MW |  | 21342.352
Range of Potential Risks
|  | Forecasted Season Peak Load (May) | Extreme Generation Outages During Peak Maintenance Season (March-April) | Extreme Generation Outages During Peak Maintenance Season (March-April) and Extreme Peak Load (April)
| Seasonal Load Adjustment | 0 | -7868 | -3072 | April peak forecast is 56,365 MW, and the extreme peak forecast is 61,161 MW; adjustments reflect April peak forecast for average and 90th percentile weather conditions, respectively
| Typical May Maintenance Outages | 6064 | 6064 | 6064 | Based on historical average of planned maintenance outages for May weekdays, hours ending 3 pm - 8 pm (starting in 2017)
| Typical May Forced Outages | 5174 | 5174 | 5174 | Based on historical average of forced outages for May weekdays, hours ending 3 pm - 8 pm (starting in 2017)
| Incremental Unit Outages to Reflect April Peak Maintenance Season | 0 | 8785 | 8785 | Incremental outages based on historical average of forced and planned maintenance outages for April weekdays, hours ending 3 pm - 8 pm (starting in 2017)
[d] Total Uses of Reserve Capacity |  | 11238 | 12155 | 16951
[e] Capacity Available for Operating Reserves, Normal Operating Conditions [c - d], MW |  | 10104.352 | 9187.352 | 4391.352 | See the Background tab for additional details
Less than 2,300 MW indicates risk of EEA1

## SpringCapacities
Unit Capacities - Spring
| UNIT NAME | GENERATION INTERCONNECTION PROJECT CODE | UNIT CODE | COUNTY | FUEL | CDR ZONE | START YEAR | CAPACITY (MW)
Operational Resources (Thermal)
4 | COMANCHE PEAK U1 |  | CPSES_UNIT1 | SOMERVELL | NUCLEAR | NORTH | 1990 | 1227
5 | COMANCHE PEAK U2 |  | CPSES_UNIT2 | SOMERVELL | NUCLEAR | NORTH | 1993 | 1214
6 | SOUTH TEXAS U1 | 20INR0287 | STP_STP_G1 | MATAGORDA | NUCLEAR | COASTAL | 1988 | 1323.2
7 | SOUTH TEXAS U2 |  | STP_STP_G2 | MATAGORDA | NUCLEAR | COASTAL | 1989 | 1310
8 | COLETO CREEK |  | COLETO_COLETOG1 | GOLIAD | COAL | SOUTH | 1980 | 655
9 | FAYETTE POWER U1 |  | FPPYD1_FPP_G1 | FAYETTE | COAL | SOUTH | 1979 | 608
10 | FAYETTE POWER U2 |  | FPPYD1_FPP_G2 | FAYETTE | COAL | SOUTH | 1980 | 608
11 | FAYETTE POWER U3 |  | FPPYD2_FPP_G3 | FAYETTE | COAL | SOUTH | 1988 | 448
12 | J K SPRUCE U1 |  | CALAVERS_JKS1 | BEXAR | COAL | SOUTH | 1992 | 560
13 | J K SPRUCE U2 |  | CALAVERS_JKS2 | BEXAR | COAL | SOUTH | 2010 | 785
14 | LIMESTONE U1 |  | LEG_LEG_G1 | LIMESTONE | COAL | NORTH | 1985 | 824
15 | LIMESTONE U2 |  | LEG_LEG_G2 | LIMESTONE | COAL | NORTH | 1986 | 836
16 | MARTIN LAKE U1 |  | MLSES_UNIT1 | RUSK | COAL | NORTH | 1977 | 815
17 | MARTIN LAKE U2 |  | MLSES_UNIT2 | RUSK | COAL | NORTH | 1978 | 820
18 | MARTIN LAKE U3 |  | MLSES_UNIT3 | RUSK | COAL | NORTH | 1979 | 820
19 | OAK GROVE SES U1 |  | OGSES_UNIT1A | ROBERTSON | COAL | NORTH | 2010 | 855
20 | OAK GROVE SES U2 |  | OGSES_UNIT2 | ROBERTSON | COAL | NORTH | 2011 | 855
21 | OKLAUNION U1 |  | OKLA_OKLA_G1 | WILBARGER | COAL | WEST | 1986 | 650
22 | SAN MIGUEL U1 |  | SANMIGL_G1 | ATASCOSA | COAL | SOUTH | 1982 | 391
23 | SANDY CREEK U1 |  | SCES_UNIT1 | MCLENNAN | COAL | NORTH | 2013 | 945
24 | TWIN OAKS U1 |  | TNP_ONE_TNP_O_1 | ROBERTSON | COAL | NORTH | 1990 | 155
25 | TWIN OAKS U2 |  | TNP_ONE_TNP_O_2 | ROBERTSON | COAL | NORTH | 1991 | 155
26 | W A PARISH U5 |  | WAP_WAP_G5 | FT. BEND | COAL | HOUSTON | 1977 | 664
27 | W A PARISH U6 |  | WAP_WAP_G6 | FT. BEND | COAL | HOUSTON | 1978 | 663
28 | W A PARISH U7 |  | WAP_WAP_G7 | FT. BEND | COAL | HOUSTON | 1980 | 577
29 | W A PARISH U8 |  | WAP_WAP_G8 | FT. BEND | COAL | HOUSTON | 1982 | 610
30 | ARTHUR VON ROSENBERG 1 CTG 1 |  | BRAUNIG_AVR1_CT1 | BEXAR | GAS | SOUTH | 2000 | 164
31 | ARTHUR VON ROSENBERG 1 CTG 2 |  | BRAUNIG_AVR1_CT2 | BEXAR | GAS | SOUTH | 2000 | 164
32 | ARTHUR VON ROSENBERG 1 STG |  | BRAUNIG_AVR1_ST | BEXAR | GAS | SOUTH | 2000 | 190
33 | ATKINS CTG 7 |  | ATKINS_ATKINSG7 | BRAZOS | GAS | NORTH | 1973 | 19
34 | BARNEY M DAVIS CTG 3 |  | B_DAVIS_B_DAVIG3 | NUECES | GAS | COASTAL | 2010 | 161
35 | BARNEY M DAVIS CTG 4 |  | B_DAVIS_B_DAVIG4 | NUECES | GAS | COASTAL | 2010 | 161
36 | BARNEY M DAVIS STG 1 |  | B_DAVIS_B_DAVIG1 | NUECES | GAS | COASTAL | 1974 | 330
37 | BARNEY M DAVIS STG 2 |  | B_DAVIS_B_DAVIG2 | NUECES | GAS | COASTAL | 1976 | 322
38 | BASTROP ENERGY CENTER CTG 1 |  | BASTEN_GTG1100 | BASTROP | GAS | SOUTH | 2002 | 157
39 | BASTROP ENERGY CENTER CTG 2 |  | BASTEN_GTG2100 | BASTROP | GAS | SOUTH | 2002 | 157
40 | BASTROP ENERGY CENTER STG |  | BASTEN_ST0100 | BASTROP | GAS | SOUTH | 2002 | 236
41 | BOSQUE ENERGY CENTER CTG 1 |  | BOSQUESW_BSQSU_1 | BOSQUE | GAS | NORTH | 2000 | 161.8
42 | BOSQUE ENERGY CENTER CTG 2 |  | BOSQUESW_BSQSU_2 | BOSQUE | GAS | NORTH | 2000 | 161.8
43 | BOSQUE ENERGY CENTER CTG 3 |  | BOSQUESW_BSQSU_3 | BOSQUE | GAS | NORTH | 2001 | 160.6
44 | BOSQUE ENERGY CENTER STG 4 |  | BOSQUESW_BSQSU_4 | BOSQUE | GAS | NORTH | 2001 | 83.6
45 | BOSQUE ENERGY CENTER STG 5 |  | BOSQUESW_BSQSU_5 | BOSQUE | GAS | NORTH | 2009 | 222.4
46 | BRAZOS VALLEY CTG 1 |  | BVE_UNIT1 | FORT BEND | GAS | HOUSTON | 2003 | 169
47 | BRAZOS VALLEY CTG 2 |  | BVE_UNIT2 | FORT BEND | GAS | HOUSTON | 2003 | 169
48 | BRAZOS VALLEY STG 3 |  | BVE_UNIT3 | FORT BEND | GAS | HOUSTON | 2003 | 270
49 | CALENERGY-FALCON SEABOARD CTG 1 |  | FLCNS_UNIT1 | HOWARD | GAS | WEST | 1987 | 77
50 | CALENERGY-FALCON SEABOARD CTG 2 |  | FLCNS_UNIT2 | HOWARD | GAS | WEST | 1987 | 77
51 | CALENERGY-FALCON SEABOARD STG 3 |  | FLCNS_UNIT3 | HOWARD | GAS | WEST | 1988 | 71
52 | CALHOUN (PORT COMFORT) CTG 1 |  | CALHOUN_UNIT1 | CALHOUN | GAS | COASTAL | 2017 | 46.7
53 | CALHOUN (PORT COMFORT) CTG 2 |  | CALHOUN_UNIT2 | CALHOUN | GAS | COASTAL | 2017 | 46.7
54 | CASTLEMAN CHAMON CTG 1 |  | CHAMON_CTG_0101 | HARRIS | GAS | HOUSTON | 2017 | 46.7
55 | CASTLEMAN CHAMON CTG 2 |  | CHAMON_CTG_0301 | HARRIS | GAS | HOUSTON | 2017 | 46.7
56 | CEDAR BAYOU 4 CTG 1 |  | CBY4_CT41 | CHAMBERS | GAS | HOUSTON | 2009 | 168
57 | CEDAR BAYOU 4 CTG 2 |  | CBY4_CT42 | CHAMBERS | GAS | HOUSTON | 2009 | 168
58 | CEDAR BAYOU 4 STG |  | CBY4_ST04 | CHAMBERS | GAS | HOUSTON | 2009 | 182
59 | CEDAR BAYOU STG 1 |  | CBY_CBY_G1 | CHAMBERS | GAS | HOUSTON | 1970 | 745
60 | CEDAR BAYOU STG 2 |  | CBY_CBY_G2 | CHAMBERS | GAS | HOUSTON | 1972 | 749
61 | COLORADO BEND ENERGY CENTER CTG 1 |  | CBEC_GT1 | WHARTON | GAS | SOUTH | 2007 | 74
62 | COLORADO BEND ENERGY CENTER CTG 2 |  | CBEC_GT2 | WHARTON | GAS | SOUTH | 2007 | 67
63 | COLORADO BEND ENERGY CENTER CTG 3 |  | CBEC_GT3 | WHARTON | GAS | SOUTH | 2008 | 73
64 | COLORADO BEND ENERGY CENTER CTG 4 |  | CBEC_GT4 | WHARTON | GAS | SOUTH | 2008 | 68
65 | COLORADO BEND ENERGY CENTER STG 1 |  | CBEC_STG1 | WHARTON | GAS | SOUTH | 2007 | 100
66 | COLORADO BEND ENERGY CENTER STG 2 |  | CBEC_STG2 | WHARTON | GAS | SOUTH | 2008 | 105
67 | COLORADO BEND II CTG 7 | 18INR0077 | CBECII_CT7 | WHARTON | GAS | SOUTH | 2017 | 332.1
68 | COLORADO BEND II CTG 8 | 18INR0077 | CBECII_CT8 | WHARTON | GAS | SOUTH | 2017 | 337.8
69 | COLORADO BEND II STG 9 | 18INR0077 | CBECII_STG9 | WHARTON | GAS | SOUTH | 2017 | 482.3
70 | CVC CHANNELVIEW CTG 1 |  | CVC_CVC_G1 | HARRIS | GAS | HOUSTON | 2008 | 181
71 | CVC CHANNELVIEW CTG 2 |  | CVC_CVC_G2 | HARRIS | GAS | HOUSTON | 2008 | 178
72 | CVC CHANNELVIEW CTG 3 |  | CVC_CVC_G3 | HARRIS | GAS | HOUSTON | 2008 | 178
73 | CVC CHANNELVIEW STG 5 |  | CVC_CVC_G5 | HARRIS | GAS | HOUSTON | 2008 | 144
74 | DANSBY CTG 2 |  | DANSBY_DANSBYG2 | BRAZOS | GAS | NORTH | 2004 | 46.5
75 | DANSBY CTG 3 |  | DANSBY_DANSBYG3 | BRAZOS | GAS | NORTH | 2010 | 48.5
76 | DANSBY STG 1 |  | DANSBY_DANSBYG1 | BRAZOS | GAS | NORTH | 1978 | 108.5
77 | DECKER CREEK CTG 1 |  | DECKER_DPGT_1 | TRAVIS | GAS | SOUTH | 1989 | 50
78 | DECKER CREEK CTG 2 |  | DECKER_DPGT_2 | TRAVIS | GAS | SOUTH | 1989 | 50
79 | DECKER CREEK CTG 3 |  | DECKER_DPGT_3 | TRAVIS | GAS | SOUTH | 1989 | 50
80 | DECKER CREEK CTG 4 |  | DECKER_DPGT_4 | TRAVIS | GAS | SOUTH | 1989 | 50
81 | DECKER CREEK STG 1 |  | DECKER_DPG1 | TRAVIS | GAS | SOUTH | 1971 | 320
82 | DECKER CREEK STG 2 |  | DECKER_DPG2 | TRAVIS | GAS | SOUTH | 1978 | 428
83 | DECORDOVA CTG 1 |  | DCSES_CT10 | HOOD | GAS | NORTH | 1990 | 71
84 | DECORDOVA CTG 2 |  | DCSES_CT20 | HOOD | GAS | NORTH | 1990 | 70
85 | DECORDOVA CTG 3 |  | DCSES_CT30 | HOOD | GAS | NORTH | 1990 | 70
86 | DECORDOVA CTG 4 |  | DCSES_CT40 | HOOD | GAS | NORTH | 1990 | 71
87 | DEER PARK ENERGY CENTER CTG 1 |  | DDPEC_GT1 | HARRIS | GAS | HOUSTON | 2002 | 190
88 | DEER PARK ENERGY CENTER CTG 2 |  | DDPEC_GT2 | HARRIS | GAS | HOUSTON | 2002 | 202
89 | DEER PARK ENERGY CENTER CTG 3 |  | DDPEC_GT3 | HARRIS | GAS | HOUSTON | 2002 | 190
90 | DEER PARK ENERGY CENTER CTG 4 |  | DDPEC_GT4 | HARRIS | GAS | HOUSTON | 2002 | 202
91 | DEER PARK ENERGY CENTER CTG 6 |  | DDPEC_GT6 | HARRIS | GAS | HOUSTON | 2014 | 174
92 | DEER PARK ENERGY CENTER STG 1 |  | DDPEC_ST1 | HARRIS | GAS | HOUSTON | 2002 | 290
93 | DENTON ENERGY CENTER IC A |  | DEC_AGR_A | DENTON | GAS | NORTH | 2018 | 56.5
94 | DENTON ENERGY CENTER IC B |  | DEC_AGR_B | DENTON | GAS | NORTH | 2018 | 56.5
95 | DENTON ENERGY CENTER IC C |  | DEC_AGR_C | DENTON | GAS | NORTH | 2018 | 56.5
96 | DENTON ENERGY CENTER IC D |  | DEC_AGR_D | DENTON | GAS | NORTH | 2018 | 56.5
97 | ECTOR COUNTY ENERGY CTG 1 |  | ECEC_G1 | ECTOR | GAS | WEST | 2015 | 153.6
98 | ECTOR COUNTY ENERGY CTG 2 |  | ECEC_G2 | ECTOR | GAS | WEST | 2015 | 153.6
99 | ELK STATION IC 3 |  | AEEC_ELK_3 | HALE | GAS | PANHANDLE | 2016 | 195
100 | ENNIS POWER STATION CTG 2 | 21INR0448 | ETCCS_CT1 | ELLIS | GAS | NORTH | 2002 | 209
101 | ENNIS POWER STATION STG 1 | 21INR0448 | ETCCS_UNIT1 | ELLIS | GAS | NORTH | 2002 | 116
102 | EXTEX LAPORTE GEN STN CTG 1 |  | AZ_AZ_G1 | HARRIS | GAS | HOUSTON | 2009 | 36
103 | EXTEX LAPORTE GEN STN CTG 2 |  | AZ_AZ_G2 | HARRIS | GAS | HOUSTON | 2009 | 36
104 | EXTEX LAPORTE GEN STN CTG 3 |  | AZ_AZ_G3 | HARRIS | GAS | HOUSTON | 2009 | 36
105 | EXTEX LAPORTE GEN STN CTG 4 |  | AZ_AZ_G4 | HARRIS | GAS | HOUSTON | 2009 | 36
106 | FERGUSON REPLACEMENT CTG 1 |  | FERGCC_FERGGT1 | LLANO | GAS | SOUTH | 2014 | 176
107 | FERGUSON REPLACEMENT CTG 2 |  | FERGCC_FERGGT2 | LLANO | GAS | SOUTH | 2014 | 176
108 | FERGUSON REPLACEMENT STG 1 |  | FERGCC_FERGST1 | LLANO | GAS | SOUTH | 2014 | 189
109 | FORNEY ENERGY CENTER CTG 11 |  | FRNYPP_GT11 | KAUFMAN | GAS | NORTH | 2003 | 167
110 | FORNEY ENERGY CENTER CTG 12 |  | FRNYPP_GT12 | KAUFMAN | GAS | NORTH | 2003 | 159
111 | FORNEY ENERGY CENTER CTG 13 |  | FRNYPP_GT13 | KAUFMAN | GAS | NORTH | 2003 | 159
112 | FORNEY ENERGY CENTER CTG 21 |  | FRNYPP_GT21 | KAUFMAN | GAS | NORTH | 2003 | 167
113 | FORNEY ENERGY CENTER CTG 22 |  | FRNYPP_GT22 | KAUFMAN | GAS | NORTH | 2003 | 159
114 | FORNEY ENERGY CENTER CTG 23 |  | FRNYPP_GT23 | KAUFMAN | GAS | NORTH | 2003 | 159
115 | FORNEY ENERGY CENTER STG 10 |  | FRNYPP_ST10 | KAUFMAN | GAS | NORTH | 2003 | 408
116 | FORNEY ENERGY CENTER STG 20 |  | FRNYPP_ST20 | KAUFMAN | GAS | NORTH | 2003 | 408
117 | FREESTONE ENERGY CENTER CTG 1 |  | FREC_GT1 | FREESTONE | GAS | NORTH | 2002 | 156.2
118 | FREESTONE ENERGY CENTER CTG 2 |  | FREC_GT2 | FREESTONE | GAS | NORTH | 2002 | 156.2
119 | FREESTONE ENERGY CENTER CTG 4 |  | FREC_GT4 | FREESTONE | GAS | NORTH | 2002 | 156.5
120 | FREESTONE ENERGY CENTER CTG 5 |  | FREC_GT5 | FREESTONE | GAS | NORTH | 2002 | 156.5
121 | FREESTONE ENERGY CENTER STG 3 |  | FREC_ST3 | FREESTONE | GAS | NORTH | 2002 | 178
122 | FREESTONE ENERGY CENTER STG 6 |  | FREC_ST6 | FREESTONE | GAS | NORTH | 2002 | 177.1
123 | FRIENDSWOOD G |  | FEGC_UNIT1 | HARRIS | GAS | HOUSTON | 2018 | 119
124 | GRAHAM STG 1 |  | GRSES_UNIT1 | YOUNG | GAS | WEST | 1960 | 234
125 | GRAHAM STG 2 |  | GRSES_UNIT2 | YOUNG | GAS | WEST | 1969 | 390
126 | GREENS BAYOU CTG 73 |  | GBY_GBYGT73 | HARRIS | GAS | HOUSTON | 1976 | 57
127 | GREENS BAYOU CTG 74 |  | GBY_GBYGT74 | HARRIS | GAS | HOUSTON | 1976 | 57
128 | GREENS BAYOU CTG 81 |  | GBY_GBYGT81 | HARRIS | GAS | HOUSTON | 1976 | 57
129 | GREENS BAYOU CTG 82 |  | GBY_GBYGT82 | HARRIS | GAS | HOUSTON | 1976 | 50
130 | GREENS BAYOU CTG 83 |  | GBY_GBYGT83 | HARRIS | GAS | HOUSTON | 1976 | 57
131 | GREENS BAYOU CTG 84 |  | GBY_GBYGT84 | HARRIS | GAS | HOUSTON | 1976 | 57
132 | GREENVILLE IC ENGINE PLANT IC 1 |  | STEAM_ENGINE_1 | HUNT | GAS | NORTH | 2010 | 8.2
133 | GREENVILLE IC ENGINE PLANT IC 2 |  | STEAM_ENGINE_2 | HUNT | GAS | NORTH | 2010 | 8.2
134 | GREENVILLE IC ENGINE PLANT IC 3 |  | STEAM_ENGINE_3 | HUNT | GAS | NORTH | 2010 | 8.2
135 | GUADALUPE ENERGY CENTER CTG 1 |  | GUADG_GAS1 | GUADALUPE | GAS | SOUTH | 2000 | 158
136 | GUADALUPE ENERGY CENTER CTG 2 |  | GUADG_GAS2 | GUADALUPE | GAS | SOUTH | 2000 | 158
137 | GUADALUPE ENERGY CENTER CTG 3 |  | GUADG_GAS3 | GUADALUPE | GAS | SOUTH | 2000 | 158
138 | GUADALUPE ENERGY CENTER CTG 4 |  | GUADG_GAS4 | GUADALUPE | GAS | SOUTH | 2000 | 158
139 | GUADALUPE ENERGY CENTER STG 5 |  | GUADG_STM5 | GUADALUPE | GAS | SOUTH | 2000 | 200
140 | GUADALUPE ENERGY CENTER STG 6 |  | GUADG_STM6 | GUADALUPE | GAS | SOUTH | 2000 | 200
141 | HANDLEY STG 3 |  | HLSES_UNIT3 | TARRANT | GAS | NORTH | 1963 | 395
142 | HANDLEY STG 4 |  | HLSES_UNIT4 | TARRANT | GAS | NORTH | 1976 | 435
143 | HANDLEY STG 5 |  | HLSES_UNIT5 | TARRANT | GAS | NORTH | 1977 | 435
144 | HAYS ENERGY FACILITY CSG 1 |  | HAYSEN_HAYSENG1 | HAYS | GAS | SOUTH | 2002 | 213
145 | HAYS ENERGY FACILITY CSG 2 |  | HAYSEN_HAYSENG2 | HAYS | GAS | SOUTH | 2002 | 214
146 | HAYS ENERGY FACILITY CSG 3 |  | HAYSEN_HAYSENG3 | HAYS | GAS | SOUTH | 2002 | 213
147 | HAYS ENERGY FACILITY CSG 4 |  | HAYSEN_HAYSENG4 | HAYS | GAS | SOUTH | 2002 | 216
148 | HIDALGO ENERGY CENTER CTG 1 |  | DUKE_DUKE_GT1 | HIDALGO | GAS | SOUTH | 2000 | 143
149 | HIDALGO ENERGY CENTER CTG 2 |  | DUKE_DUKE_GT2 | HIDALGO | GAS | SOUTH | 2000 | 143
150 | HIDALGO ENERGY CENTER STG 1 |  | DUKE_DUKE_ST1 | HIDALGO | GAS | SOUTH | 2000 | 172
151 | JACK COUNTY GEN FACILITY CTG 1 |  | JACKCNTY_CT1 | JACK | GAS | NORTH | 2006 | 150
152 | JACK COUNTY GEN FACILITY CTG 2 |  | JACKCNTY_CT2 | JACK | GAS | NORTH | 2006 | 150
153 | JACK COUNTY GEN FACILITY CTG 3 |  | JCKCNTY2_CT3 | JACK | GAS | NORTH | 2011 | 150
154 | JACK COUNTY GEN FACILITY CTG 4 |  | JCKCNTY2_CT4 | JACK | GAS | NORTH | 2011 | 150
155 | JACK COUNTY GEN FACILITY STG 1 |  | JACKCNTY_STG | JACK | GAS | NORTH | 2006 | 285
156 | JACK COUNTY GEN FACILITY STG 2 |  | JCKCNTY2_ST2 | JACK | GAS | NORTH | 2011 | 285
157 | JOHNSON COUNTY GEN FACILITY CTG 1 |  | TEN_CT1 | JOHNSON | GAS | NORTH | 1997 | 163
158 | JOHNSON COUNTY GEN FACILITY STG 1 |  | TEN_STG | JOHNSON | GAS | NORTH | 1997 | 106
159 | LAKE HUBBARD STG 1 |  | LHSES_UNIT1 | DALLAS | GAS | NORTH | 1970 | 392
160 | LAKE HUBBARD STG 2 |  | LHSES_UNIT2A | DALLAS | GAS | NORTH | 1973 | 523
161 | LAMAR ENERGY CENTER CTG 11 |  | LPCCS_CT11 | LAMAR | GAS | NORTH | 2000 | 161
162 | LAMAR ENERGY CENTER CTG 12 |  | LPCCS_CT12 | LAMAR | GAS | NORTH | 2000 | 153
163 | LAMAR ENERGY CENTER CTG 21 |  | LPCCS_CT21 | LAMAR | GAS | NORTH | 2000 | 153
164 | LAMAR ENERGY CENTER CTG 22 |  | LPCCS_CT22 | LAMAR | GAS | NORTH | 2000 | 161
165 | LAMAR ENERGY CENTER STG 1 |  | LPCCS_UNIT1 | LAMAR | GAS | NORTH | 2000 | 204
166 | LAMAR ENERGY CENTER STG 2 |  | LPCCS_UNIT2 | LAMAR | GAS | NORTH | 2000 | 204
167 | LAREDO CTG 4 |  | LARDVFTN_G4 | WEBB | GAS | SOUTH | 2008 | 92.9
168 | LAREDO CTG 5 |  | LARDVFTN_G5 | WEBB | GAS | SOUTH | 2008 | 90.1
169 | LEON CREEK PEAKER CTG 1 |  | LEON_CRK_LCPCT1 | BEXAR | GAS | SOUTH | 2004 | 46
170 | LEON CREEK PEAKER CTG 2 |  | LEON_CRK_LCPCT2 | BEXAR | GAS | SOUTH | 2004 | 46
171 | LEON CREEK PEAKER CTG 3 |  | LEON_CRK_LCPCT3 | BEXAR | GAS | SOUTH | 2004 | 46
172 | LEON CREEK PEAKER CTG 4 |  | LEON_CRK_LCPCT4 | BEXAR | GAS | SOUTH | 2004 | 46
173 | LOST PINES POWER CTG 1 |  | LOSTPI_LOSTPGT1 | BASTROP | GAS | SOUTH | 2001 | 183
174 | LOST PINES POWER CTG 2 |  | LOSTPI_LOSTPGT2 | BASTROP | GAS | SOUTH | 2001 | 175
175 | LOST PINES POWER STG 1 |  | LOSTPI_LOSTPST1 | BASTROP | GAS | SOUTH | 2001 | 192
176 | MAGIC VALLEY STATION CTG 1 |  | NEDIN_NEDIN_G1 | HIDALGO | GAS | SOUTH | 2001 | 213.6
177 | MAGIC VALLEY STATION CTG 2 |  | NEDIN_NEDIN_G2 | HIDALGO | GAS | SOUTH | 2001 | 213.6
178 | MAGIC VALLEY STATION STG 3 |  | NEDIN_NEDIN_G3 | HIDALGO | GAS | SOUTH | 2001 | 255.5
179 | MIDLOTHIAN ENERGY FACILITY CTG 1 |  | MDANP_CT1 | ELLIS | GAS | NORTH | 2001 | 232
180 | MIDLOTHIAN ENERGY FACILITY CTG 2 |  | MDANP_CT2 | ELLIS | GAS | NORTH | 2001 | 230
181 | MIDLOTHIAN ENERGY FACILITY CTG 3 |  | MDANP_CT3 | ELLIS | GAS | NORTH | 2001 | 229
182 | MIDLOTHIAN ENERGY FACILITY CTG 4 |  | MDANP_CT4 | ELLIS | GAS | NORTH | 2001 | 232
183 | MIDLOTHIAN ENERGY FACILITY CTG 5 |  | MDANP_CT5 | ELLIS | GAS | NORTH | 2002 | 244
184 | MIDLOTHIAN ENERGY FACILITY CTG 6 |  | MDANP_CT6 | ELLIS | GAS | NORTH | 2002 | 246
185 | MORGAN CREEK CTG 1 |  | MGSES_CT1 | MITCHELL | GAS | WEST | 1988 | 67
186 | MORGAN CREEK CTG 2 |  | MGSES_CT2 | MITCHELL | GAS | WEST | 1988 | 66
187 | MORGAN CREEK CTG 3 |  | MGSES_CT3 | MITCHELL | GAS | WEST | 1988 | 66
188 | MORGAN CREEK CTG 4 |  | MGSES_CT4 | MITCHELL | GAS | WEST | 1988 | 67
189 | MORGAN CREEK CTG 5 |  | MGSES_CT5 | MITCHELL | GAS | WEST | 1988 | 68
190 | MORGAN CREEK CTG 6 |  | MGSES_CT6 | MITCHELL | GAS | WEST | 1988 | 68
191 | MOUNTAIN CREEK STG 6 |  | MCSES_UNIT6 | DALLAS | GAS | NORTH | 1956 | 122
192 | MOUNTAIN CREEK STG 7 |  | MCSES_UNIT7 | DALLAS | GAS | NORTH | 1958 | 118
193 | MOUNTAIN CREEK STG 8 |  | MCSES_UNIT8 | DALLAS | GAS | NORTH | 1967 | 568
194 | NUECES BAY REPOWER CTG 8 |  | NUECES_B_NUECESG8 | NUECES | GAS | COASTAL | 2010 | 161
195 | NUECES BAY REPOWER CTG 9 |  | NUECES_B_NUECESG9 | NUECES | GAS | COASTAL | 2010 | 161
196 | NUECES BAY REPOWER STG 7 |  | NUECES_B_NUECESG7 | NUECES | GAS | COASTAL | 1972 | 322
197 | O W SOMMERS STG 1 |  | CALAVERS_OWS1 | BEXAR | GAS | SOUTH | 1972 | 420
198 | O W SOMMERS STG 2 |  | CALAVERS_OWS2 | BEXAR | GAS | SOUTH | 1974 | 410
199 | ODESSA-ECTOR POWER CTG 11 |  | OECCS_CT11 | ECTOR | GAS | WEST | 2001 | 164.6
200 | ODESSA-ECTOR POWER CTG 12 |  | OECCS_CT12 | ECTOR | GAS | WEST | 2001 | 156.1
201 | ODESSA-ECTOR POWER CTG 21 | 20INR0282 | OECCS_CT21 | ECTOR | GAS | WEST | 2001 | 164.6
202 | ODESSA-ECTOR POWER CTG 22 | 20INR0282 | OECCS_CT22 | ECTOR | GAS | WEST | 2001 | 156.1
203 | ODESSA-ECTOR POWER STG 1 |  | OECCS_UNIT1 | ECTOR | GAS | WEST | 2001 | 206.4
204 | ODESSA-ECTOR POWER STG 2 | 20INR0282 | OECCS_UNIT2 | ECTOR | GAS | WEST | 2001 | 206.4
205 | PANDA SHERMAN POWER CTG 1 |  | PANDA_S_SHER1CT1 | GRAYSON | GAS | NORTH | 2014 | 218.5
206 | PANDA SHERMAN POWER CTG 2 |  | PANDA_S_SHER1CT2 | GRAYSON | GAS | NORTH | 2014 | 218.5
207 | PANDA SHERMAN POWER STG 1 |  | PANDA_S_SHER1ST1 | GRAYSON | GAS | NORTH | 2014 | 353.1
208 | PANDA TEMPLE I POWER CTG 1 |  | PANDA_T1_TMPL1CT1 | BELL | GAS | NORTH | 2014 | 218.5
209 | PANDA TEMPLE I POWER CTG 2 |  | PANDA_T1_TMPL1CT2 | BELL | GAS | NORTH | 2014 | 218.5
210 | PANDA TEMPLE I POWER STG 1 |  | PANDA_T1_TMPL1ST1 | BELL | GAS | NORTH | 2014 | 353.1
211 | PANDA TEMPLE II POWER CTG 1 |  | PANDA_T2_TMPL2CT1 | BELL | GAS | NORTH | 2015 | 218.5
212 | PANDA TEMPLE II POWER CTG 2 |  | PANDA_T2_TMPL2CT2 | BELL | GAS | NORTH | 2015 | 218.5
213 | PANDA TEMPLE II POWER STG 1 |  | PANDA_T2_TMPL2ST1 | BELL | GAS | NORTH | 2015 | 353.1
214 | PARIS ENERGY CENTER CTG 1 |  | TNSKA_GT1 | LAMAR | GAS | NORTH | 1989 | 86
215 | PARIS ENERGY CENTER CTG 2 |  | TNSKA_GT2 | LAMAR | GAS | NORTH | 1989 | 86
216 | PARIS ENERGY CENTER STG 1 |  | TNSKA_STG | LAMAR | GAS | NORTH | 1990 | 87
217 | PASADENA COGEN FACILITY CTG 2 |  | PSG_PSG_GT2 | HARRIS | GAS | HOUSTON | 2000 | 170
218 | PASADENA COGEN FACILITY CTG 3 |  | PSG_PSG_GT3 | HARRIS | GAS | HOUSTON | 2000 | 170
219 | PASADENA COGEN FACILITY STG 2 |  | PSG_PSG_ST2 | HARRIS | GAS | HOUSTON | 2000 | 168
220 | PEARSALL ENGINE PLANT IC A |  | PEARSAL2_AGR_A | FRIO | GAS | SOUTH | 2012 | 50.6
221 | PEARSALL ENGINE PLANT IC B |  | PEARSAL2_AGR_B | FRIO | GAS | SOUTH | 2012 | 50.6
222 | PEARSALL ENGINE PLANT IC C |  | PEARSAL2_AGR_C | FRIO | GAS | SOUTH | 2012 | 50.6
223 | PEARSALL ENGINE PLANT IC D |  | PEARSAL2_AGR_D | FRIO | GAS | SOUTH | 2012 | 50.6
224 | PERMIAN BASIN CTG 1 |  | PB2SES_CT1 | WARD | GAS | WEST | 1988 | 64
225 | PERMIAN BASIN CTG 2 |  | PB2SES_CT2 | WARD | GAS | WEST | 1988 | 64
226 | PERMIAN BASIN CTG 3 |  | PB2SES_CT3 | WARD | GAS | WEST | 1988 | 64
227 | PERMIAN BASIN CTG 4 |  | PB2SES_CT4 | WARD | GAS | WEST | 1990 | 64
228 | PERMIAN BASIN CTG 5 |  | PB2SES_CT5 | WARD | GAS | WEST | 1990 | 65
229 | PHR PEAKERS (BAC) CTG 1 |  | BAC_CTG1 | GALVESTON | GAS | HOUSTON | 2018 | 61
230 | PHR PEAKERS (BAC) CTG 2 |  | BAC_CTG2 | GALVESTON | GAS | HOUSTON | 2018 | 62
231 | PHR PEAKERS (BAC) CTG 3 |  | BAC_CTG3 | GALVESTON | GAS | HOUSTON | 2018 | 52
232 | PHR PEAKERS (BAC) CTG 4 |  | BAC_CTG4 | GALVESTON | GAS | HOUSTON | 2018 | 56
233 | PHR PEAKERS (BAC) CTG 5 |  | BAC_CTG5 | GALVESTON | GAS | HOUSTON | 2018 | 56
234 | PHR PEAKERS (BAC) CTG 6 |  | BAC_CTG6 | GALVESTON | GAS | HOUSTON | 2018 | 54
235 | POWERLANE PLANT STG 1 |  | STEAM1A_STEAM_1 | HUNT | GAS | NORTH | 1966 | 17.5
236 | POWERLANE PLANT STG 2 |  | STEAM_STEAM_2 | HUNT | GAS | NORTH | 1967 | 23.5
237 | POWERLANE PLANT STG 3 |  | STEAM_STEAM_3 | HUNT | GAS | NORTH | 1978 | 39.5
238 | QUAIL RUN ENERGY CTG 1 |  | QALSW_GT1 | ECTOR | GAS | WEST | 2007 | 80
239 | QUAIL RUN ENERGY CTG 2 |  | QALSW_GT2 | ECTOR | GAS | WEST | 2007 | 80
240 | QUAIL RUN ENERGY CTG 3 |  | QALSW_GT3 | ECTOR | GAS | WEST | 2008 | 80
241 | QUAIL RUN ENERGY CTG 4 |  | QALSW_GT4 | ECTOR | GAS | WEST | 2008 | 80
242 | QUAIL RUN ENERGY STG 1 |  | QALSW_STG1 | ECTOR | GAS | WEST | 2007 | 98
243 | QUAIL RUN ENERGY STG 2 |  | QALSW_STG2 | ECTOR | GAS | WEST | 2008 | 98
244 | R W MILLER CTG 4 |  | MIL_MILLERG4 | PALO PINTO | GAS | NORTH | 1994 | 104
245 | R W MILLER CTG 5 |  | MIL_MILLERG5 | PALO PINTO | GAS | NORTH | 1994 | 104
246 | R W MILLER STG 1 |  | MIL_MILLERG1 | PALO PINTO | GAS | NORTH | 1968 | 75
247 | R W MILLER STG 2 |  | MIL_MILLERG2 | PALO PINTO | GAS | NORTH | 1972 | 120
248 | R W MILLER STG 3 |  | MIL_MILLERG3 | PALO PINTO | GAS | NORTH | 1975 | 208
249 | RAY OLINGER CTG 4 |  | OLINGR_OLING_4 | COLLIN | GAS | NORTH | 2001 | 75
250 | RAY OLINGER STG 1 |  | OLINGR_OLING_1 | COLLIN | GAS | NORTH | 1967 | 78
251 | RAY OLINGER STG 2 |  | OLINGR_OLING_2 | COLLIN | GAS | NORTH | 1971 | 107
252 | RAY OLINGER STG 3 |  | OLINGR_OLING_3 | COLLIN | GAS | NORTH | 1975 | 146
253 | REDGATE IC A |  | REDGATE_AGR_A | HIDALGO | GAS | SOUTH | 2016 | 56.3
254 | REDGATE IC B |  | REDGATE_AGR_B | HIDALGO | GAS | SOUTH | 2016 | 56.3
255 | REDGATE IC C |  | REDGATE_AGR_C | HIDALGO | GAS | SOUTH | 2016 | 56.3
256 | REDGATE IC D |  | REDGATE_AGR_D | HIDALGO | GAS | SOUTH | 2016 | 56.3
257 | RIO NOGALES POWER CTG 1 |  | RIONOG_CT1 | GUADALUPE | GAS | SOUTH | 2002 | 173
258 | RIO NOGALES POWER CTG 2 | 21INR0328 | RIONOG_CT2 | GUADALUPE | GAS | SOUTH | 2002 | 160
259 | RIO NOGALES POWER CTG 3 | 20INR0272 | RIONOG_CT3 | GUADALUPE | GAS | SOUTH | 2002 | 173
260 | RIO NOGALES POWER STG 4 |  | RIONOG_ST1 | GUADALUPE | GAS | SOUTH | 2002 | 310
261 | SAM RAYBURN POWER CTG 1 |  | RAYBURN_RAYBURG1 | VICTORIA | GAS | SOUTH | 1963 | 13.5
262 | SAM RAYBURN POWER CTG 2 |  | RAYBURN_RAYBURG2 | VICTORIA | GAS | SOUTH | 1963 | 13.5
263 | SAM RAYBURN POWER CTG 7 |  | RAYBURN_RAYBURG7 | VICTORIA | GAS | SOUTH | 2003 | 50
264 | SAM RAYBURN POWER CTG 8 |  | RAYBURN_RAYBURG8 | VICTORIA | GAS | SOUTH | 2003 | 51
265 | SAM RAYBURN POWER CTG 9 |  | RAYBURN_RAYBURG9 | VICTORIA | GAS | SOUTH | 2003 | 50
266 | SAM RAYBURN POWER STG 10 |  | RAYBURN_RAYBURG10 | VICTORIA | GAS | SOUTH | 2003 | 40
267 | SAN JACINTO SES CTG 1 |  | SJS_SJS_G1 | HARRIS | GAS | HOUSTON | 1995 | 83
268 | SAN JACINTO SES CTG 2 |  | SJS_SJS_G2 | HARRIS | GAS | HOUSTON | 1995 | 83
269 | SANDHILL ENERGY CENTER CTG 1 |  | SANDHSYD_SH1 | TRAVIS | GAS | SOUTH | 2001 | 47
270 | SANDHILL ENERGY CENTER CTG 2 |  | SANDHSYD_SH2 | TRAVIS | GAS | SOUTH | 2001 | 47
271 | SANDHILL ENERGY CENTER CTG 3 |  | SANDHSYD_SH3 | TRAVIS | GAS | SOUTH | 2001 | 47
272 | SANDHILL ENERGY CENTER CTG 4 |  | SANDHSYD_SH4 | TRAVIS | GAS | SOUTH | 2001 | 47
273 | SANDHILL ENERGY CENTER CTG 5A |  | SANDHSYD_SH_5A | TRAVIS | GAS | SOUTH | 2004 | 151
274 | SANDHILL ENERGY CENTER CTG 6 |  | SANDHSYD_SH6 | TRAVIS | GAS | SOUTH | 2010 | 47
275 | SANDHILL ENERGY CENTER CTG 7 |  | SANDHSYD_SH7 | TRAVIS | GAS | SOUTH | 2010 | 47
276 | SANDHILL ENERGY CENTER STG 5C |  | SANDHSYD_SH_5C | TRAVIS | GAS | SOUTH | 2004 | 148
277 | SILAS RAY CTG 10 |  | SILASRAY_SILAS_10 | CAMERON | GAS | COASTAL | 2004 | 46
278 | SILAS RAY POWER CTG 9 |  | SILASRAY_SILAS_9 | CAMERON | GAS | COASTAL | 1996 | 40
279 | SILAS RAY POWER STG 6 |  | SILASRAY_SILAS_6 | CAMERON | GAS | COASTAL | 1962 | 20
280 | SIM GIDEON STG 1 |  | GIDEON_GIDEONG1 | BASTROP | GAS | SOUTH | 1965 | 130
281 | SIM GIDEON STG 2 |  | GIDEON_GIDEONG2 | BASTROP | GAS | SOUTH | 1968 | 133
282 | SIM GIDEON STG 3 |  | GIDEON_GIDEONG3 | BASTROP | GAS | SOUTH | 1972 | 336
283 | SKY GLOBAL POWER ONE IC A |  | SKY1_SKY1A | COLORADO | GAS | SOUTH | 2016 | 26.7
284 | SKY GLOBAL POWER ONE IC B |  | SKY1_SKY1B | COLORADO | GAS | SOUTH | 2016 | 26.7
285 | STRYKER CREEK STG 1 |  | SCSES_UNIT1A | CHEROKEE | GAS | NORTH | 1958 | 167
286 | STRYKER CREEK STG 2 |  | SCSES_UNIT2 | CHEROKEE | GAS | NORTH | 1965 | 502
287 | T H WHARTON CTG 1 |  | THW_THWGT_1 | HARRIS | GAS | HOUSTON | 1967 | 13
288 | T H WHARTON POWER CTG 31 |  | THW_THWGT31 | HARRIS | GAS | HOUSTON | 1972 | 56
289 | T H WHARTON POWER CTG 32 |  | THW_THWGT32 | HARRIS | GAS | HOUSTON | 1972 | 56
290 | T H WHARTON POWER CTG 33 |  | THW_THWGT33 | HARRIS | GAS | HOUSTON | 1972 | 56
291 | T H WHARTON POWER CTG 34 |  | THW_THWGT34 | HARRIS | GAS | HOUSTON | 1972 | 56
292 | T H WHARTON POWER CTG 41 |  | THW_THWGT41 | HARRIS | GAS | HOUSTON | 1972 | 56
293 | T H WHARTON POWER CTG 42 |  | THW_THWGT42 | HARRIS | GAS | HOUSTON | 1972 | 56
294 | T H WHARTON POWER CTG 43 |  | THW_THWGT43 | HARRIS | GAS | HOUSTON | 1974 | 56
295 | T H WHARTON POWER CTG 44 |  | THW_THWGT44 | HARRIS | GAS | HOUSTON | 1974 | 56
296 | T H WHARTON POWER CTG 51 |  | THW_THWGT51 | HARRIS | GAS | HOUSTON | 1975 | 57
297 | T H WHARTON POWER CTG 52 |  | THW_THWGT52 | HARRIS | GAS | HOUSTON | 1975 | 57
298 | T H WHARTON POWER CTG 53 |  | THW_THWGT53 | HARRIS | GAS | HOUSTON | 1975 | 57
299 | T H WHARTON POWER CTG 54 |  | THW_THWGT54 | HARRIS | GAS | HOUSTON | 1975 | 57
300 | T H WHARTON POWER CTG 55 |  | THW_THWGT55 | HARRIS | GAS | HOUSTON | 1975 | 57
301 | T H WHARTON POWER CTG 56 |  | THW_THWGT56 | HARRIS | GAS | HOUSTON | 1975 | 57
302 | T H WHARTON POWER STG 3 |  | THW_THWST_3 | HARRIS | GAS | HOUSTON | 1974 | 109
303 | T H WHARTON POWER STG 4 |  | THW_THWST_4 | HARRIS | GAS | HOUSTON | 1974 | 109
304 | TEXAS CITY POWER CTG A |  | TXCTY_CTA | GALVESTON | GAS | HOUSTON | 2000 | 100.6
305 | TEXAS CITY POWER CTG B |  | TXCTY_CTB | GALVESTON | GAS | HOUSTON | 2000 | 100.6
306 | TEXAS CITY POWER CTG C |  | TXCTY_CTC | GALVESTON | GAS | HOUSTON | 2000 | 100.6
307 | TEXAS CITY POWER STG |  | TXCTY_ST | GALVESTON | GAS | HOUSTON | 2000 | 131.5
308 | TEXAS GULF SULPHUR CTG 1 |  | TGF_TGFGT_1 | WHARTON | GAS | SOUTH | 1985 | 70
309 | TRINIDAD STG 6 |  | TRSES_UNIT6 | HENDERSON | GAS | NORTH | 1965 | 235
310 | V H BRAUNIG CTG 5 |  | BRAUNIG_VHB6CT5 | BEXAR | GAS | SOUTH | 2009 | 48
311 | V H BRAUNIG CTG 6 |  | BRAUNIG_VHB6CT6 | BEXAR | GAS | SOUTH | 2009 | 48
312 | V H BRAUNIG CTG 7 |  | BRAUNIG_VHB6CT7 | BEXAR | GAS | SOUTH | 2009 | 48
313 | V H BRAUNIG CTG 8 |  | BRAUNIG_VHB6CT8 | BEXAR | GAS | SOUTH | 2009 | 47
314 | V H BRAUNIG STG 1 |  | BRAUNIG_VHB1 | BEXAR | GAS | SOUTH | 1966 | 217
315 | V H BRAUNIG STG 2 |  | BRAUNIG_VHB2 | BEXAR | GAS | SOUTH | 1968 | 230
316 | V H BRAUNIG STG 3 |  | BRAUNIG_VHB3 | BEXAR | GAS | SOUTH | 1970 | 412
317 | VICTORIA CITY (CITYVICT) CTG 1 |  | CITYVICT_CTG01 | REFUGIO | GAS | COASTAL | 2020 | 46.7
318 | VICTORIA CITY (CITYVICT) CTG 2 |  | CITYVICT_CTG02 | REFUGIO | GAS | COASTAL | 2020 | 46.7
319 | VICTORIA PORT (VICTPORT) CTG 1 |  | VICTPORT_CTG01 | CALHOUN | GAS | SOUTH | 2019 | 46.7
320 | VICTORIA PORT (VICTPORT) CTG 2 |  | VICTPORT_CTG02 | CALHOUN | GAS | SOUTH | 2019 | 46.7
321 | VICTORIA POWER CTG 6 |  | VICTORIA_VICTORG6 | VICTORIA | GAS | SOUTH | 2009 | 171
322 | VICTORIA POWER STG 5 |  | VICTORIA_VICTORG5 | VICTORIA | GAS | SOUTH | 1963 | 132
323 | W A PARISH CTG 1 |  | WAP_WAPGT_1 | FT. BEND | GAS | HOUSTON | 1967 | 13
324 | W A PARISH STG 1 |  | WAP_WAP_G1 | FT. BEND | GAS | HOUSTON | 1958 | 169
325 | W A PARISH STG 2 |  | WAP_WAP_G2 | FT. BEND | GAS | HOUSTON | 1958 | 169
326 | W A PARISH STG 3 |  | WAP_WAP_G3 | FT. BEND | GAS | HOUSTON | 1961 | 246
327 | W A PARISH STG 4 |  | WAP_WAP_G4 | FT. BEND | GAS | HOUSTON | 1968 | 536
328 | WICHITA FALLS CTG 1 |  | WFCOGEN_UNIT1 | WICHITA | GAS | WEST | 1987 | 20
329 | WICHITA FALLS CTG 2 |  | WFCOGEN_UNIT2 | WICHITA | GAS | WEST | 1987 | 20
330 | WICHITA FALLS CTG 3 |  | WFCOGEN_UNIT3 | WICHITA | GAS | WEST | 1987 | 20
331 | WICHITA FALLS STG 4 |  | WFCOGEN_UNIT4 | WICHITA | GAS | WEST | 1987 | 17
332 | WINCHESTER POWER PARK CTG 1 |  | WIPOPA_WPP_G1 | FAYETTE | GAS | SOUTH | 2009 | 44
333 | WINCHESTER POWER PARK CTG 2 |  | WIPOPA_WPP_G2 | FAYETTE | GAS | SOUTH | 2009 | 44
334 | WINCHESTER POWER PARK CTG 3 |  | WIPOPA_WPP_G3 | FAYETTE | GAS | SOUTH | 2009 | 44
335 | WINCHESTER POWER PARK CTG 4 |  | WIPOPA_WPP_G4 | FAYETTE | GAS | SOUTH | 2009 | 44
336 | WISE-TRACTEBEL POWER CTG 1 | 20INR0286 | WCPP_CT1 | WISE | GAS | NORTH | 2004 | 211
337 | WISE-TRACTEBEL POWER CTG 2 | 20INR0286 | WCPP_CT2 | WISE | GAS | NORTH | 2004 | 206
338 | WISE-TRACTEBEL POWER STG 1 | 20INR0286 | WCPP_ST1 | WISE | GAS | NORTH | 2004 | 273
339 | WOLF HOLLOW 2 CTG 4 | 18INR0076 | WHCCS2_CT4 | HOOD | GAS | NORTH | 2017 | 330.6
340 | WOLF HOLLOW 2 CTG 5 | 18INR0076 | WHCCS2_CT5 | HOOD | GAS | NORTH | 2017 | 331.1
341 | WOLF HOLLOW 2 STG 6 | 18INR0076 | WHCCS2_STG6 | HOOD | GAS | NORTH | 2017 | 468.9
342 | WOLF HOLLOW POWER CTG 1 |  | WHCCS_CT1 | HOOD | GAS | NORTH | 2002 | 227
343 | WOLF HOLLOW POWER CTG 2 |  | WHCCS_CT2 | HOOD | GAS | NORTH | 2002 | 227
344 | WOLF HOLLOW POWER STG |  | WHCCS_STG | HOOD | GAS | NORTH | 2002 | 286
345 | NACOGDOCHES POWER |  | NACPW_UNIT1 | NACOGDOCHES | BIOMASS | NORTH | 2012 | 105
346 | BIOENERGY AUSTIN WALZEM RD LFG |  | DG_WALZE_4UNITS | BEXAR | BIOMASS | SOUTH | 2002 | 9.8
347 | BIOENERGY TEXAS COVEL GARDENS LFG |  | DG_MEDIN_1UNIT | BEXAR | BIOMASS | SOUTH | 2005 | 9.6
348 | FARMERS BRANCH LANDFILL GAS TO ENERGY |  | DG_HBR_2UNITS | DENTON | BIOMASS | NORTH | 2011 | 3.2
349 | GRAND PRAIRIE LFG |  | DG_TRIRA_1UNIT | DALLAS | BIOMASS | NORTH | 2015 | 4
350 | NELSON GARDENS LFG |  | DG_78252_4UNITS | BEXAR | BIOMASS | SOUTH | 2013 | 4.2
351 | SKYLINE LFG |  | DG_FERIS_4 UNITS | DALLAS | BIOMASS | NORTH | 2007 | 6.4
352 | WM RENEWABLE-AUSTIN LFG |  | DG_SPRIN_4UNITS | TRAVIS | BIOMASS | SOUTH | 2007 | 6.4
353 | WM RENEWABLE-BIOENERGY PARTNERS LFG |  | DG_BIOE_2UNITS | DENTON | BIOMASS | NORTH | 1988 | 6.2
354 | WM RENEWABLE-DFW GAS RECOVERY LFG |  | DG_BIO2_4UNITS | DENTON | BIOMASS | NORTH | 2009 | 6.4
355 | WM RENEWABLE-MESQUITE CREEK LFG |  | DG_FREIH_2UNITS | COMAL | BIOMASS | SOUTH | 2011 | 3.2
356 | WM RENEWABLE-WESTSIDE LFG |  | DG_WSTHL_3UNITS | PARKER | BIOMASS | NORTH | 2010 | 4.8
357 | Operational Capacity Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 66080.8
358
359 | Operational Resources (Hydro)
360 | AMISTAD HYDRO 1 |  | AMISTAD_AMISTAG1 | VAL VERDE | HYDRO | WEST | 1983 | 37.9
361 | AMISTAD HYDRO 2 |  | AMISTAD_AMISTAG2 | VAL VERDE | HYDRO | WEST | 1983 | 37.9
362 | AUSTIN HYDRO 1 |  | AUSTPL_AUSTING1 | TRAVIS | HYDRO | SOUTH | 1940 | 8
363 | AUSTIN HYDRO 2 |  | AUSTPL_AUSTING2 | TRAVIS | HYDRO | SOUTH | 1940 | 9
364 | BUCHANAN HYDRO 1 |  | BUCHAN_BUCHANG1 | LLANO | HYDRO | SOUTH | 1938 | 16
365 | BUCHANAN HYDRO 2 |  | BUCHAN_BUCHANG2 | LLANO | HYDRO | SOUTH | 1938 | 16
366 | BUCHANAN HYDRO 3 |  | BUCHAN_BUCHANG3 | LLANO | HYDRO | SOUTH | 1950 | 17
367 | DENISON DAM 1 |  | DNDAM_DENISOG1 | GRAYSON | HYDRO | NORTH | 1944 | 40
368 | DENISON DAM 2 |  | DNDAM_DENISOG2 | GRAYSON | HYDRO | NORTH | 1948 | 40
369 | EAGLE PASS HYDRO |  | EAGLE_HY_EAGLE_HY1 | MAVERICK | HYDRO | SOUTH | 2005 | 9.6
370 | FALCON HYDRO 1 |  | FALCON_FALCONG1 | STARR | HYDRO | SOUTH | 1954 | 12
371 | FALCON HYDRO 2 |  | FALCON_FALCONG2 | STARR | HYDRO | SOUTH | 1954 | 12
372 | FALCON HYDRO 3 |  | FALCON_FALCONG3 | STARR | HYDRO | SOUTH | 1954 | 12
373 | GRANITE SHOALS HYDRO 1 |  | WIRTZ_WIRTZ_G1 | BURNET | HYDRO | SOUTH | 1951 | 29
374 | GRANITE SHOALS HYDRO 2 |  | WIRTZ_WIRTZ_G2 | BURNET | HYDRO | SOUTH | 1951 | 29
375 | GUADALUPE BLANCO RIVER AUTH-CANYON |  | CANYHY_CANYHYG1 | COMAL | HYDRO | SOUTH | 1989 | 6
376 | INKS HYDRO 1 |  | INKSDA_INKS_G1 | LLANO | HYDRO | SOUTH | 1938 | 14
377 | MARBLE FALLS HYDRO 1 |  | MARBFA_MARBFAG1 | BURNET | HYDRO | SOUTH | 1951 | 21
378 | MARBLE FALLS HYDRO 2 |  | MARBFA_MARBFAG2 | BURNET | HYDRO | SOUTH | 1951 | 20
379 | MARSHALL FORD HYDRO 1 |  | MARSFO_MARSFOG1 | TRAVIS | HYDRO | SOUTH | 1941 | 36
380 | MARSHALL FORD HYDRO 2 |  | MARSFO_MARSFOG2 | TRAVIS | HYDRO | SOUTH | 1941 | 36
381 | MARSHALL FORD HYDRO 3 |  | MARSFO_MARSFOG3 | TRAVIS | HYDRO | SOUTH | 1941 | 36
382 | WHITNEY DAM HYDRO |  | WND_WHITNEY1 | BOSQUE | HYDRO | NORTH | 1953 | 22
383 | WHITNEY DAM HYDRO 2 |  | WND_WHITNEY2 | BOSQUE | HYDRO | NORTH | 1953 | 22
384 | ARLINGTON OUTLET HYDROELECTRIC FACILITY |  | DG_OAKHL_1UNIT | TARRANT | HYDRO | NORTH | 2014 | 1.4
385 | CITY OF GONZALES HYDRO |  | DG_GONZ_HYDRO_GONZ_HYDRO | GONZALES | HYDRO | SOUTH | 1986 | 1.5
386 | GUADALUPE BLANCO RIVER AUTH-LAKEWOOD TAP |  | DG_LKWDT_2UNITS | GONZALES | HYDRO | SOUTH | 1931 | 2.4
387 | GUADALUPE BLANCO RIVER AUTH-MCQUEENEY |  | DG_MCQUE_5UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 7.7
388 | GUADALUPE BLANCO RIVER AUTH-SCHUMANSVILLE |  | DG_SCHUM_2UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 0
389 | LEWISVILLE HYDRO-CITY OF GARLAND |  | DG_LWSVL_1UNIT | DENTON | HYDRO | NORTH | 1991 | 2.2
390 | Operational Capacity Total (Hydro) | [6 empty] | 553.6
391 | Hydro Capacity Contribution (Top 20 Hours) |  | HYDRO_CAP_CONT |  |  |  |  | 443.5
392
393 | Operational Thermal Capacity Unavailable due to Extended Outage or Derate |  | OPERATION_UNAVAIL |  |  |  |  | 0
394 | Operational Capacity Total (Including Hydro) |  | OPERATION_TOTAL |  |  |  |  | 66524.3
395
396 | Operational Resources (Switchable)
397 | ANTELOPE IC 1 |  | AEEC_ANTLP_1 | HALE | GAS | PANHANDLE | 2016 | 56
398 | ANTELOPE IC 2 |  | AEEC_ANTLP_2 | HALE | GAS | PANHANDLE | 2016 | 56
399 | ANTELOPE IC 3 |  | AEEC_ANTLP_3 | HALE | GAS | PANHANDLE | 2016 | 56
400 | ELK STATION CTG 1 |  | AEEC_ELK_1 | HALE | GAS | PANHANDLE | 2016 | 195
401 | ELK STATION CTG 2 |  | AEEC_ELK_2 | HALE | GAS | PANHANDLE | 2016 | 195
402 | TENASKA FRONTIER STATION CTG 1 |  | FTR_FTR_G1 | GRIMES | GAS | NORTH | 2000 | 180
403 | TENASKA FRONTIER STATION CTG 2 |  | FTR_FTR_G2 | GRIMES | GAS | NORTH | 2000 | 180
404 | TENASKA FRONTIER STATION CTG 3 |  | FTR_FTR_G3 | GRIMES | GAS | NORTH | 2000 | 180
405 | TENASKA FRONTIER STATION STG 4 |  | FTR_FTR_G4 | GRIMES | GAS | NORTH | 2000 | 400
406 | TENASKA GATEWAY STATION CTG 1 |  | TGCCS_CT1 | RUSK | GAS | NORTH | 2001 | 162
407 | TENASKA GATEWAY STATION CTG 2 |  | TGCCS_CT2 | RUSK | GAS | NORTH | 2001 | 179
408 | TENASKA GATEWAY STATION CTG 3 |  | TGCCS_CT3 | RUSK | GAS | NORTH | 2001 | 178
409 | TENASKA GATEWAY STATION STG 4 |  | TGCCS_UNIT4 | RUSK | GAS | NORTH | 2001 | 389
410 | TENASKA KIAMICHI STATION 1CT101 |  | KMCHI_1CT101 | FANNIN | GAS | NORTH | 2003 | 162
411 | TENASKA KIAMICHI STATION 1CT201 |  | KMCHI_1CT201 | FANNIN | GAS | NORTH | 2003 | 158
412 | TENASKA KIAMICHI STATION 1ST |  | KMCHI_1ST | FANNIN | GAS | NORTH | 2003 | 322
413 | TENASKA KIAMICHI STATION 2CT101 |  | KMCHI_2CT101 | FANNIN | GAS | NORTH | 2003 | 159
414 | TENASKA KIAMICHI STATION 2CT201 |  | KMCHI_2CT201 | FANNIN | GAS | NORTH | 2003 | 161
415 | TENASKA KIAMICHI STATION 2ST |  | KMCHI_2ST | FANNIN | GAS | NORTH | 2003 | 323
416 | Switchable Capacity Total | [6 empty] | 3691
417
418 | Switchable Capacity Unavailable to ERCOT
419 | ANTELOPE IC 1 |  | AEEC_ANTLP_1_UNAVAIL | HALE | GAS | PANHANDLE | 2017 | -56
420 | ANTELOPE IC 2 |  | AEEC_ANTLP_2_UNAVAIL | HALE | GAS | PANHANDLE | 2017 | -56
421 | ANTELOPE IC 3 |  | AEEC_ANTLP_3_UNAVAIL | HALE | GAS | PANHANDLE | 2017 | -56
422 | ELK STATION CTG 1 |  | AEEC_ELK_1_UNAVAIL | HALE | GAS | PANHANDLE | 2017 | -200
423 | ELK STATION CTG 2 |  | AEEC_ELK_2_UNAVAIL | HALE | GAS | PANHANDLE | 2017 | -200
424 | TENASKA FRONTIER STATION |  | FTR_FTR_UNAVAIL | GRIMES | GAS | NORTH | 2016 | -300
425 | Switchable Capacity Unavailable to ERCOT |  | SWITCH_UNAVAIL |  |  |  |  | -868
426
427 | Available Mothball Capacity based on Owner's Return Probability |  | MOTH_AVAIL |  |  |  |  | 0
428
429 | Private-Use Network Capacity Contribution (Top 20 Hours) |  | PUN_CAP_CONT |  | GAS |  |  | 3027
430 | Private-Use Network Forecast Adjustment (per Protocol 10.3.2.4) |  | PUN_CAP_ADJUST |  | GAS |  |  | 30
431
432 | Operational Resources (Wind)
433 | BAFFIN WIND UNIT1 |  | BAFFIN_UNIT1 | KENEDY | WIND-C | COASTAL | 2016 | 100
434 | BAFFIN WIND UNIT2 |  | BAFFIN_UNIT2 | KENEDY | WIND-C | COASTAL | 2016 | 102
435 | BRUENNING'S BREEZE A |  | BBREEZE_UNIT1 | WILLACY | WIND-C | COASTAL | 2017 | 120
436 | BRUENNING'S BREEZE B |  | BBREEZE_UNIT2 | WILLACY | WIND-C | COASTAL | 2017 | 108
437 | CAMERON COUNTY WIND |  | CAMWIND_UNIT1 | CAMERON | WIND-C | COASTAL | 2016 | 165
438 | CHAPMAN RANCH WIND IA (SANTA CRUZ) |  | SANTACRU_UNIT1 | NUECES | WIND-C | COASTAL | 2017 | 150.6
439 | CHAPMAN RANCH WIND IB (SANTA CRUZ) |  | SANTACRU_UNIT2 | NUECES | WIND-C | COASTAL | 2017 | 98.4
440 | GULF WIND I |  | TGW_T1 | KENEDY | WIND-C | COASTAL | 2009 | 141.6
441 | GULF WIND II |  | TGW_T2 | KENEDY | WIND-C | COASTAL | 2009 | 141.6
442 | KARANKAWA WIND 1A |  | KARAKAW1_UNIT1 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 103.3
443 | KARANKAWA WIND 1B |  | KARAKAW1_UNIT2 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 103.3
444 | KARANKAWA WIND 2 |  | KARAKAW2_UNIT3 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 100.4
445 | LOS VIENTOS WIND I |  | LV1_LV1A | WILLACY | WIND-C | COASTAL | 2013 | 200.1
446 | LOS VIENTOS WIND II |  | LV1_LV1B | WILLACY | WIND-C | COASTAL | 2013 | 201.6
447 | MAGIC VALLEY WIND (REDFISH) 1A |  | REDFISH_MV1A | WILLACY | WIND-C | COASTAL | 2012 | 99.8
448 | MAGIC VALLEY WIND (REDFISH) 1B |  | REDFISH_MV1B | WILLACY | WIND-C | COASTAL | 2012 | 103.5
449 | MIDWAY WIND |  | MIDWIND_UNIT1 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 162.8
450 | PAPALOTE CREEK WIND |  | PAP1_PAP1 | SAN PATRICIO | WIND-C | COASTAL | 2009 | 179.9
451 | PAPALOTE CREEK WIND II |  | COTTON_PAP2 | SAN PATRICIO | WIND-C | COASTAL | 2010 | 200.1
452 | PENASCAL WIND 1 |  | PENA_UNIT1 | KENEDY | WIND-C | COASTAL | 2009 | 160.8
453 | PENASCAL WIND 2 |  | PENA_UNIT2 | KENEDY | WIND-C | COASTAL | 2009 | 141.6
454 | PENASCAL WIND 3 |  | PENA3_UNIT3 | KENEDY | WIND-C | COASTAL | 2011 | 100.8
455 | SAN ROMAN WIND |  | SANROMAN_WIND_1 | CAMERON | WIND-C | COASTAL | 2017 | 95.2
456 | STELLA WIND |  | STELLA_UNIT1 | KENEDY | WIND-C | COASTAL | 2018 | 201
457 | HARBOR WIND |  | DG_NUECE_6UNITS | NUECES | WIND-C | COASTAL | 2012 | 9
458 | BRISCOE WIND |  | BRISCOE_WIND | BRISCOE | WIND-P | PANHANDLE | 2015 | 149.8
459 | CANADIAN BREAKS WIND |  | CN_BRKS_UNIT_1 | OLDHAM | WIND-P | PANHANDLE | 2019 | 210.1
460 | COTTON PLAINS WIND |  | COTPLNS_COTTONPL | FLOYD | WIND-P | PANHANDLE | 2017 | 50.4
461 | DOUG COLBECK'S CORNER (CONWAY) B |  | GRANDVW1_COLB | CARSON | WIND-P | PANHANDLE | 2016 | 100.2
462 | DOUG COLBECK'S CORNER (CONWAY) A |  | GRANDVW1_COLA | CARSON | WIND-P | PANHANDLE | 2016 | 100.2
463 | FALVEZ ASTRA WIND |  | ASTRA_UNIT1 | RANDALL | WIND-P | PANHANDLE | 2017 | 163.2
464 | GRANDVIEW WIND 1 (CONWAY) GV1A |  | GRANDVW1_GV1A | CARSON | WIND-P | PANHANDLE | 2014 | 107.4
465 | GRANDVIEW WIND 1 (CONWAY) GV1B |  | GRANDVW1_GV1B | CARSON | WIND-P | PANHANDLE | 2014 | 103.8
466 | HEREFORD WIND G |  | HRFDWIND_WIND_G | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 99.9
467 | HEREFORD WIND V |  | HRFDWIND_WIND_V | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 100
468 | JUMBO ROAD WIND 1 |  | HRFDWIND_JRDWIND1 | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 146.2
469 | JUMBO ROAD WIND 2 |  | HRFDWIND_JRDWIND2 | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 153.6
470 | LONGHORN WIND NORTH U1 |  | LHORN_N_UNIT1 | FLOYD | WIND-P | PANHANDLE | 2015 | 100
471 | LONGHORN WIND NORTH U2 |  | LHORN_N_UNIT2 | FLOYD | WIND-P | PANHANDLE | 2015 | 100
472 | MARIAH DEL NORTE 1 |  | MARIAH_NORTE1 | PARMER | WIND-P | PANHANDLE | 2017 | 115.2
473 | MARIAH DEL NORTE 2 |  | MARIAH_NORTE2 | PARMER | WIND-P | PANHANDLE | 2017 | 115.2
474 | MCADOO WIND | 20INR0295 | MWEC_G1 | DICKENS | WIND-P | PANHANDLE | 2008 | 150
475 | MIAMI WIND G1 |  | MIAM1_G1 | GRAY | WIND-P | PANHANDLE | 2014 | 144.3
476 | MIAMI WIND G2 |  | MIAM1_G2 | GRAY | WIND-P | PANHANDLE | 2014 | 144.3
477 | OLD SETTLER WIND |  | COTPLNS_OLDSETLR | FLOYD | WIND-P | PANHANDLE | 2017 | 151.2
478 | PANHANDLE WIND 1 U1 |  | PH1_UNIT1 | CARSON | WIND-P | PANHANDLE | 2014 | 109.2
479 | PANHANDLE WIND 1 U2 |  | PH1_UNIT2 | CARSON | WIND-P | PANHANDLE | 2014 | 109.2
480 | PANHANDLE WIND 2 U1 |  | PH2_UNIT1 | CARSON | WIND-P | PANHANDLE | 2014 | 94.2
481 | PANHANDLE WIND 2 U2 |  | PH2_UNIT2 | CARSON | WIND-P | PANHANDLE | 2014 | 96.6
482 | ROUTE 66 WIND |  | ROUTE_66_WIND1 | CARSON | WIND-P | PANHANDLE | 2015 | 150
483 | SALT FORK 1 WIND U1 |  | SALTFORK_UNIT1 | DONLEY | WIND-P | PANHANDLE | 2017 | 64
484 | SALT FORK 1 WIND U2 |  | SALTFORK_UNIT2 | DONLEY | WIND-P | PANHANDLE | 2017 | 110
485 | SOUTH PLAINS WIND 1 U1 |  | SPLAIN1_WIND1 | FLOYD | WIND-P | PANHANDLE | 2015 | 102
486 | SOUTH PLAINS WIND 1 U2 |  | SPLAIN1_WIND2 | FLOYD | WIND-P | PANHANDLE | 2015 | 98
487 | SOUTH PLAINS WIND 2 U1 |  | SPLAIN2_WIND21 | FLOYD | WIND-P | PANHANDLE | 2016 | 148.5
488 | SOUTH PLAINS WIND 2 U2 |  | SPLAIN2_WIND22 | FLOYD | WIND-P | PANHANDLE | 2016 | 151.8
489 | SPINNING SPUR WIND TWO A |  | SSPURTWO_WIND_1 | OLDHAM | WIND-P | PANHANDLE | 2014 | 161
490 | SPINNING SPUR WIND TWO B |  | SSPURTWO_SS3WIND2 | OLDHAM | WIND-P | PANHANDLE | 2015 | 98
491 | SPINNING SPUR WIND TWO C |  | SSPURTWO_SS3WIND1 | OLDHAM | WIND-P | PANHANDLE | 2015 | 96
492 | WAKE WIND 1 |  | WAKEWE_G1 | DICKENS | WIND-P | PANHANDLE | 2016 | 114.9
493 | WAKE WIND 2 |  | WAKEWE_G2 | DICKENS | WIND-P | PANHANDLE | 2016 | 142.3
494 | WHIRLWIND ENERGY |  | WEC_WECG1 | FLOYD | WIND-P | PANHANDLE | 2007 | 57
495 | WOLF FLATS WIND (WIND MGT) |  | DG_TURL_UNIT1 | HALL | WIND-P | PANHANDLE | 2007 | 1
496 | ANACACHO WIND |  | ANACACHO_ANA | KINNEY | WIND-O | SOUTH | 2012 | 99.8
497 | BARTON CHAPEL WIND |  | BRTSW_BCW1 | JACK | WIND-O | NORTH | 2007 | 120
498 | BLUE SUMMIT WIND 1 A | 18INR0072 | BLSUMMIT_BLSMT1_5 | WILBARGER | WIND-O | WEST | 2013 | 9
499 | BLUE SUMMIT WIND 1 B | 18INR0072 | BLSUMMIT_BLSMT1_6 | WILBARGER | WIND-O | WEST | 2013 | 126.4
500 | BOBCAT BLUFF WIND | 18INR0078 | BCATWIND_WIND_1 | ARCHER | WIND-O | WEST | 2012 | 162
501 | BUCKTHORN WIND 1 A |  | BUCKTHRN_UNIT1 | ERATH | WIND-O | NORTH | 2017 | 44.9
502 | BUCKTHORN WIND 1 B |  | BUCKTHRN_UNIT2 | ERATH | WIND-O | NORTH | 2017 | 55.7
503 | BUFFALO GAP WIND 1 |  | BUFF_GAP_UNIT1 | TAYLOR | WIND-O | WEST | 2006 | 120.6
504 | BUFFALO GAP WIND 2_1 |  | BUFF_GAP_UNIT2_1 | TAYLOR | WIND-O | WEST | 2007 | 115.5
505 | BUFFALO GAP WIND 2_2 |  | BUFF_GAP_UNIT2_2 | TAYLOR | WIND-O | WEST | 2007 | 117
506 | BUFFALO GAP WIND 3 |  | BUFF_GAP_UNIT3 | TAYLOR | WIND-O | WEST | 2008 | 170.2
507 | BULL CREEK WIND U1 |  | BULLCRK_WND1 | BORDEN | WIND-O | WEST | 2009 | 88
508 | BULL CREEK WIND U2 |  | BULLCRK_WND2 | BORDEN | WIND-O | WEST | 2009 | 90
509 | CABEZON WIND (RIO BRAVO I WIND) 1 A |  | CABEZON_WIND1 | STARR | WIND-O | SOUTH | 2019 | 115.2
510 | CABEZON WIND (RIO BRAVO I WIND) 1 B |  | CABEZON_WIND2 | STARR | WIND-O | SOUTH | 2019 | 122.4
511 | CALLAHAN WIND |  | CALLAHAN_WND1 | CALLAHAN | WIND-O | WEST | 2004 | 114
512 | CAMP SPRINGS WIND 1 |  | CSEC_CSECG1 | SCURRY | WIND-O | WEST | 2007 | 130.5
513 | CAMP SPRINGS WIND 2 |  | CSEC_CSECG2 | SCURRY | WIND-O | WEST | 2007 | 120
514 | CAPRICORN RIDGE WIND 1 | 17INR0054 | CAPRIDGE_CR1 | STERLING | WIND-O | WEST | 2007 | 214.5
515 | CAPRICORN RIDGE WIND 2 | 17INR0054 | CAPRIDGE_CR2 | STERLING | WIND-O | WEST | 2007 | 149.5
516 | CAPRICORN RIDGE WIND 3 | 17INR0054 | CAPRIDGE_CR3 | STERLING | WIND-O | WEST | 2008 | 186
517 | CAPRICORN RIDGE WIND 4 | 17INR0061 | CAPRIDG4_CR4 | COKE | WIND-O | WEST | 2008 | 121.5
518 | CEDRO HILL WIND 1 |  | CEDROHIL_CHW1 | WEBB | WIND-O | SOUTH | 2010 | 75
519 | CEDRO HILL WIND 2 |  | CEDROHIL_CHW2 | WEBB | WIND-O | SOUTH | 2010 | 75
520 | CHAMPION WIND |  | CHAMPION_UNIT1 | NOLAN | WIND-O | WEST | 2008 | 126.5
521 | DERMOTT WIND 1_1 |  | DERMOTT_UNIT1 | SCURRY | WIND-O | WEST | 2017 | 126.5
522 | DERMOTT WIND 1_2 |  | DERMOTT_UNIT2 | SCURRY | WIND-O | WEST | 2017 | 126.5
523 | DESERT SKY WIND 1 | 17INR0070 | INDNENR_INDNENR | PECOS | WIND-O | WEST | 2002 | 85.1
524 | DESERT SKY WIND 2 | 17INR0070 | INDNENR_INDNENR_2 | PECOS | WIND-O | WEST | 2002 | 85.1
525 | ELBOW CREEK WIND |  | ELB_ELBCREEK | HOWARD | WIND-O | WEST | 2008 | 118.7
526 | ELECTRA WIND 1 |  | DIGBY_UNIT1 | WILBARGER | WIND-O | WEST | 2017 | 98.9
527 | ELECTRA WIND 2 |  | DIGBY_UNIT2 | WILBARGER | WIND-O | WEST | 2017 | 131.1
528 | FLAT TOP WIND I |  | FTWIND_UNIT_1 | MILLS | WIND-O | NORTH | 2018 | 200
529 | FLUVANNA RENEWABLE 1 A |  | FLUVANNA_UNIT1 | SCURRY | WIND-O | WEST | 2017 | 79.8
530 | FLUVANNA RENEWABLE 1 B |  | FLUVANNA_UNIT2 | SCURRY | WIND-O | WEST | 2017 | 75.6
531 | FOARD CITY WIND 1 A |  | FOARDCTY_UNIT1 | FOARD | WIND-O | WEST | 2019 | 186.5
532 | FOARD CITY WIND 1 B |  | FOARDCTY_UNIT2 | FOARD | WIND-O | WEST | 2019 | 163.8
533 | FOREST CREEK WIND |  | MCDLD_FCW1 | GLASSCOCK | WIND-O | WEST | 2007 | 124.2
534 | GOAT WIND |  | GOAT_GOATWIND | STERLING | WIND-O | WEST | 2008 | 80
535 | GOAT WIND 2 |  | GOAT_GOATWIN2 | STERLING | WIND-O | WEST | 2010 | 69.6
536 | GOLDTHWAITE WIND 1 |  | GWEC_GWEC_G1 | MILLS | WIND-O | NORTH | 2014 | 148.6
537 | GREEN MOUNTAIN WIND (BRAZOS) U1 |  | BRAZ_WND_WND1 | SCURRY | WIND-O | WEST | 2003 | 99
538 | GREEN MOUNTAIN WIND (BRAZOS) U2 |  | BRAZ_WND_WND2 | SCURRY | WIND-O | WEST | 2003 | 61
539 | GREEN PASTURES WIND I |  | GPASTURE_WIND_I | BAYLOR | WIND-O | WEST | 2015 | 150
540 | VERTIGO WIND (FORMERLY GREEN PASTURES WIND 2) |  | VERTIGO_WIND_I | BAYLOR | WIND-O | WEST | 2015 | 150
541 | GUNSIGHT MOUNTAIN WIND |  | GUNMTN_G1 | HOWARD | WIND-O | WEST | 2016 | 119.9
542 | HACKBERRY WIND |  | HWF_HWFG1 | SHACKELFORD | WIND-O | WEST | 2008 | 163.5
543 | HICKMAN (SANTA RITA WIND) 1 |  | HICKMAN_G1 | REGAN AND IRION | WIND-O | WEST | 2018 | 152.5
544 | HICKMAN (SANTA RITA WIND) 2 |  | HICKMAN_G2 | REGAN AND IRION | WIND-O | WEST | 2018 | 147.5
545 | HIDALGO & STARR WIND 11 |  | MIRASOLE_MIR11 | HIDALGO | WIND-O | SOUTH | 2016 | 52
546 | HIDALGO & STARR WIND 12 |  | MIRASOLE_MIR12 | HIDALGO | WIND-O | SOUTH | 2016 | 98
547 | HIDALGO & STARR WIND 21 |  | MIRASOLE_MIR21 | HIDALGO | WIND-O | SOUTH | 2016 | 100
548 | HORSE CREEK WIND 1 |  | HORSECRK_UNIT1 | HASKELL | WIND-O | WEST | 2017 | 131.1
549 | HORSE CREEK WIND 2 |  | HORSECRK_UNIT2 | HASKELL | WIND-O | WEST | 2017 | 98.9
550 | HORSE HOLLOW WIND 1 | 17INR0052 | H_HOLLOW_WND1 | TAYLOR | WIND-O | WEST | 2019 | 230
551 | HORSE HOLLOW WIND 2 | 17INR0052 | HHOLLOW2_WIND1 | TAYLOR | WIND-O | WEST | 2006 | 184
552 | HORSE HOLLOW WIND 3 | 17INR0052 | HHOLLOW3_WND_1 | TAYLOR | WIND-O | WEST | 2006 | 223.5
553 | HORSE HOLLOW WIND 4 | 17INR0052 | HHOLLOW4_WND1 | TAYLOR | WIND-O | WEST | 2006 | 115
554 | INADALE WIND 1 |  | INDL_INADALE1 | NOLAN | WIND-O | WEST | 2008 | 95
555 | INADALE WIND 2 |  | INDL_INADALE2 | NOLAN | WIND-O | WEST | 2008 | 102
556 | INDIAN MESA WIND |  | INDNNWP_INDNNWP2 | PECOS | WIND-O | WEST | 2001 | 91.9
557 | JAVELINA I WIND 18 |  | BORDAS_JAVEL18 | WEBB | WIND-O | SOUTH | 2015 | 19.7
558 | JAVELINA I WIND 20 |  | BORDAS_JAVEL20 | WEBB | WIND-O | SOUTH | 2015 | 230
559 | JAVELINA II WIND 1 |  | BORDAS2_JAVEL2_A | WEBB | WIND-O | SOUTH | 2017 | 96
560 | JAVELINA II WIND 2 |  | BORDAS2_JAVEL2_B | WEBB | WIND-O | SOUTH | 2017 | 74
561 | JAVELINA II WIND 3 |  | BORDAS2_JAVEL2_C | WEBB | WIND-O | SOUTH | 2017 | 30
562 | KEECHI WIND |  | KEECHI_U1 | JACK | WIND-O | NORTH | 2015 | 110
563 | KING MOUNTAIN WIND (NE) |  | KING_NE_KINGNE | UPTON | WIND-O | WEST | 2001 | 79.7
564 | KING MOUNTAIN WIND (NW) |  | KING_NW_KINGNW | UPTON | WIND-O | WEST | 2001 | 79.7
565 | KING MOUNTAIN WIND (SE) |  | KING_SE_KINGSE | UPTON | WIND-O | WEST | 2001 | 40.5
566 | KING MOUNTAIN WIND (SW) |  | KING_SW_KINGSW | UPTON | WIND-O | WEST | 2001 | 79.7
567 | LANGFORD WIND POWER |  | LGD_LANGFORD | TOM GREEN | WIND-O | WEST | 2009 | 155
568 | LOCKETT WIND FARM |  | LOCKETT_UNIT1 | WILBARGER | WIND-O | WEST | 2019 | 183.7
569 | LOGANS GAP WIND I U1 |  | LGW_UNIT1 | COMANCHE | WIND-O | NORTH | 2015 | 106.3
570 | LOGANS GAP WIND I U2 |  | LGW_UNIT2 | COMANCHE | WIND-O | NORTH | 2015 | 103.8
571 | LONE STAR WIND 1 (MESQUITE) |  | LNCRK_G83 | SHACKELFORD | WIND-O | WEST | 2006 | 200
572 | LONE STAR WIND 2 (POST OAK) U1 |  | LNCRK2_G871 | SHACKELFORD | WIND-O | WEST | 2007 | 100
573 | LONE STAR WIND 2 (POST OAK) U2 |  | LNCRK2_G872 | SHACKELFORD | WIND-O | WEST | 2007 | 100
574 | LORAINE WINDPARK I |  | LONEWOLF_G1 | MITCHELL | WIND-O | WEST | 2010 | 49.5
575 | LORAINE WINDPARK II |  | LONEWOLF_G2 | MITCHELL | WIND-O | WEST | 2010 | 51
576 | LORAINE WINDPARK III |  | LONEWOLF_G3 | MITCHELL | WIND-O | WEST | 2011 | 25.5
577 | LORAINE WINDPARK IV |  | LONEWOLF_G4 | MITCHELL | WIND-O | WEST | 2011 | 24
578 | LOS VIENTOS III WIND |  | LV3_UNIT_1 | STARR | WIND-O | SOUTH | 2015 | 200
579 | LOS VIENTOS IV WIND |  | LV4_UNIT_1 | STARR | WIND-O | SOUTH | 2016 | 200
580 | LOS VIENTOS V WIND |  | LV5_UNIT_1 | STARR | WIND-O | SOUTH | 2016 | 110
581 | MESQUITE CREEK WIND 1 |  | MESQCRK_WND1 | DAWSON | WIND-O | WEST | 2015 | 105.6
582 | MESQUITE CREEK WIND 2 |  | MESQCRK_WND2 | DAWSON | WIND-O | WEST | 2015 | 105.6
583 | NIELS BOHR WIND A (BEARKAT WIND A) |  | NBOHR_UNIT1 | GLASSCOCK | WIND-O | WEST | 2018 | 196.6
584 | NOTREES WIND 1 |  | NWF_NWF1 | WINKLER | WIND-O | WEST | 2009 | 92.6
585 | NOTREES WIND 2 |  | NWF_NWF2 | WINKLER | WIND-O | WEST | 2009 | 60
586 | OCOTILLO WIND |  | OWF_OWF | HOWARD | WIND-O | WEST | 2008 | 58.8
587 | PANTHER CREEK WIND 1 |  | PC_NORTH_PANTHER1 | HOWARD | WIND-O | WEST | 2008 | 142.5
588 | PANTHER CREEK WIND 2 |  | PC_SOUTH_PANTHER2 | HOWARD | WIND-O | WEST | 2019 | 115.5
589 | PANTHER CREEK WIND 3 | 21INR0449 | PC_SOUTH_PANTHER3 | HOWARD | WIND-O | WEST | 2009 | 199.5
590 | PECOS WIND 1 (WOODWARD) |  | WOODWRD1_WOODWRD1 | PECOS | WIND-O | WEST | 2001 | 91.9
591 | PECOS WIND 2 (WOODWARD) |  | WOODWRD2_WOODWRD2 | PECOS | WIND-O | WEST | 2001 | 86
592 | PYRON WIND 1 |  | PYR_PYRON1 | SCURRY | WIND-O | WEST | 2008 | 121.5
593 | PYRON WIND 2 |  | PYR_PYRON2 | SCURRY AND FISHER | WIND-O | WEST | 2008 | 127.5
594 | RATTLESNAKE I WIND ENERGY CENTER G1 |  | RSNAKE_G1 | GLASSCOCK | WIND-O | WEST | 2015 | 104.3
595 | RATTLESNAKE I WIND ENERGY CENTER G2 |  | RSNAKE_G2 | GLASSCOCK | WIND-O | WEST | 2015 | 103
596 | RED CANYON WIND |  | RDCANYON_RDCNY1 | BORDEN | WIND-O | WEST | 2006 | 89.6
597 | ROCK SPRINGS VAL VERDE WIND (FERMI) 1 |  | FERMI_WIND1 | VAL VERDE | WIND-O | WEST | 2017 | 121.9
598 | ROCK SPRINGS VAL VERDE WIND (FERMI) 2 |  | FERMI_WIND2 | VAL VERDE | WIND-O | WEST | 2017 | 27.4
599 | ROSCOE WIND |  | TKWSW1_ROSCOE | NOLAN | WIND-O | WEST | 2008 | 114
600 | ROSCOE WIND 2A |  | TKWSW1_ROSCOE2A | NOLAN | WIND-O | WEST | 2008 | 95
601 | RTS WIND |  | RTS_U1 | MCCULLOCH | WIND-O | SOUTH | 2018 | 160
602 | SAND BLUFF WIND | 20INR0296 | MCDLD_SBW1 | GLASSCOCK | WIND-O | WEST | 2008 | 90
603 | SENDERO WIND ENERGY |  | EXGNSND_WIND_1 | JIM HOGG | WIND-O | SOUTH | 2015 | 76
604 | SEYMOUR HILLS WIND (S_HILLS WIND) |  | S_HILLS_UNIT1 | BAYLOR | WIND-O | WEST | 2019 | 30.2
605 | SENATE WIND |  | SENATEWD_UNIT1 | JACK | WIND-O | NORTH | 2012 | 150
606 | SHANNON WIND |  | SHANNONW_UNIT_1 | CLAY | WIND-O | WEST | 2015 | 204.1
607 | SHERBINO 1 WIND | 19INR0120 | KEO_KEO_SM1 | PECOS | WIND-O | WEST | 2008 | 150
608 | SHERBINO 2 WIND | 19INR0120 | KEO_SHRBINO2 | PECOS | WIND-O | WEST | 2011 | 145
609 | SILVER STAR WIND | 18INR0064 | FLTCK_SSI | EASTLAND | WIND-O | NORTH | 2008 | 60
610 | SNYDER WIND | 20INR0257 | ENAS_ENA1 | SCURRY | WIND-O | WEST | 2007 | 63
611 | SOUTH TRENT WIND |  | STWF_T1 | NOLAN | WIND-O | WEST | 2008 | 98.2
612 | STANTON WIND ENERGY |  | SWEC_G1 | MARTIN | WIND-O | WEST | 2008 | 120
613 | STEPHENS RANCH WIND 1 |  | SRWE1_UNIT1 | BORDEN | WIND-O | WEST | 2014 | 211.2
614 | STEPHENS RANCH WIND 2 |  | SRWE1_SRWE2 | BORDEN | WIND-O | WEST | 2015 | 164.7
615 | SWEETWATER WIND 1 | 18INR0073 | SWEETWND_WND1 | NOLAN | WIND-O | WEST | 2003 | 42.5
616 | SWEETWATER WIND 2A | 17INR0068 | SWEETWN2_WND24 | NOLAN | WIND-O | WEST | 2006 | 16.8
617 | SWEETWATER WIND 2B | 17INR0068 | SWEETWN2_WND2 | NOLAN | WIND-O | WEST | 2004 | 110.8
618 | SWEETWATER WIND 3A |  | SWEETWN3_WND3A | NOLAN | WIND-O | WEST | 2011 | 34
619 | SWEETWATER WIND 3B |  | SWEETWN3_WND3B | NOLAN | WIND-O | WEST | 2011 | 117
620 | SWEETWATER WIND 4-5 |  | SWEETWN4_WND5 | NOLAN | WIND-O | WEST | 2007 | 85
621 | SWEETWATER WIND 4-4B |  | SWEETWN4_WND4B | NOLAN | WIND-O | WEST | 2007 | 112
622 | SWEETWATER WIND 4-4A |  | SWEETWN4_WND4A | NOLAN | WIND-O | WEST | 2007 | 125
623 | TAHOKA WIND 1 |  | TAHOKA_UNIT_1 | LYNN | WIND-O | WEST | 2019 | 150
624 | TAHOKA WIND 2 |  | TAHOKA_UNIT_2 | LYNN | WIND-O | WEST | 2019 | 150
625 | TEXAS BIG SPRING WIND A |  | SGMTN_SIGNALMT | HOWARD | WIND-O | WEST | 1999 | 27.7
626 | TEXAS BIG SPRING WIND B |  | SGMTN_SIGNALM2 | HOWARD | WIND-O | WEST | 1999 | 6.6
627 | TORRECILLAS WIND 1 |  | TORR_UNIT1_25 | WEBB | WIND-O | SOUTH | 2019 | 150
628 | TORRECILLAS WIND 2 |  | TORR_UNIT2_23 | WEBB | WIND-O | SOUTH | 2019 | 23
629 | TORRECILLAS WIND 3 |  | TORR_UNIT2_25 | WEBB | WIND-O | SOUTH | 2019 | 127.5
630 | TRENT WIND | 17INR0069 | TRENT_TRENT | NOLAN | WIND-O | WEST | 2001 | 150
631 | TRINITY HILLS WIND 1 | 20INR0019 | TRINITY_TH1_BUS1 | YOUNG | WIND-O | WEST | 2012 | 117.5
632 | TRINITY HILLS WIND 2 | 20INR0019 | TRINITY_TH1_BUS2 | YOUNG | WIND-O | WEST | 2012 | 107.5
633 | TURKEY TRACK WIND |  | TTWEC_G1 | NOLAN | WIND-O | WEST | 2008 | 169.5
634 | TYLER BLUFF WIND |  | TYLRWIND_UNIT1 | COOKE | WIND-O | NORTH | 2017 | 125.6
635 | WHITETAIL WIND |  | EXGNWTL_WIND_1 | WEBB | WIND-O | SOUTH | 2012 | 92.3
636 | WINDTHORST 2 WIND |  | WNDTHST2_UNIT1 | ARCHER | WIND-O | WEST | 2014 | 67.6
637 | WKN MOZART WIND |  | MOZART_WIND_1 | KENT | WIND-O | WEST | 2012 | 30
638 | WILLOW SPRINGS WIND A |  | SALVTION_UNIT1 | HASKELL | WIND-O | WEST | 2017 | 125
639 | WILLOW SPRINGS WIND B |  | SALVTION_UNIT2 | HASKELL | WIND-O | WEST | 2017 | 125
640 | WOLF RIDGE WIND |  | WHTTAIL_WR1 | COOKE | WIND-O | NORTH | 2008 | 112.5
641 | TSTC WEST TEXAS WIND |  | DG_ROSC2_1UNIT | NOLAN | WIND-O | WEST | 2008 | 2
642 | Operational Capacity Total (Wind) | [6 empty] | 23864.8
643
644 | Operational Wind Capacity Sub-total (Coastal Counties) |  | WIND_OPERATIONAL_C |  |  |  |  | 3290.4
645 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PEAK_PCT_C | % |  |  |  | 66
646
647 | Operational Wind Capacity Sub-total (Panhandle Counties) |  | WIND_OPERATIONAL_P |  |  |  |  | 4408.7
648 | Wind Peak Average Capacity Percentage (Panhandle) |  | WIND_PEAK_PCT_P |  |  |  |  | 36
649
650 | Operational Wind Capacity Sub-total (Other Counties) |  | WIND_OPERATIONAL_O |  |  |  |  | 16165.7
651 | Wind Peak Average Capacity Percentage (Other) |  | WIND_PEAK_PCT_O |  |  |  |  | 34
652
653 | Operational Resources (Solar)
654 | ACACIA SOLAR |  | ACACIA_UNIT_1 | PRESIDIO | SOLAR | WEST | 2012 | 10
655 | BHE SOLAR PEARL PROJECT (SIRIUS 2) |  | SIRIUS_UNIT2 | PECOS | SOLAR | WEST | 2017 | 49.1
656 | BLUEBELL SOLAR (CAPRICORN RIDGE SOLAR) |  | CAPRIDG4_BB_PV | STERLING | SOLAR | WEST | 2019 | 30
657 | BNB LAMESA SOLAR (PHASE I) |  | LMESASLR_UNIT1 | DAWSON | SOLAR | WEST | 2018 | 101.6
658 | BNB LAMESA SOLAR (PHASE II) |  | LMESASLR_IVORY | DAWSON | SOLAR | WEST | 2018 | 50
659 | CASTLE GAP SOLAR |  | CASL_GAP_UNIT1 | UPTON | SOLAR | WEST | 2018 | 180
660 | FS BARILLA SOLAR-PECOS |  | HOVEY_UNIT1 | PECOS | SOLAR | WEST | 2015 | 22
661 | FS EAST PECOS SOLAR |  | BOOTLEG_UNIT1 | PECOS | SOLAR | WEST | 2017 | 121.1
662 | OCI ALAMO 1 SOLAR |  | OCI_ALM1_UNIT1 | BEXAR | SOLAR | SOUTH | 2013 | 39.2
663 | OCI ALAMO 4 SOLAR-BRACKETVILLE |  | ECLIPSE_UNIT1 | KINNEY | SOLAR | SOUTH | 2014 | 37.6
664 | OCI ALAMO 5 (DOWNIE RANCH) |  | HELIOS_UNIT1 | UVALDE | SOLAR | SOUTH | 2015 | 95
665 | OCI ALAMO 6 (SIRIUS/WEST TEXAS) |  | SIRIUS_UNIT1 | PECOS | SOLAR | WEST | 2017 | 110.2
666 | OCI ALAMO 7 (PAINT CREEK) |  | SOLARA_UNIT1 | HASKELL | SOLAR | WEST | 2016 | 112
667 | PHOEBE SOLAR 1 |  | PHOEBE_UNIT1 | WINKLER | SOLAR | WEST | 2019 | 125.1
668 | PHOEBE SOLAR 2 |  | PHOEBE_UNIT2 | WINKLER | SOLAR | WEST | 2019 | 128.1
669 | RE ROSEROCK SOLAR 1 |  | REROCK_UNIT1 | PECOS | SOLAR | WEST | 2016 | 78.8
670 | RE ROSEROCK SOLAR 2 |  | REROCK_UNIT2 | PECOS | SOLAR | WEST | 2016 | 78.8
671 | RIGGINS (SE BUCKTHORN WESTEX SOLAR) |  | RIGGINS_UNIT1 | PECOS | SOLAR | WEST | 2018 | 150
672 | SOLAIREHOLMAN 1 |  | LASSO_UNIT1 | BREWSTER | SOLAR | WEST | 2018 | 50
673 | SP-TX-12-PHASE B |  | SPTX12B_UNIT1 | UPTON | SOLAR | WEST | 2017 | 157.5
674 | WAYMARK SOLAR |  | WAYMARK_UNIT1 | UPTON | SOLAR | WEST | 2018 | 182
675 | WEBBERVILLE SOLAR |  | WEBBER_S_WSP1 | TRAVIS | SOLAR | SOUTH | 2011 | 26.7
676 | WEST OF PECOS SOLAR |  | W_PECOS_UNIT1 | REEVES | SOLAR | WEST | 2019 | 101
677 | ALEXIS SOLAR |  | DG_ALEXIS_ALEXIS | BROOKS | SOLAR | SOUTH | 2019 | 10
678 | BECK 1 |  | DG_CECSOLAR_DG_BECK1 | BEXAR | SOLAR | SOUTH | 2016 | 1
679 | BLUE WING 1 SOLAR |  | DG_BROOK_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.6
680 | BLUE WING 2 SOLAR |  | DG_ELMEN_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.3
681 | BOVINE SOLAR LLC |  | DG_BOVINE_BOVINE | AUSTIN | SOLAR | SOUTH | 2018 | 5
682 | BOVINE SOLAR LLC |  | DG_BOVINE2_BOVINE2 | AUSTIN | SOLAR | SOUTH | 2018 | 5
683 | BRONSON SOLAR I |  | DG_BRNSN_BRNSN | FORT BEND | SOLAR | HOUSTON | 2018 | 5
684 | BRONSON SOLAR II |  | DG_BRNSN2_BRNSN2 | FORT BEND | SOLAR | HOUSTON | 2018 | 5
685 | CASCADE SOLAR I |  | DG_CASCADE_CASCADE | WHARTON | SOLAR | SOUTH | 2018 | 5
686 | CASCADE SOLAR II |  | DG_CASCADE2_CASCADE2 | WHARTON | SOLAR | SOUTH | 2018 | 5
687 | CHISUM SOLAR |  | DG_CHISUM_CHISUM | LAMAR | SOLAR | NORTH | 2018 | 10
688 | COMMERCE_SOLAR |  | DG_ X443PV1_SWRI_PV1 | BEXAR | SOLAR | SOUTH | 2019 | 5
689 | EDDY SOLAR II |  | DG_EDDYII_EDDYII | MCLENNAN | SOLAR | NORTH | 2018 | 10
690 | FIFTH GENERATION SOLAR 1 |  | DG_FGSOLAR1 | TRAVIS | SOLAR | SOUTH | 2016 | 1.6
691 | GRIFFIN SOLAR |  | DG_GRIFFIN_GRIFFIN | MCLEENNAN | SOLAR | NORTH | 2019 | 5
692 | HIGHWAY 56 |  | DG_HWY56_HWY56 | GRAYSON | SOLAR | NORTH | 2017 | 5.3
693 | HM SEALY SOLAR 1 |  | DG_SEALY_1UNIT | AUSTIN | SOLAR | SOUTH | 2015 | 1.6
694 | LAMPWICK SOLAR |  | DG_LAMPWICK_LAMPWICK | MENARD | SOLAR | SOUTH | 2019 | 7.5
695 | LEON |  | DG_LEON_LEON | HUNT | SOLAR | NORTH | 2017 | 10
696 | MARLIN |  | DG_MARLIN_MARLIN | FALLS | SOLAR | NORTH | 2017 | 5.3
697 | MARS SOLAR (DG) |  | DG_MARS_MARS | WEBB | SOLAR | SOUTH | 2019 | 10
698 | NORTH GAINESVILLE |  | DG_NGNSVL_NGAINESV | COOKE | SOLAR | NORTH | 2017 | 5.2
699 | OCI ALAMO 2 SOLAR-ST. HEDWIG |  | DG_STHWG_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 4.4
700 | OCI ALAMO 3-WALZEM SOLAR |  | DG_WALZM_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 5.5
701 | POWERFIN KINGSBERY |  | DG_PFK_PFKPV | TRAVIS | SOLAR | SOUTH | 2017 | 2.6
702 | RENEWABLE ENERGY ALTERNATIVES-CCS1 |  | DG_COSERVSS_CCS1 | DENTON | SOLAR | NORTH | 2015 | 2
703 | STERLING |  | DG_STRLING_STRLING | HUNT | SOLAR | NORTH | 2018 | 10
704 | SUNEDISON RABEL ROAD SOLAR |  | DG_VALL1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9
705 | SUNEDISON VALLEY ROAD SOLAR |  | DG_VALL2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9
706 | SUNEDISON CPS3 SOMERSET 1 SOLAR |  | DG_SOME1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5.6
707 | SUNEDISON SOMERSET 2 SOLAR |  | DG_SOME2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5
708 | WALNUT SPRINGS |  | DG_WLNTSPRG_1UNIT | BOSQUE | SOLAR | NORTH | 2016 | 10
709 | WEST MOORE II |  | DG_WMOOREII_WMOOREII | GRAYSON | SOLAR | NORTH | 2018 | 5
710 | WHITESBORO |  | DG_WBORO_WHTSBORO | GRAYSON | SOLAR | NORTH | 2017 | 5
711 | WHITESBORO II |  | DG_WBOROII_WHBOROII | GRAYSON | SOLAR | NORTH | 2017 | 5
712 | WHITEWRIGHT |  | DG_WHTRT_WHTRGHT | FANNIN | SOLAR | NORTH | 2017 | 10
713 | WHITNEY SOLAR |  | DG_WHITNEY_SOLAR1 | BOSQUE | SOLAR | NORTH | 2017 | 10
714 | YELLOW JACKET SOLAR |  | DG_YLWJACKET_YLWJACKET | BOSQUE | SOLAR | NORTH | 2018 | 5
715 | Operational Capacity Total (Solar) | [6 empty] | 2273.1
716 | Solar Peak Average Capacity Percentage |  | SOLAR_PEAK_PCT | % |  |  |  | 62
717
718 | Operational Resources (Storage)
719 | BLUE SUMMIT BATTERY |  | BLSUMMIT_BATTERY | WILBARGER | STORAGE | WEST | 2017 | 30
720 | CASTLE GAP BATTERY |  | CASL_GAP_BATTERY1 | UPTON | STORAGE | WEST | 2019 | 9.9
721 | INADALE ESS |  | INDL_ESS | NOLAN | STORAGE | WEST | 2018 | 9.9
722 | NOTREES BATTERY FACILITY |  | NWF_NBS | WINKLER | STORAGE | WEST | 2013 | 33.7
723 | OCI ALAMO 1 |  | OCI_ALM1_ASTRO1 | BEXAR | STORAGE | SOUTH | 2016 | 1
724 | PORT LAVACA BATTERY |  | PTLBES_BESS1 | CALHOUN | STORAGE | SOUTH | 2019 | 9.9
725 | PROSPECT STORAGE |  | WCOLLDG_BSS_U1 | BRAZORIA | STORAGE | HOUSTON | 2019 | 9.9
726 | PYRON ESS |  | PYR_ESS | SCURRY | STORAGE | WEST | 2018 | 9.9
727 | YOUNICOS FACILITY |  | YOUNICOS_YINC1_1 | TRAVIS | STORAGE | SOUTH | 2015 | 2
728 | KINGSBERY ENERGY STORAGE SYSTEM |  | DG_KB_ESS_KB_ESS | TRAVIS | STORAGE | SOUTH | 2017 | 1.5
729 | MU ENERGY STORAGE SYSTEM |  | DG_MU_ESS_MU_ESS | TRAVIS | STORAGE | SOUTH | 2018 | 1.5
730 | TOS BATTERY STORAGE |  | DG_TOSBATT_UNIT1 | MIDLAND | STORAGE | WEST | 2017 | 2
731 | Operational Capacity Total (Storage) | [6 empty] | 121.2
732 | Storage Peak Average Capacity Percentage |  | STORAGE_PEAK_PCT | % |  |  |  | 0
733
734 | Reliability Must-Run (RMR) Capacity |  | RMR_CAP_CONT |  |  |  |  | 0
735
736 | Capacity Pending Retirement |  | PENDRETIRE_CAP |  |  |  |  | 0
737
738 | Non-Synchronous Tie Resources
739 | EAST TIE |  | DC_E | FANNIN | OTHER | NORTH |  | 600
740 | NORTH TIE |  | DC_N | WILBARGER | OTHER | WEST |  | 220
741 | EAGLE PASS TIE |  | DC_S | MAVERICK | OTHER | SOUTH |  | 30
742 | LAREDO VFT TIE |  | DC_L | WEBB | OTHER | SOUTH |  | 100
743 | SHARYLAND RAILROAD TIE |  | DC_R | HIDALGO | OTHER | SOUTH |  | 300
744 | Non-Synchronous Ties Total | [6 empty] | 1250
745 | Non-Synchronous Ties Peak Average Capacity Percentage |  | DCTIE_PEAK_PCT | % |  |  |  | 67
746
747 | Planned Thermal Resources with Executed SGIA, Air Permit, GHG Permit and Proof of Adequate Water Supplies
748 | FRIENDSWOOD II | 19INR0180 |  | BRAZORIA | GAS | COASTAL | 2021 | 0
749 | HALYARD WHARTON ENERGY CENTER | 16INR0044 |  | WHARTON | GAS | SOUTH | 2021 | 0
750 | HUDSON (BRAZORIA ENERGY G) | 16INR0076 |  | BRAZORIA | GAS | COASTAL | 2020 | 96
751 | MIRAGE | 17INR0022 |  | HARRIS | GAS | HOUSTON | 2020 | 0
752 | PES1 | 20INR0206 |  | HARRIS | GAS | HOUSTON | 2020 | 0
753 | Planned Capacity Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 96
754
755 | Planned Wind Resources with Executed SGIA
756 | CHALUPA WIND | 20INR0042 |  | CAMERON | WIND-C | COASTAL | 2020 | 0
757 | CHOCOLATE BAYOU W | 16INR0074 |  | BRAZORIA | WIND-C | COASTAL | 2021 | 0
758 | CRANEL WIND | 19INR0112 |  | REFUGIO | WIND-C | COASTAL | 2020 | 0
759 | EAST RAYMOND WIND | 18INR0059 |  | WILLACY | WIND-C | COASTAL | 2020 | 0
760 | ESPIRITU WIND | 17INR0031 |  | CAMERON | WIND-C | COASTAL | 2020 | 0
761 | LAS MAJADAS WIND | 17INR0035 |  | WILLACY | WIND-C | COASTAL | 2020 | 0
762 | MONTE ALTO I | 19INR0022 |  | WILLACY | WIND-C | COASTAL | 2021 | 0
763 | PALMAS ALTAS WIND | 17INR0037 |  | CAMERON | WIND-C | COASTAL | 2020 | 144.9
764 | PEYTON CREEK WIND | 18INR0018 |  | MATAGORDA | WIND-C | COASTAL | 2020 | 151.2
765 | SHAFFER (PATRIOT WIND/PETRONILLA) | 11INR0062 |  | NUECES | WIND-C | COASTAL | 2020 | 226
766 | WEST RAYMOND (EL TRUENO) WIND | 20INR0088 |  | WILLACY | WIND-C | COASTAL | 2020 | 0
767 | GOODNIGHT WIND | 14INR0033 |  | ARMSTRONG | WIND-P | PANHANDLE | 2020 | 0
768 | HART WIND | 16INR0033 |  | CASTRO | WIND-P | PANHANDLE | 2021 | 0
769 | MARIAH DEL ESTE | 13INR0010a |  | PARMER | WIND-P | PANHANDLE | 2020 | 0
770 | NORTHDRAW WIND | 13INR0025 |  | RANDALL | WIND-P | PANHANDLE | 2020 | 0
771 | PANHANDLE WIND 3 | 14INR0030c |  | CARSON | WIND-P | PANHANDLE | 2022 | 0
772 | PUMPKIN FARM WIND | 16INR0037c |  | FLOYD | WIND-P | PANHANDLE | 2020 | 0
773 | WILDROSE WIND (SWISHER WIND) | 13INR0038 |  | SWISHER | WIND-P | PANHANDLE | 2021 | 0
774 | AVIATOR WIND | 19INR0156 |  | COKE | WIND-O | WEST | 2020 | 0
775 | BAIRD NORTH WIND | 20INR0083 |  | CALLAHAN | WIND-O | WEST | 2021 | 0
776 | BARROW RANCH (JUMBO HILL WIND) | 18INR0038 |  | ANDREWS | WIND-O | WEST | 2020 | 160
777 | BIG SAMPSON WIND | 16INR0104 |  | CROCKETT | WIND-O | WEST | 2021 | 0
778 | BLACKJACK CREEK WIND | 20INR0068 |  | BEE | WIND-O | SOUTH | 2021 | 0
779 | BLUE SUMMIT WIND 2 | 18INR0070 |  | WILBARGER | WIND-O | WEST | 2020 | 0
780 | BLUE SUMMIT WIND 3 | 19INR0182 |  | WILBARGER | WIND-O | WEST | 2020 | 0
781 | CACTUS FLATS WIND | 16INR0086 |  | CONCHO | WIND-O | WEST | 2020 | 0
782 | CANYON WIND | 18INR0030 |  | SCURRY | WIND-O | WEST | 2021 | 0
783 | COYOTE WIND | 17INR0027b |  | SCURRY | WIND-O | WEST | 2020 | 0
784 | EDMONDSON RANCH WIND | 18INR0043 |  | GLASSCOCK | WIND-O | WEST | 2021 | 0
785 | GOPHER CREEK WIND | 18INR0067 |  | BORDEN | WIND-O | WEST | 2020 | 158
786 | GRIFFIN TRAIL WIND | 20INR0052 |  | KNOX | WIND-O | WEST | 2020 | 0
787 | HARALD (BEARKAT WIND B) | 15INR0064b |  | GLASSCOCK | WIND-O | WEST | 2020 | 0
788 | HIDALGO II WIND | 19INR0053 |  | HIDALGO | WIND-O | SOUTH | 2020 | 51
789 | HIGH LONESOME W | 19INR0038 |  | CROCKETT | WIND-O | WEST | 2019 | 449.5
790 | HIGH LONESOME WIND PHASE II | 20INR0262 |  | CROCKETT | WIND-O | WEST | 2020 | 50.6
791 | KAISER CREEK WIND | 18INR0042 |  | CALLAHAN | WIND-O | WEST | 2020 | 0
792 | KONTIKI 1 WIND (ERIK) | 19INR0099a |  | GLASSCOCK | WIND-O | WEST | 2021 | 0
793 | KONTIKI 2 WIND (ERNEST) | 19INR0099b |  | GLASSCOCK | WIND-O | WEST | 2022 | 0
794 | LAS LOMAS WIND | 16INR0111 |  | STARR | WIND-O | SOUTH | 2020 | 0
795 | LOMA PINTA WIND | 16INR0112 |  | LA SALLE | WIND-O | SOUTH | 2020 | 0
796 | LORAINE WINDPARK PHASE III | 18INR0068 |  | MITCHELL | WIND-O | WEST | 2021 | 0
797 | MARYNEAL WINDPOWER | 18INR0031 |  | NOLAN | WIND-O | WEST | 2021 | 0
798 | MAVERICK CREEK I | 20INR0045 |  | CONCHO | WIND-O | WEST | 2020 | 0
799 | MAVERICK CREEK II | 20INR0046 |  | CONCHO | WIND-O | WEST | 2020 | 0
800 | MESTENO WIND | 16INR0081 |  | STARR | WIND-O | SOUTH | 2020 | 201.6
801 | OVEJA WIND | 18INR0033 |  | IRION | WIND-O | WEST | 2020 | 300
802 | PRAIRIE HILL WIND | 19INR0100 |  | MCLENNAN | WIND-O | NORTH | 2020 | 0
803 | RANCHERO WIND | 20INR0011 |  | CROCKETT | WIND-O | WEST | 2020 | 300
804 | RELOJ DEL SOL WIND | 17INR0025 |  | ZAPATA | WIND-O | SOUTH | 2020 | 0
805 | RTS 2 WIND (HEART OF TEXAS WIND) | 18INR0016 |  | MCCULLOCH | WIND-O | SOUTH | 2020 | 0
806 | SAGE DRAW WIND | 19INR0163 |  | LYNN | WIND-O | WEST | 2020 | 338
807 | TG EAST WIND | 19INR0052 |  | KNOX | WIND-O | WEST | 2021 | 0
808 | VERA WIND | 19INR0051 |  | KNOX | WIND-O | WEST | 2020 | 0
809 | WHITE MESA WIND | 19INR0128 |  | CROCKETT | WIND-O | WEST | 2020 | 0
810 | WHITEHORSE WIND | 19INR0080 |  | FISHER | WIND-O | WEST | 2020 | 418.9
811 | WILSON RANCH (INFINITY LIVE OAK WIND) | 12INR0060 |  | SCHLEICHER | WIND-O | WEST | 2020 | 199.5
812 | WKN AMADEUS WIND | 14INR0009 |  | FISHER | WIND-O | WEST | 2020 | 0
813 | Planned Capacity Total (Wind) | [6 empty] | 3149.2
814
815 | Planned Wind Capacity Sub-total (Coastal Counties) |  | WIND_PLANNED_C |  |  |  |  | 522.1
816 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PL_PEAK_PCT_C | % |  |  |  | 66
817
818 | Planned Wind Capacity Sub-total (Panhandle Counties) |  | WIND_PLANNED_P |  |  |  |  | 0
819 | Wind Peak Average Capacity Percentage (Panhandle) |  | WIND_PL_PEAK_PCT_P |  |  |  |  | 36
820
821 | Planned Wind Capacity Sub-total (Other counties) |  | WIND_PLANNED_O |  |  |  |  | 2627.1
822 | Wind Peak Average Capacity Percentage (Other) |  | WIND_PL_PEAK_PCT_O |  |  |  |  | 34
823
824 | Planned Solar Resources with Executed SGIA
825 | AGATE SOLAR | 20INR0023 |  | ELLIS | SOLAR | NORTH | 2020 | 0
826 | ANSON SOLAR | 19INR0081 |  | JONES | SOLAR | WEST | 2020 | 0
827 | ARAGORN SOLAR | 19INR0088 |  | CULBERSON | SOLAR | WEST | 2021 | 0
828 | BRAVEPOST SOLAR | 20INR0053 |  | TOM GREEN | SOLAR | WEST | 2021 | 0
829 | CORAZON SOLAR | 15INR0044 |  | WEBB | SOLAR | SOUTH | 2020 | 0
830 | COTTONWOOD BAYOU | 19INR0134 |  | BRAZORIA | SOLAR | COASTAL | 2021 | 0
831 | CROWDED STAR SOLAR | 20INR0241 |  | JONES | SOLAR | WEST | 2021 | 0
832 | ELARA SOLAR | 21INR0276 |  | FRIO | SOLAR | SOUTH | 2021 | 0
833 | EMERALD GROVE SOLAR (PECOS SOLAR POWER I) | 15INR0059 |  | PECOS | SOLAR | WEST | 2021 | 0
834 | EUNICE SOLAR | 20INR0219 |  | ANDREWS | SOLAR | WEST | 2020 | 0
835 | FORT BEND SOLAR | 18INR0053 |  | FORT BEND | SOLAR | HOUSTON | 2021 | 0
836 | FOWLER RANCH | 18INR0039 |  | CRANE | SOLAR | WEST | 2020 | 0
837 | GALLOWAY 1 SOLAR | 19INR0121 |  | CONCHO | SOLAR | WEST | 2021 | 0
838 | GALLOWAY 2 SOLAR | 21INR0431 |  | CONCHO | SOLAR | WEST | 2021 | 0
839 | GARNET SOLAR | 20INR0021 |  | WILLIAMSON | SOLAR | SOUTH | 2020 | 0
840 | GREASEWOOD SOLAR | 19INR0034 |  | PECOS | SOLAR | WEST | 2020 | 0
841 | HOLSTEIN SOLAR | 19INR0009 |  | NOLAN | SOLAR | WEST | 2020 | 0
842 | HORIZON SOLAR | 21INR0261 |  | FRIO | SOLAR | SOUTH | 2021 | 0
843 | HOVEY (BARILLA SOLAR 1B) | 12INR0059b |  | PECOS | SOLAR | WEST | 2020 | 0
844 | IMPACT SOLAR | 19INR0151 |  | LAMAR | SOLAR | NORTH | 2020 | 0
845 | IP TITAN | 20INR0032 |  | CULBERSON | SOLAR | WEST | 2021 | 0
846 | JUNO SOLAR | 21INR0026 |  | BORDEN | SOLAR | WEST | 2021 | 0
847 | KELLAM SOLAR | 20INR0261 |  | VAN ZANDT | SOLAR | NORTH | 2020 | 0
848 | LAPETUS SOLAR | 19INR0185 |  | ANDREWS | SOLAR | WEST | 2020 | 100
849 | LILY SOLAR | 19INR0044 |  | KAUFMAN | SOLAR | NORTH | 2021 | 0
850 | LONG DRAW SOLAR | 18INR0055 |  | BORDEN | SOLAR | WEST | 2020 | 0
851 | LONG POINT SOLAR | 19INR0042 |  | BRAZORIA | SOLAR | COASTAL | 2021 | 0
852 | MISAE SOLAR | 18INR0045 |  | CHILDRESS | SOLAR | PANHANDLE | 2020 | 240.8
853 | MISAE SOLAR II | 20INR0091 |  | CHILDRESS | SOLAR | PANHANDLE | 2021 | 0
854 | MORROW LAKE SOLAR | 19INR0155 |  | FRIO | SOLAR | SOUTH | 2021 | 0
855 | MURPHY LAKE SOLAR | 19INR0033 |  | KAUFMAN | SOLAR | NORTH | 2021 | 0
856 | MUSTANG CREEK SOLAR | 18INR0050 |  | JACKSON | SOLAR | SOUTH | 2021 | 0
857 | MYRTLE SOLAR | 19INR0041 |  | BRAZORIA | SOLAR | COASTAL | 2021 | 0
858 | NAZARETH SOLAR | 16INR0049 |  | CASTRO | SOLAR | PANHANDLE | 2022 | 0
859 | NORTON SOLAR | 19INR0035 |  | RUNNELS | SOLAR | WEST | 2021 | 0
860 | OBERON SOLAR | 19INR0083 |  | ECTOR | SOLAR | WEST | 2020 | 0
861 | OXY SOLAR | 19INR0184 |  | ECTOR | SOLAR | WEST | 2020 | 0
862 | PFLUGERVILLE SOLAR | 15INR0090 |  | TRAVIS | SOLAR | SOUTH | 2020 | 0
863 | PHOENIX SOLAR | 19INR0091 |  | FANNIN | SOLAR | NORTH | 2021 | 0
864 | PROSPERO SOLAR | 19INR0092 |  | ANDREWS | SOLAR | WEST | 2020 | 0
865 | PROSPERO SOLAR II | 21INR0229 |  | ANDREWS | SOLAR | WEST | 2021 | 0
866 | QUEEN SOLAR | 19INR0102 |  | UPTON | SOLAR | WEST | 2019 | 200
867 | QUEEN SOLAR PHASE II | 20INR0298 |  | UPTON | SOLAR | WEST | 2020 | 0
868 | RAMBLER SOLAR | 19INR0114 |  | TOM GREEN | SOLAR | WEST | 2020 | 0
869 | RAYOS DEL SOL | 19INR0045 |  | CAMERON | SOLAR | COASTAL | 2020 | 0
870 | RE MAPLEWOOD 2A SOLAR | 17INR0020a |  | PECOS | SOLAR | WEST | 2021 | 0
871 | RE MAPLEWOOD 2B SOLAR | 17INR0020b |  | PECOS | SOLAR | WEST | 2020 | 0
872 | RE MAPLEWOOD 2C SOLAR | 17INR0020c |  | PECOS | SOLAR | WEST | 2021 | 0
873 | RIPPEY SOLAR | 20INR0031 |  | COOKE | SOLAR | NORTH | 2020 | 0
874 | RODEO SOLAR | 19INR0103 |  | ANDREWS | SOLAR | WEST | 2021 | 0
875 | SHAKES SOLAR | 19INR0073 |  | ZAVALA | SOLAR | SOUTH | 2021 | 0
876 | SODA LAKE SOLAR 1 | 18INR0040 |  | CRANE | SOLAR | WEST | 2021 | 0
877 | SODA LAKE SOLAR 2 | 20INR0143 |  | CRANE | SOLAR | WEST | 2021 | 0
878 | SPINEL SOLAR | 20INR0025 |  | MEDINA | SOLAR | SOUTH | 2020 | 0
879 | TAYGETE II SOLAR | 21INR0233 |  | PECOS | SOLAR | WEST | 2021 | 0
880 | TAYGETE SOLAR | 20INR0054 |  | PECOS | SOLAR | WEST | 2020 | 0
881 | TEXAS SOLAR NOVA | 19INR0001 |  | KENT | SOLAR | WEST | 2022 | 0
882 | UPTON SOLAR | 16INR0114 |  | UPTON | SOLAR | WEST | 2020 | 0
883 | WAGYU SOLAR | 18INR0062 |  | BRAZORIA | SOLAR | COASTAL | 2020 | 0
884 | Planned Capacity Total (Solar) | [6 empty] | 540.8
885 | Solar Peak Average Capacity Percentage |  | SOLAR_PL_PEAK_PCT | % |  |  |  | 62
886
887 | Planned Storage Resources with Executed SGIA
888 | CHISHOLM GRID | 20INR0089 |  | TARRANT | STORAGE | NORTH | 2020 | 0
889 | EUNICE STORAGE | 20INR0220 |  | ANDREWS | STORAGE | WEST | 2020 | 0
890 | MADERO GRID | 21INR0244 |  | HIDALGO | STORAGE | SOUTH | 2021 | 0
891 | COMMERCE ST ESS |  | X443ESS1 | BEXAR | STORAGE | SOUTH | 2019 | 10
892 | FLAT TOP BATTERY |  | FLTBES_BESS1 | REEVES | STORAGE | WEST | 2019 | 9.9
893 | JOHNSON CITY BESS |  | JC_BAT | BLANCO | STORAGE | SOUTH | 2020 | 2.3
894 | RABBIT HILL ENERGY STORAGE PROJECT |  | RHESS2_ESS_1 | WILLIAMSON | STORAGE | SOUTH | 2019 | 9.9
895 | WORSHAM BATTERY |  | WRSBES_BESS1 | REEVES | STORAGE | WEST | 2019 | 9.9
896 | Planned Capacity Total (Storage) | [6 empty] | 42
897 | Storage Peak Average Capacity Percentage |  | STORAGE_PL_PEAK_PCT | % |  |  |  | 0
898
899 | Seasonal Mothballed Resources
900 | GREGORY POWER PARTNERS GT1 (AS OF 10/17/2019) |  | LGE_LGE_GT1 | SAN PATRICIO | GAS | COASTAL | 2000 | 152
901 | GREGORY POWER PARTNERS GT2 (AS OF 10/17/2019) |  | LGE_LGE_GT2 | SAN PATRICIO | GAS | COASTAL | 2000 | 151
902 | GREGORY POWER PARTNERS STG (AS OF 10/17/2019) |  | LGE_LGE_STG | SAN PATRICIO | GAS | COASTAL | 2000 | 75
903 | SPENCER STG U4 (AS OF 10/3/2018) |  | SPNCER_SPNCE_4 | DENTON | GAS | NORTH | 1966 | 57
904 | SPENCER STG U5 (AS OF 10/3/2018) |  | SPNCER_SPNCE_5 | DENTON | GAS | NORTH | 1973 | 61
905 | Total Seasonal Mothballed Capacity | [6 empty] | 496
906
907 | Mothballed Resources
908 | J T DEELY U1 (AS OF 12/31/2018) |  | CALAVERS_JTD1_M | BEXAR | COAL | SOUTH | 1977 | 430
909 | J T DEELY U2 (AS OF 12/31/2018) |  | CALAVERS_JTD2_M | BEXAR | COAL | SOUTH | 1978 | 420
910 | Total Mothballed Capacity | [6 empty] | 850
911
912 | Retiring Resources Unavailable to ERCOT (since last CDR/SARA)
913 | Total Retiring Capacity | [6 empty] | 0
Notes:
Capacity changes due to planned repower/upgrade projects are reflected in the operational units' ratings upon (1) receipt and ERCOT approval of a new Resource Asset Registration Form (RARF). Projects associated with interconnection change requests that change the MW capacity by more than zero are indicated with a code in the “Generation Interconnection Project Code” column of operational units.
Although seasonal capacity ratings for battery energy storage systems are reported above, the ratings are not included in the operational/planned capacity formulae. These resources are assumed to provide regulation reserves rather than sustained capacity available to meet system peak loads.
* The projects listed in the 'Planned Storage Resources with Executed SGIA' section are all Distributed Generation Resources (DGRs). Since they are 10 MW or less, they are not going through the GINR application process.
Note on I386: Original capacity rating of 4.8 MW reduced to 2.4 MW due to a spill gate failure.
Note on I388: Original capacity rating of 3.6 MW reduced to zero MW due to a spill gate failure.
Note on I749: This project is categorized as Inactive.
Note on I769: This project is categorized as Inactive.
Note on I770: This project is categorized as Inactive.
Note on I771: This project is categorized as Inactive.
Note on I773: This project is categorized as Inactive.
Note on I795: This project is categorized as Inactive.
Note on I825: This project is categorized as Inactive.
Note on I839: This project is categorized as Inactive.
Note on I843: This project is categorized as Inactive.
Note on I847: This project is categorized as Inactive.
Note on I873: This project is categorized as Inactive.
Note on I878: This project is categorized as Inactive.

## Background
Release Date: March 5, 2020
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Background
The Seasonal Assessment of Resource Adequacy (SARA) report is a deterministic approach to considering the impact of potential variables that may affect the sufficiency of installed resources to meet the peak electrical demand on the ERCOT System during a particular season.
The standard approach to assessing resource adequacy for one or more years into the future is to account for projected load and resources on a normalized basis and to require sufficient reserves (resources in excess of peak demand, on this normalized basis) to cover the uncertainty in peak demand and resource availability to meet a probabilistic reliability standard.
For seasonal assessments that look ahead less than a year, specific information may be available (such as seasonal climate forecasts or anticipated common-mode events such as drought) which can be used to consider the range of resource adequacy in a more deterministic manner.
The SARA report focuses on the availability of sufficient operating reserves to avoid emergency actions such as deployment of voluntary load reduction resources. It uses an operating reserve threshold of 2,300 MW to indicate the risk that an Energy Emergency Alert Level 1 (EEA1) may be triggered during the time of the forecasted seasonal peak load. This threshold level is intended to be roughly analogous to the 2,300 MW Physical Responsive Capability (PRC) threshold for EEA1. However, PRC is a real-time capability measure for Resources that can quickly respond to system disturbances. In contrast, the SARA operating reserve reflects additional capability assumed to be available before energy emergency procedures are initiated, such as from Resources qualified to provide non-spinning reserves. Additionally, the amount of operating reserves available may increase relative to what is included in the SARA report due to the market responding to wholesale market price increases and anticipated capacity scarcity conditions. Given these considerations, ERCOT believes that the 2,300 MW reserve capacity threshold is a reasonable indicator for the risk of Energy Emergency Alerts given the uncertainties in predicting system conditions months in advance.
The SARA report is intended to illustrate the range of resource adequacy outcomes that might occur. It serves as a situational awareness tool for ERCOT operational planning purposes, and helps fulfill the "extreme weather" resource adequacy assessment requirement per Public Utility Commission of Texas rule 25.362(i)(2)(H). In addition to a base scenario, several other scenarios are developed by varying the value of load forecast and resource availability parameters. The variation in these parameters is based on historic ranges of the parameter values or known changes expected in the near-term. The SARA report is not intended to indicate the likelihood of any of these scenario outcomes.