## Slide 1
ERCOT Frequency Control Report
February 2020
ERCOT
Operations Planning
PDCWG | March 18th, 2020

## Slide 2: Summary of February 2020
CPS1: 173.38%
Current CPS1 12-Month Rolling Average: 174.78%
4 BAAL Exceedances
2 hourly CPS1 score below 100%
BAAL-003 Events have updated through 2019
2018 BAAL-003 FRM Performance: -843.17
2020 RMS1 Statistics
  Mean: 15.56 mHz
  Min: 12.25 mHz
  Max: 19.33 mHz
Energy Statistics
  Total Energy: 27,974,671 MWh
  Wind Energy: 7,200,513 MWh
  Percent Energy from Wind: 25.74%
  Solar Energy: 368,579 MWh
  Percent Energy from Solar: 1.32%
Minimum System Inertia
  Mean: 180,848
  Max: 249,044 on Feb 27th
  Min: 139,638 on Feb 9th
Notes: Mean: 180,848
Max: 249,044 on Feb 27th
Min: 139,638 on Feb 9th

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
Feb-20 CPS1 (%): 173.38
Notes: Outliers:
2/4/2020 20:00: Large Expected generation deviation in the middle of the hour
2/5/2020 17:00: Large Expected generation deviation in the middle of the hour
2/10/2020 16:00: Loss of generation event

## Slide 5: BAAL Exceedances & Violations
There were 4 BAAL exceedances in Feb
Notes: BAAL Exceedances related to the two FMEs on 2/6/2020 and 2/10/2020

## Slide 6: 15-Minute Average CPS1%
Feb-20 CPS1 (%): 173.38

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 174.78%

## Slide 8: Daily RMS1 of ERCOT Frequency by Year

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2018 BAL-003 Selected Events – Update
Notes: BAL-003

## Slide 19: Op. Year 2018 BAL-003 FRM Performance - Update
Notes: OP2018: FRO = -381.0, FRM_median = -843.17, FRM_average = -959.7
OP2019: FRO = -381.0
OP2020: FRO = -425.0, FRM_median = -811.14, FRM_average = -892.5

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 27,974,671 MWh

## Slide 22: Total Energy from Wind Generation
Notes: 7,200,513 MWh

## Slide 23: % Energy from Wind Generation
Notes: 25.74%

## Slide 24: Total Energy From Solar Generation
Notes: 3368,579 MWh

## Slide 25: % Energy from Solar Generation
Notes: 1.32%

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia = 139,638 MW*s on 2/9/2020
Previous Minimum was 128,759 MW*s on 11/18/2018.
Data:
Mean: 180,848
Max: 249,044 on Feb 27th
Min: 139,638 on Feb 9th

## Slide 28: Questions?
Thank you!