Texas SET Change Control Request Form Change Control Number: 2020 –818 Implementation Version: Future

This Section Is Completed by Submitter of Change Control Request Only:

| Submitter Name: Kathy Scott | Submitting Company Name: CenterPoint Energy | Phone Number: 713-582-8654 |
| --- | --- | --- |
| Date of Submission: April 7, 2020 | Affected TX SET Transaction(s): 814_28 | Submitter’s E-Mail Address: Kathy.Scott@CenterPointEnergy.com |
| Texas SET Issue cross-reference number: |  | Protocol Impact (Y/N): N |
| Detailed Description and Reason for Proposed Change(s): This Change Control includes the following changes or clarifications that are the result of market recommendations following Hurricane Harvey Lessons Learned Workshop and several follow-up discussions held during TX SET meetings over the past 18 months: 814_28 Complete Unexecutable or Permit Required Adds the following in the REF~G7 (Complete Unexecutable Reason) REF02 – Completed Unexecutable: Add: New Code “J009” – “Distributed Generation (DG) Premise requires ATS and signed Interconnection Agreement.” Add: New Code “S004” – “Service Standards Clearance Violation” Add: New Code “U007” – “Service Standards Clearance Violation” 814_28 Complete Unexecutable or Permit Required Adds the following in the REF~G7 (Complete Unexecutable Reason) REF03 Description: Add: “S004” and “U007” Codes requires additional details of the Service Standards Clearance Violation. On March 26, 2020 after reviewing the draft version of this 814_28 redlined changes consensus was gained by TX SET members in attendance to draft this change control that will be discussed during a subsequent TX SET Change Control Conference Call. |  |  |
| NOTE: Requester must complete above fields and include a redlined example of modifications to each impacted implementation guide. This must be included at the time the request form is submitted. Please submit this completed form via e-mail to txsetchangecontrol@ercot.com and RMS Chair. |  |  |

For ERCOT Change Control Manager Use Only:

| Texas SET Recommendation: | Recommendation for Emergency (Y/N): | Date of TX SET Recommendation: |
| --- | --- | --- |
| Detailed Description and Reason for Revision: |  |  |
| RMS Decision: | Emergency (Y/N): | Date of RMS Decision: |
| Summary of RMS Discussion: |  |  |

814_28 Complete Unexecutable or Permit Required

Segment:	REF Reference Identification (Complete Unexecutable Reason)

Position:	030

Loop:	LIN        Optional

Level:	Detail

Usage:	Optional

Max Use:	>1

Purpose:	To specify identifying information

Syntax Notes:	1	At least one of REF02 or REF03 is required.

2	If either C04003 or C04004 is present, then the other is required.

3	If either C04005 or C04006 is present, then the other is required.

Semantic Notes:	1	REF04 contains data relating to the value cited in REF02.

Comments:

| Notes: |  | Required when ASI01 = 9 (Completed Unexecutable), otherwise not used. If codes containing "T018", “S004”, “U007” or "000" are used, an explanation is required in REF03. Otherwise, the REF03 is optional. |
| --- | --- | --- |
|  |  | REF~G7~A000~OTHER WEATHERHEAD REASON REF~G7~B003~NONE INSTALLED REF~G7~B003 |

Data Element Summary

Ref.	Data

Des.	Element	Name	Attributes

| Must Use | REF01 | 128 | Reference Identification Qualifier |  |  |  | M |  | ID 2/3 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Code qualifying the Reference Identification |  |  |  |  |  |  |  |  |
|  |  |  |  | G7 |  | Resubmission Reason Code |  |  |  |  |  |
|  |  |  |  |  |  | Completed Unexecutable |  |  |  |  |  |
| Must Use | REF02 | 127 | Reference Identification |  |  |  | X |  | AN 1/30 |  |  |
|  |  |  | Reference information as defined for a particular Transaction Set or as specified by the Reference Identification Qualifier |  |  |  |  |  |  |  |  |
|  |  |  |  | A000 |  | ===== WEATHERHEAD (SERVICE OUTLET) ===== |  |  |  |  |  |
|  |  |  |  | A001 |  | Need Meter Loop and Outlet Installed |  |  |  |  |  |
|  |  |  |  | A002 |  | Need fiber spacer for service entrance conductors |  |  |  |  |  |
|  |  |  |  | A003 |  | Need weatherhead on conduit above meter base |  |  |  |  |  |
|  |  |  |  | A004 |  | Fiber wire spacer protector broken in weatherhead |  |  |  |  |  |
|  |  |  |  | A005 |  | Screws holding head in place broken off or threads stripped |  |  |  |  |  |
|  |  |  |  | A006 |  | Exceeds 25' above finished grade |  |  |  |  |  |
|  |  |  |  | A007 |  | Damaged Meter Loop |  |  |  |  |  |
|  |  |  |  | A008 |  | Needs clamps at Weatherhead |  |  |  |  |  |
|  |  |  |  | B000 |  | ===== POINT OF ATTACHMENT ===== |  |  |  |  |  |
|  |  |  |  | B001 |  | Too close to window, door or porch, needs to be 3' away |  |  |  |  |  |
|  |  |  |  | B002 |  | Point of attachment over 3' above roof without guy or bracing |  |  |  |  |  |
|  |  |  |  | B003 |  | None Installed |  |  |  |  |  |
|  |  |  |  | B004 |  | Drop attachment. Too far from service outlet, should be within 18" of drop |  |  |  |  |  |
|  |  |  |  | B005 |  | Anchorage not sufficient to support drop cable - 300 lb pull of service drops |  |  |  |  |  |
|  |  |  |  | B006 |  | Need penta or creosote treated pole, or a 4" x 6" timber for permanent service |  |  |  |  |  |
|  |  |  |  | B007 |  | Temporary meter pole needs bracing to withstand 300 lb. pull of service drops |  |  |  |  |  |
|  |  |  |  | B008 |  | Meter pole not set deep enough to support drops and withstand 300 lb pull of service drops |  |  |  |  |  |
|  |  |  |  | B009 |  | Pole not of proper height over driveway. Need 12' vertical clearance above finished grade, over residential driveways |  |  |  |  |  |
|  |  |  |  | B010 |  | Service attachment needs to be higher for driveway, alleys, roads and streets |  |  |  |  |  |
|  |  |  |  | B011 |  | Unable to get drop attachment high enough to get clearance from low point of sag in service cable, over sidewalk, porch or platform |  |  |  |  |  |
|  |  |  |  | B012 |  | Need bracket on the service mast for attaching service rack |  |  |  |  |  |
|  |  |  |  | B013 |  | Requires secondary rack |  |  |  |  |  |
|  |  |  |  | B014 |  | Exceeds service drop distance |  |  |  |  |  |
|  |  |  |  | B015 |  | No Meter Pole |  |  |  |  |  |
|  |  |  |  | B016 |  | Does not have 12" clearance from SWBT, Cable TV, etc. cables |  |  |  |  |  |
|  |  |  |  | C000 |  | ===== LINE CONDUIT ===== |  |  |  |  |  |
|  |  |  |  | C001 |  | Should not be water pipe fittings |  |  |  |  |  |
|  |  |  |  | C002 |  | Water pipe not allowed for service outlet conduit |  |  |  |  |  |
|  |  |  |  | C003 |  | Service outlet conduit not sufficiently clamped to building |  |  |  |  |  |
|  |  |  |  | C004 |  | Two inch G.I. or I.M.C. or three inch aluminum conduit required for mast head |  |  |  |  |  |
|  |  |  |  | C005 |  | Electrical junction boxes not sealable type |  |  |  |  |  |
|  |  |  |  | D000 |  | ===== LINE OF CONDUCTORS ===== |  |  |  |  |  |
|  |  |  |  | D001 |  | Service entrance conductors not identified |  |  |  |  |  |
|  |  |  |  | D002 |  | Line wire of wrong type insulation |  |  |  |  |  |
|  |  |  |  | D003 |  | Line wires too short to reach lugs in meter can |  |  |  |  |  |
|  |  |  |  | D004 |  | Wires from service outlet too short for TDSP to connect drops |  |  |  |  |  |
|  |  |  |  | D005 |  | No line wires in service outlet |  |  |  |  |  |
|  |  |  |  | D006 |  | Bare aluminum neutral conductor in meter loop |  |  |  |  |  |
|  |  |  |  | E000 |  | ===== METER BASE ===== |  |  |  |  |  |
|  |  |  |  | E001 |  | Improperly mounted on pole. Too low or too high. |  |  |  |  |  |
|  |  |  |  | E002 |  | Un-used holes in meter base not close up or covered |  |  |  |  |  |
|  |  |  |  | E003 |  | No neutral connector in meter base |  |  |  |  |  |
|  |  |  |  | E004 |  | Meter base improperly mounted. Upside down. |  |  |  |  |  |
|  |  |  |  | E005 |  | Need 125 amp meter base to match customers wire size |  |  |  |  |  |
|  |  |  |  | E006 |  | Need 200 amp meter base to match customers wire size |  |  |  |  |  |
|  |  |  |  | E007 |  | Customer wired for current transformer installation. Refer to primary meter man. |  |  |  |  |  |
|  |  |  |  | E008 |  | Foreign type of meter base, TDSP does not have equipment to fit it |  |  |  |  |  |
|  |  |  |  | E009 |  | Gang type meter socket base not completely wired |  |  |  |  |  |
|  |  |  |  | E010 |  | No cover on meter base |  |  |  |  |  |
|  |  |  |  | E011 |  | Meter base mounted too high above finished grade ground level, should be 5' to 6' |  |  |  |  |  |
|  |  |  |  | E012 |  | Residential meter socket, need commercial |  |  |  |  |  |
|  |  |  |  | E013 |  | Meter socket base not level |  |  |  |  |  |
|  |  |  |  | E014 |  | Ground in meter can |  |  |  |  |  |
|  |  |  |  | E015 |  | Meter base needs to be replaced |  |  |  |  |  |
|  |  |  |  | E016 |  | Customer not ready |  |  |  |  |  |
|  |  |  |  | E017 |  | Faceplate need Tamper Proof lid |  |  |  |  |  |
|  |  |  |  | F000 |  | ===== CUSTOMER'S NEUTRAL WIRE ===== |  |  |  |  |  |
|  |  |  |  | F001 |  | Must be electronically continuous inside socket base |  |  |  |  |  |
|  |  |  |  | F002 |  | Conductors unidentified in service entrance conductors. Must be white, bare or gray. |  |  |  |  |  |
|  |  |  |  | F003 |  | All 3 phase wires must be identified |  |  |  |  |  |
|  |  |  |  | F004 |  | Uninsulated aluminum conductor |  |  |  |  |  |
|  |  |  |  | F005 |  | Bonding conductor for 480 volt, 3 wire service must be a minimum of #6 copper or equivalent and must be insulated |  |  |  |  |  |
|  |  |  |  | G000 |  | ===== LOAD CONDUIT ===== |  |  |  |  |  |
|  |  |  |  | G001 |  | Customer used water pipe nipple going to switch box. Need water tight conduit. |  |  |  |  |  |
|  |  |  |  | G002 |  | No bushing on conduit from meter base. Weather proof entrance fitting. |  |  |  |  |  |
|  |  |  |  | H000 |  | ===== CUSTOMER'S LOAD CONDUCTORS ====== |  |  |  |  |  |
|  |  |  |  | H001 |  | Exceeds ampacity of meter socket |  |  |  |  |  |
|  |  |  |  | H002 |  | Has the wrong type of insulation |  |  |  |  |  |
|  |  |  |  | H003 |  | No wires in load side of meter box |  |  |  |  |  |
|  |  |  |  | J000 |  | ===== SWITCH BOX ===== |  |  |  |  |  |
|  |  |  |  | J001 |  | Holes in customers switch box not used or closed. Bare wires and connections exposed. |  |  |  |  |  |
|  |  |  |  | J002 |  | No ground connector attached to box |  |  |  |  |  |
|  |  |  |  | J003 |  | Inside main switch box mounted outside. Must have water tight connections between meter base and switch box |  |  |  |  |  |
|  |  |  |  | J004 |  | No cover on breaker box. Lighted connections exposed to public. |  |  |  |  |  |
|  |  |  |  | J005 |  | Load wires still energized from backfeed. |  |  |  |  |  |
|  |  |  |  | J006 |  | Neutral connection must be electrically continuous and not fused |  |  |  |  |  |
|  |  |  |  | J007 |  | Main switch inside premises are unable to relieve load from loop |  |  |  |  |  |
|  |  |  |  | J008 |  | Need main breaker if over 6 breakers |  |  |  |  |  |
|  |  |  |  | J009 |  | Distributed Generation (DG) Premise Requires ATS and Signed Interconnection Agreement |  |  |  |  |  |
|  |  |  |  |  |  | TDSP requires Automatic Transfer Switch (ATS) Installed and/or TDSP requires Customer’s signed Interconnection Agreement |  |  |  |  |  |
|  |  |  |  | K000 |  | ===== GROUNDING ELECTRODE CONDUCTORS ===== |  |  |  |  |  |
|  |  |  |  | K001 |  | Grounding electrode conductor not sized in accordance with table 250-94 of NEC |  |  |  |  |  |
|  |  |  |  | K002 |  | Where used outside, aluminum or copper clad aluminum conductors shall not be installed within 18" of earth. |  |  |  |  |  |
|  |  |  |  | K003 |  | Grounding electrode conductor not securely fastened to the premises below the meter can |  |  |  |  |  |
|  |  |  |  | K004 |  | No grounding electrode conductor installed |  |  |  |  |  |
|  |  |  |  | K005 |  | Grounding electrode conductor not attached to ground rod with approved clamp |  |  |  |  |  |
|  |  |  |  | K006 |  | Has aluminum grounding electrode conductor in direct contact with a masonry or earth |  |  |  |  |  |
|  |  |  |  | K007 |  | Grounding electrode conductor must go from switch box to ground rod |  |  |  |  |  |
|  |  |  |  | L000 |  | ===== GROUND CONDUIT OR ARMORED CABLE ===== |  |  |  |  |  |
|  |  |  |  | L001 |  | Not attached to switch box with water tight connector |  |  |  |  |  |
|  |  |  |  | L002 |  | Not bonded to ground rod |  |  |  |  |  |
|  |  |  |  | L003 |  | Not attached to switch box |  |  |  |  |  |
|  |  |  |  | L004 |  | Not secure to building or pole |  |  |  |  |  |
|  |  |  |  | M000 |  | ===== GROUND CLAMP ===== |  |  |  |  |  |
|  |  |  |  | M001 |  | Unapproved ground clamp |  |  |  |  |  |
|  |  |  |  | M002 |  | No ground clamp |  |  |  |  |  |
|  |  |  |  | N000 |  | ===== GROUND ROD ===== |  |  |  |  |  |
|  |  |  |  | N001 |  | Must be at least 3/4" galvanized pipe |  |  |  |  |  |
|  |  |  |  | N002 |  | Steel rod must be 5/8" minimum diameter |  |  |  |  |  |
|  |  |  |  | N003 |  | Rod or pipe must be 8' deep |  |  |  |  |  |
|  |  |  |  | N004 |  | No Ground Rod |  |  |  |  |  |
|  |  |  |  | P000 |  | ===== PERMITS ===== |  |  |  |  |  |
|  |  |  |  | P001 |  | No permit |  |  |  |  |  |
|  |  |  |  | P002 |  | Needs city inspection |  |  |  |  |  |
|  |  |  |  | Q000 |  | ===== CONSTRUCTION ===== |  |  |  |  |  |
|  |  |  |  | Q001 |  | TDSP construction required |  |  |  |  |  |
|  |  |  |  | Q002 |  | Customer needs to meet electrician |  |  |  |  |  |
|  |  |  |  | Q003 |  | Need house or apartment numbers permanently identified |  |  |  |  |  |
|  |  |  |  | Q004 |  | Corrections not made from previous turndown |  |  |  |  |  |
|  |  |  |  | Q005 |  | Drops would trespass other's property |  |  |  |  |  |
|  |  |  |  | Q006 |  | Unable to determine meter base location |  |  |  |  |  |
|  |  |  |  | Q007 |  | Customer needs to bore (ex. driveway, sidewalk, etc....) |  |  |  |  |  |
|  |  |  |  | Q008 |  | Service path obstructed (ex. building materials, dirt, fence, etc....) |  |  |  |  |  |
|  |  |  |  | Q009 |  | No equipment access (ex. need 5' to 10' wide path) |  |  |  |  |  |
|  |  |  |  | Q010 |  | Needs grade work |  |  |  |  |  |
|  |  |  |  | Q011 |  | Customer owned utilities not located (ex. water, sewer, gas, etc...) |  |  |  |  |  |
|  |  |  |  | Q012 |  | Customer installed conduit insufficient, does not meet TDSP specifications |  |  |  |  |  |
|  |  |  |  | R000 |  | ===== UNDERGROUND SERVICE DROPS OWNED BY CUSTOMER ===== |  |  |  |  |  |
|  |  |  |  | R001 |  | Service drop not installed |  |  |  |  |  |
|  |  |  |  | R002 |  | URD drops too short |  |  |  |  |  |
|  |  |  |  | R003 |  | URD ditch not covered |  |  |  |  |  |
|  |  |  |  | R004 |  | URD drops not run to the proper point (small notch "V" of the transformer pad) |  |  |  |  |  |
|  |  |  |  | R005 |  | Wrong type of URD meter can |  |  |  |  |  |
|  |  |  |  | R006 |  | Unapproved wire for underground |  |  |  |  |  |
|  |  |  |  | R007 |  | URD service conductors not deep enough |  |  |  |  |  |
|  |  |  |  | R008 |  | Drops need to be dug within 12" of transformer on pad. Must be clear to open transformer. |  |  |  |  |  |
|  |  |  |  | R009 |  | Underground drops cut in two |  |  |  |  |  |
|  |  |  |  | R010 |  | T-Saw pole not 4 feet from front of transformer on pad. Must be clear to open transformer. |  |  |  |  |  |
|  |  |  |  | R011 |  | T-Saw pole not 3 feet from rear of transformer |  |  |  |  |  |
|  |  |  |  | R012 |  | P.V.C. or conduit elbow not deep enough |  |  |  |  |  |
|  |  |  |  | R013 |  | No P.V.C. or conduit elbow |  |  |  |  |  |
|  |  |  |  | R014 |  | No line conduit installed |  |  |  |  |  |
|  |  |  |  | R015 |  | Meter pole set in easement |  |  |  |  |  |
|  |  |  |  | S000 |  | ===== CUT-INS/CUT-OUTS ===== |  |  |  |  |  |
|  |  |  |  | S001 |  | Inside trouble on customer side |  |  |  |  |  |
|  |  |  |  | S002 |  | Weatherhead pulled from house or broken |  |  |  |  |  |
|  |  |  |  | S003 |  | Cannot cut-out at pole, MD, Weatherhead, or remove meter and drops |  |  |  |  |  |
|  |  |  |  | S004 |  | Service Standards Clearance Violation(s) |  |  |  |  |  |
|  |  |  |  |  |  | Requires explanation in REF03 |  |  |  |  |  |
|  |  |  |  | T000 |  | ===== MISCELLANEOUS ===== |  |  |  |  |  |
|  |  |  |  | T001 |  | Business Closed/Customer not home |  |  |  |  |  |
|  |  |  |  | T002 |  | Meter inside, building locked |  |  |  |  |  |
|  |  |  |  | T003 |  | Bad Dog |  |  |  |  |  |
|  |  |  |  | T004 |  | High fence, locked gate |  |  |  |  |  |
|  |  |  |  | T005 |  | Electrician needs to meet with TDSP meter man |  |  |  |  |  |
|  |  |  |  | T006 |  | Customer needs to trim trees |  |  |  |  |  |
|  |  |  |  | T007 |  | No breakers |  |  |  |  |  |
|  |  |  |  | T008 |  | Customer's facilities under secondary and primary |  |  |  |  |  |
|  |  |  |  | T009 |  | Meter blocked |  |  |  |  |  |
|  |  |  |  | T010 |  | Meter in wall |  |  |  |  |  |
|  |  |  |  | T011 |  | Voided per customer |  |  |  |  |  |
|  |  |  |  |  |  | Cannot be used for Disconnect Non-Pay |  |  |  |  |  |
|  |  |  |  | T012 |  | Re-schedule per customer |  |  |  |  |  |
|  |  |  |  |  |  | Cannot be used for Disconnect Non-Pay |  |  |  |  |  |
|  |  |  |  | T013 |  | Meter Damaged |  |  |  |  |  |
|  |  |  |  | T014 |  | No Meter |  |  |  |  |  |
|  |  |  |  | T015 |  | Muddy Road |  |  |  |  |  |
|  |  |  |  | T016 |  | High Water |  |  |  |  |  |
|  |  |  |  | T017 |  | Customer Requested Clearance - Unable to do work on date requested |  |  |  |  |  |
|  |  |  |  | T018 |  | Other |  |  |  |  |  |
|  |  |  |  |  |  | Requires explanation in REF03 |  |  |  |  |  |
|  |  |  |  | T019 |  | Tampering |  |  |  |  |  |
|  |  |  |  | T021 |  | Competitive Retailer in Default |  |  |  |  |  |
|  |  |  |  | T022 |  | Force Majeure Event |  |  |  |  |  |
|  |  |  |  | T023 |  | Move-Out transaction (814_24) was treated as a force off since (814_03) Move-In transaction received by the TDSP was scheduled for the same date. |  |  |  |  |  |
|  |  |  |  | T024 |  | Switch or Move-In Request cannot be completed due to Switch Hold recently applied to this ESI ID |  |  |  |  |  |
|  |  |  |  | T025 |  | Competing Transaction Scheduled for Same Date |  |  |  |  |  |
|  |  |  |  | U000 |  | ===== UNSAFE CONDITIONS ===== |  |  |  |  |  |
|  |  |  |  | U001 |  | Exposed wires |  |  |  |  |  |
|  |  |  |  | U002 |  | Jumpers in breaker box |  |  |  |  |  |
|  |  |  |  | U003 |  | Insects |  |  |  |  |  |
|  |  |  |  | U004 |  | Excessive debris |  |  |  |  |  |
|  |  |  |  | U005 |  | Irate Customer |  |  |  |  |  |
|  |  |  |  | U006 U007 |  | Backfeed on load side jaws Service Standards Clearance Violation |  |  |  |  |  |
|  |  |  |  |  |  | Requires explanation in REF03 |  |  |  |  |  |
| Dep | REF03 | 352 | Description |  |  |  | X |  | AN 1/80 |  |  |
|  |  |  | A free-form description to clarify the related data elements and their content |  |  |  |  |  |  |  |  |
|  |  |  | Used to further describe the status reason code sent in REF02. Required when REF02 = "T018", “S004”, “U007” or when the code contains "000". Otherwise, optional. |  |  |  |  |  |  |  |  |