## Slide 1
ERCOT Frequency Control Report
March 2020
ERCOT
Operations Planning
PDCWG | April 15th, 2020

## Slide 2: Summary of March 2020
CPS1: 169.66%
Current CPS1 12-Month Rolling Average: 174.49%
2 BAAL Exceedances
6 hourly CPS1 score below 100%
BAAL-003 Events have updated through 2019
2018 BAAL-003 FRM Performance: -843.17
2020 RMS1 Statistics
  Mean: 15.70 mHz
  Min: 12.25 mHz
  Max: 19.80 mHz
Energy Statistics
  Total Energy: 28,190,392 MWh
  Wind Energy: 7,349,959 MWh
  Percent Energy from Wind: 26.07%
  Solar Energy: 419,973 MWh
  Percent Energy from Solar: 1.49%
Minimum System Inertia
  Mean: 171,265
  Max: 200,438 on Mar 17th
  Min: 139,592 on Mar 8th
Notes: Mean: 171,265
Max: 200,438 on Mar 17th
Min: 139,592 on Mar 8th

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
Mar-20 CPS1 (%): 169.66
Notes: Outliers:
3/4/2020: Large expected gen deviation at the beginning and the end of the hour from mostly wind resources. Wind down ramp at the tail of the hour.
3/17/2020: Large expected gen deviation at the beginning of the hour from mostly wind resources.
3/18/2020 : Loss of generation event.
3/21/2020 : Large expected gen deviation at the end of the hour.
3/27/2020: Large expected gen deviation at the end of the hour.
3/28/2020: Large expected gen deviation throughout the first half of the hour.

## Slide 5: BAAL Exceedances & Violations
There were 2 BAAL exceedances in March
Notes: BAAL Exceedances related to the FME on 3/18/2020

## Slide 6: 15-Minute Average CPS1%
Mar-20 CPS1 (%): 169.66

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 174.49%

## Slide 8: Daily RMS1 of ERCOT Frequency by Year

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2018 BAL-003 Selected Events – Update
Notes: BAL-003

## Slide 19: Op. Year 2018 BAL-003 FRM Performance - Update
Notes: OP2018: FRO = -381.0, FRM_median = -843.17, FRM_average = -959.7
OP2019: FRO = -381.0
OP2020: FRO = -425.0, FRM_median = -811.14, FRM_average = -892.5

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 28,190,392 MWh

## Slide 22: Total Energy from Wind Generation
Notes: 7,349,959 MWh

## Slide 23: % Energy from Wind Generation
Notes: 26.07%

## Slide 24: Total Energy From Solar Generation
Notes: 419,973 MWh

## Slide 25: % Energy from Solar Generation
Notes: 1.49%

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia = 139,592 MW*s on 3/8/2020
Previous Minimum was 128,759 MW*s on 11/18/2018.
Data:
Mean: 171,265
Max: 200,438 on Mar 17th
Min: 139,592 on Mar 8th

## Slide 28: Questions?
Thank you!