## Slide 1
Regulation Bias Analysis Post SCR-773
March 2020
ERCOT
Operations Planning
PDCWG | April 15th, 2020

## Slide 2
Discussion Points
Current GTBD Parameters & References
Metric to measure Regulation bias and performance
Regulation Deployed comparison for last three months.
Total Regulation (net) Deployed Comparison
Regulation Deployed 15-minute interval comparison by each hour for 2017, 2018, and 2019 months
Regulation Exhaustion Rate
Regulation bias for consecutive 5-min SCED intervals
Time Error & Contributing Factors
Summary

## Slide 3: Current GTBD Parameters
Notes: 3/12/18 – Integral ACE Time Constant Changed from 60 min to 45 min
5/17/18 - K4 Changed from 0.3 to 0.2 and K5 Changed from 0.4 to 0.5
12/4/18 - K6 Changed from 0 to 0.5
2/12/19 - K6 Changed from 0.5 to 1
4/01/19 - K5 changed from 0.5 to 0.4 and Max. Integral ACE Feedback changed from 250 to 150
4/24/19 - Max. Integral ACE Feedback changed from 150 to 160. PWRR Threshold changed from 20 to 25.
5/22/19 – K5 changed from 0.4 to 0.5 Max. Integral ACE Feedback changed from 160 to 200. PWRR Threshold changed from 25 to 30.

## Slide 4: Projected Wind Ramp Rate MAE

## Slide 5: Projected Wind Ramp Rate Error

## Slide 6: References

## Slide 7
Metrics to Measure SCR-773 Performance
Trend and monitor the regulation deployed by hour.
Set target of 50 MW for total regulation deployed by hour for peak hours.
Set target of 85% for the number of intervals where regulation deployment was both up and down for peak hours.
Track the Regulation exhaustion rate for all hours (not to exceed 5%).
Using a 50MW filter, target 15 occurrences or less per month for regulation bias of six or more consecutive 5 minute intervals for peak hours.

## Slide 8: Total Regulation Deployed Comparison
Total regulation deployed for the last three months.

## Slide 9: Total Regulation Deployed Comparison - Monthly

## Slide 10: Metric 1: Regulation Deployed Comparisons
Trend and monitor the regulation deployed by hour.

## Slide 11: Regulation Deployed Comparison

## Slide 12: Regulation Deployed Comparison

## Slide 13: Regulation Deployed Comparison

## Slide 14: Metric 2: Total Regulation Deployed Comparisons
Set target of 50MW for total regulation deployed by hour for peak hours.

## Slide 15: Total Regulation Deployed Comparison

## Slide 16: Metric 3: 15-min Intervals Where Both REGUP/REGDN Were Deployed
Set target of 85% for the number of intervals where regulation deployment was both up and down.

## Slide 17: “Zero” Crossing Regulation

## Slide 18: “Zero” Crossing Regulation

## Slide 19: Metric 4: Regulation Exhaustion Rate
Track the regulation exhaustion rate for all hours (not to exceed 5%.)

## Slide 20: Regulation Exhaustion Rate

## Slide 21: Regulation Exhaustion Rate

## Slide 22: Metric 5: Stats on REGUP Bias for Consecutive 5-min Intervals
Using a 50MW filter, target 15 occurrences or less per month for regulation bias of six or more consecutive 5-minute intervals for peak hours.

## Slide 23: Regulation Bias for Consecutive SCED Intervals

## Slide 24: Regulation Bias for Consecutive SCED Intervals

## Slide 25: Time Error and Contributing Factors
Accumulated Time Error, Load and Wind Ramp, PWRR Error, Start-Up/Shut-Down Hours, STLF Error, and Expected Generation Deviation.

## Slide 26: Time Error Accumulation

## Slide 27: Load Profile

## Slide 28: Net Load Profile

## Slide 29: Load Ramp

## Slide 30: Wind Profile

## Slide 31: Start-Up & Shut-Down Hours

## Slide 32: Short-Term Load Forecast Error

## Slide 33: STLF Error Chart
Notes: Min,Max, 10th, 90th percentile
15 minute intervals
Max of 741MWs on 3/24/2020 08:45

## Slide 34: Expected Generation Deviation

## Slide 35: Expected Generation Deviation

## Slide 36: Expected Generation Deviation

## Slide 37: Questions?
Thank you!