## Slide 1: FIS Stability Re-study for Downsized GINRs
Assuming there is no equipment change to projects.
Scenario 1:
  no stability issues identified in the FIS
  no need to re-study the smaller size.
Scenario 2:
  stability issues identified in the FIS
  mitigation plans identified in the FIS are not related to curtailment (e.g. Changing breaker status/relay settings, system upgrades)
  need to re-study to verify if the stability issue is still there.

## Slide 2: FIS Stability Re-study for Downsized GINRs
Scenario 3:
  stability issues and curtailments identified in the FIS
  If the amount of curtailment is bigger than the amount of downsize, no need to re-study, since the instability is still there.
  If the amount of curtailment is smaller than the amount of downsize, need to re-study to verify if the stability issue is still there.
Examples for scenario 3: a project requires a curtailment of 100 MW among generators in the study region to solve the stability issue
  if project capacity is reduced by 50 MW, no need for re-study
  if project capacity is reduced by 150 MW, need to re-study to see if the curtailment can be taken from the studied project to stabilize.