## Slide 1
2019 UFE Analysis
Randy Roberts
May 2020 WMS Information Session

## Slide 2: UFE Basics 1
UFE (Unaccounted For Energy) is computed as follows:
UFE = Generation – (Load + Losses)
Negative UFE indicates load/losses are overestimated
Sources of UFE include:
■ Generation Measurement Errors
■ DC Tie Inadvertent Energy
■ Load - Missing/Erroneous Usage Data
- Backcast Profile Error
- Load Profile ID Assignment Error
- Theft
■ Losses - Model Error
- Loss Calculation Error
- Loss Code Assignment Error

## Slide 3: UFE Basics 2
Net Generation for Settlement Interval
Profiled Energy Usage
Non-Metered Accounts
Interval Data
Energy Usage
Losses:
Transmission & Distribution
UFE
Net Generation
Compared to
Load Buildup
GAP - - - - - - >

## Slide 4: Protocol Language 11.6 – Unaccounted for Energy Analysis
11.6.1 Overview
(1) ERCOT will provide an annual Unaccounted For Energy (UFE) analysis report consisting of UFE data analysis from the preceding calendar year. This report will be based on final Settlement data and will be posted to the Market Information System (MIS) Public Area by April 30th. The appropriate …
11.6.2 Annual Unaccounted For Energy Analysis Report
The annual UFE analysis report will contain both ERCOT-wide and UFE allocation category quantities as follows:
(a) Total UFE MWhs;
(b) Total UFE cost;
(c) Percent of total UFE to ERCOT Load;
(d) Percent of total UFE cost; and
(e) Notice of any factors that may be contributing to UFE.

## Slide 5: Data Required Per Protocol Section 11.6.2
 | A – Total UFE MWHs | B – Total UFE Cost | C – Percent of Total UFE to ERCOT load | D – Percent of Total UFE Cost
TOTUFE_U1 | 252,851 | -$22,095,272 | 0.066% | 100.00%
UFEIDR_U1 | 227,371 | -$21,485,167 | 0.059% | 97.24%
UFENIDR_U1 | 8,893 | -$97,065 | 0.002% | 0.44%
UFETRANS_U1 | 16,587 | -$513,041 | 0.004% | 2.32%
Legend: | 
TOTUFE_U1 - Total ERCOT Wide UFE | 
UFEIDR_U1 - Distribution IDR UFE | 
UFENIDR_U1 - NIDR UFE | 
UFETRANS_U1 - Transmission IDR UFE | 

## Slide 6: 2010 – 2019 Average Daily % UFE (sorted low to high)

## Slide 7: Most Recent 5 Years - Average Daily % UFE (sorted low to high)

## Slide 8: UFE Monthly MWH

## Slide 9: UFE Monthly Cost

## Slide 10: Historical Yearly Values
 | MWH | COST | % of LOAD | AVG PRICE
2003 | 1,672,727 | $156,733,428 | 0.40% | $41.31
2004 | 1,344,289 | $102,693,690 | 0.40% | $42.00
2005 | 1,082,561 | $174,154,088 | 0.30% | $65.91
2006 | 2,304,458 | $187,975,534 | 0.70% | $51.26
2007 | 2,914,297 | $206,949,832 | 0.90% | $52.77
2008 | 1,541,086 | $134,692,211 | 0.40% | $68.04
2009 | 1,351,187 | $44,857,873 | 0.40% | $30.89
2010 | 1,756,344 | $85,406,714 | 0.55% | $35.74
2011 | 1,453,256 | $31,666,952 | 0.43% | $43.30
2012 | 1,002,761 | $25,945,816 | 0.31% | $26.60
2013 | -395,393 | -$17,061,127 | -0.12% | $31.71
2014 | 298,578 | $2,286,431 | 0.09% | $38.02
2015 | 240,091 | $1,441,929 | 0.07% | $24.80
2016 | 644,293 | $11,037,155 | 0.18% | $22.60
2017 | -452,775 | -$20,469,613 | -0.13% | $26.53
2018 | 657,974 | $7,209,457 | 0.17% | $32.28
2019 | 252,851 | -$22,095,272 | 0.07% | $38.83

## Slide 11: Historical UFE Cost, MWH, and Average MCPE

## Slide 12: Historical UFE as Percent of Load

## Slide 13: Transmission Loss Factor Calculation Review
13.2.3 Transmission Loss Factor Calculations
  The following formulas shall be used to translate the seasonal on-peak and off-peak TLFs into Settlement Interval TLFs.
    TLFi = (SSC * SIELi) + SIC

## Slide 14: 2019 Transmission Loss vs. UFE

## Slide 15: 2020/2021 Transmission Losses (Actual & Forecasted)