## Slide 1
System Operating Limit (SOL) Methodology Change
Dan Woodfin
May 7, 2020

## Slide 2: Overview
ERCOT intends to modify SOL Methodology to better align with NERC interconnection Reliability Operating Limit (IROL) Guideline and associated framework:
  ERCOT plans to post the revised SOL Methodology on Oct. 1st, 2020
  IROL Reliability Guideline, Sept. 2018, https://www.nerc.com/comm/PC_Reliability_Guidelines_DL/Reliability_Guideline_Methods_for_Establishing_IROLs.pdf
  IROL Framework Assessment Report, Sept. 2018, https://www.nerc.com/comm/PC/Methods%20for%20Establishing%20IROLs%20Joint%20Task%20Force%20ME/MEITF_IROL_Framework_Assessment_-_2018-08-21.pdf

## Slide 3: NERC IROL Framework Alignment
Each Reliability Coordinator (RC) shall include in its SOL Methodology a description of how the subsets of SOLs that qualify as IROLs are established. This methodology should, at a minimum:
  Describe the analytical techniques used to study and determine Instability, System Instability, Uncontrolled Separation, and Cascading
  Require that IROLs are established to prevent System Instability
  Require that loss of load greater than 2000 MW caused by Instability, Uncontrolled Separation, or Cascading is unacceptable and warrants the establishment of an IROL

## Slide 4: NERC IROL Reliability Guideline Alignment
Criteria used to trigger cascading assessment is not in SOL Methodology
Cascading Assessment
  Current Criteria
    125% of Emergency Rating
  Proposed Criteria
    125% of Emergency Rating or;
    100% of Relay Loadability Rating
Continuing discussions with TOs on this topic

## Slide 5: Next Steps
ERCOT will perform analysis on existing GTCs to identify potential IROLs with the SOL methodology change
ERCOT will communicate the analysis results with impacted TOs prior to Oct 1st, 2020