## Summary
Release Date: May 13, 2020
FINAL
Seasonal Assessment of Resource Adequacy for the ERCOT Region (SARA)
Summer 2020
SUMMARY
The ERCOT region will likely experience record electric use this summer driven by summer heat.
“There is a lot of uncertainty in today's world, but we are confident that Texas will still be hot this summer,” said ERCOT President and CEO Bill Magness. “Texans will need electric power as they do every summer, and ERCOT is prepared to do our part to keep it flowing reliably."
ERCOT adjusted its peak load forecast to 75,200 MW to account for economic impacts related to COVID-19. The new forecast is 1,496 MW less than what was reported in the preliminary summer SARA and increases the summer 2020 reserve margin to 12.6%, up from 10.6%. However, the new forecast is still higher than ERCOT’s all-time peak demand record of 74,820 MW set on Aug. 12, 2019.
The grid operator anticipates there will be sufficient generation to meet the expected demand under normal/expected operating conditions. However, extreme weather, low wind output and higher-than-normal generation outages may result in the need to declare Energy Emergency Alerts (EEAs).
Since the preliminary summer SARA was released, seven planned wind, solar, and storage projects totaling 979 MW and contributing 276 MW to summer peak began commercial operations.
Approximately 411 MW of planned resource capacity expected to be available during peak demand hours (mostly wind) has been delayed beyond summer 2020, and only one small battery project has been delayed due to COVID-19.

## Scenarios
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Summer 2020 - Final
Release Date: May 13, 2020
Forecasted Capacity and Demand
|  | Operational Resources (thermal and hydro), MW | 65224.3414 | Based on current Seasonal Maximum Sustainable Limits reported through the unit registration process
|  | Switchable Capacity Total, MW | 3490 | Installed capacity of units that can interconnect with other Regions and are available to ERCOT
|  | Less Switchable Capacity Unavailable to ERCOT, MW | -734 | Based on survey responses of Switchable Resource owners
|  | Available Mothballed Capacity, MW | 483 | Based on seasonal Mothball units plus Probability of Return responses of Mothball Resource owners
|  | Capacity from Private Use Networks, MW | 3175.5454 | Average grid injection during the top 20 summer peak load hours over the last three years, plus the forecasted net change in generation capacity available to the ERCOT grid pursuant to Nodal Protocol Section 10.3.2.4.
|  | Coastal Wind, Peak Average Capacity Contribution, MW | 2072.952 | Based on 63% of installed capacity for coastal wind resources (summer season) per ERCOT Nodal Protocols Section 3.2.6.2.2
|  | Panhandle Wind, Peak Average Capacity Contribution, MW | 1278.523 | Based on 29% of installed capacity for panhandle wind resources (summer season) per ERCOT Nodal Protocols Section 3.2.6.2.2
|  | Other Wind, Peak Average Capacity Contribution, MW | 2703.072 | Based on 16% of installed capacity for other wind resources (summer season) per ERCOT Nodal Protocols Section 3.2.6.2.2
|  | Solar Utility-Scale, Peak Average Capacity Contribution, MW | 1883.356 | Based on 76% of rated capacity for solar resources (summer season) per Nodal Protocols Section 3.2.6.2.2
|  | Storage, Peak Average Capacity Contribution, MW | 0 | Based on 0% of rated capacity (summer season); resources assumed to provide regulation reserves rather than sustained capacity available to meet peak loads
|  | RMR Capacity to be under Contract | 0
|  | Capacity Pending Retirement, MW | 0 | Announced retired capacity that is undergoing ERCOT grid reliability reviews pursuant to Nodal Protocol Section 3.14.1.2
|  | Non-Synchronous Ties, Capacity Contribution, MW | 849.974 | Based on net imports during summer 2019 Energy Emergency Alert (EEA) intervals
|  | Planned Thermal Resources with Signed IA, Air Permits and Water Rights, MW | 90 | Based on in-service dates provided by developers
|  | Planned Coastal Wind with Signed IA, Peak Average Capacity Contribution, MW | 186.543 | Based on in-service dates provided by developers and 63% summer capacity contribution for coastal wind resources
|  | Planned Panhandle Wind with Signed IA, Peak Average Capacity Contribution, MW | 0 | Based on in-service dates provided by developers and 29% summer capacity contribution for panhandle wind resources
|  | Planned Other Wind with Signed IA, Peak Average Capacity Contribution, MW | 399.6656 | Based on in-service dates provided by developers and 16% summer capacity contribution for other wind resources
|  | Planned Solar Utility-Scale, Peak Average Capacity Contribution, MW | 1095.54 | Based on in-service dates provided by developers and 76% summer capacity contribution for solar resources
|  | Planned Storage, Peak Average Capacity Contribution, MW | 0 | Based on in-service dates provided by developers and 0% summer capacity contribution for storage resources
| [a] Total Resources, MW |  | 82198.5125
| [b] Peak Demand, MW |  | 75200 | Based on average weather conditions at the time of the summer peak for 2004-2018, and adjusted to reflect the impacts of the COVID-19 pandemic on load and the economy.
| [c] Reserve Capacity [a - b], MW |  | 6998.5125
Range of Potential Risks
|  |  | Forecasted Season Peak Load / Typical Generation Outages | Forecasted Season Peak Load / Extreme Generation Outages | Forecasted Season Peak Load / Extreme Low Wind Output | Extreme Season Peak Load / Typical Generation Outages
|  | Seasonal Load Adjustment | 0 | 0 | 0 | 3216 | Based on 2011 summer weather conditions and COVID-19 impact; the extreme summer forecast is 78,416 MW
|  | Typical Maintenance Outages, Thermal | 38 | 38 | 38 | 38 | Based on the historical average of planned outages for July through August weekdays, hours ending 2 pm - 8 pm, for the last three summer seasons (2017 - 2019)
|  | Typical Forced Outages, Thermal | 4031 | 4031 | 4031 | 4031 | Based on historical average of forced outages for June through September weekdays, hours ending 2 pm - 8 pm, for the last three summer seasons (2017 - 2019)
|  | 95th Percentile Forced Outages, Thermal | 0 | 2932 | 0 | 0 | Based on the 95th percentile of historical forced outages for June through September weekdays, hours ending 2 pm - 8 pm, for the last three summer seasons (2017 - 2019); the adjustment is the 95th percentile value, 6,963 MW, less the typical forced outage amount of 4,031 MW
|  | Low Wind Output Adjustment | 0 | 0 | 5018.7556 | 0 | Based on the 5th percentile of hourly wind capacity factors (output as a percentage of installed capacity) associated with the 100 highest Net Load hours (Load minus wind output) for the 2015-2019 summer Peak Load seasons; this low wind output level is 1,622 MW
| [d] Total Uses of Reserve Capacity |  | 4069 | 7001 | 9087.7556 | 7285
| [e] Capacity Available for Operating Reserves, Normal Operating Conditions [c - d], MW |  | 2929.5125 | -2.4875 | -2089.2431 | -286.4875 | See the Background tab for additional details
Less than 2,300 MW indicates risk of EEA1

## SummerCapacities
Unit Capacities - Summer
| UNIT NAME | GENERATION INTERCONNECTION PROJECT CODE | UNIT CODE | COUNTY | FUEL | CDR ZONE | START YEAR | CAPACITY (MW)
Operational Resources (Thermal)
4 | COMANCHE PEAK U1 |  | CPSES_UNIT1 | SOMERVELL | NUCLEAR | NORTH | 1990 | 1205
5 | COMANCHE PEAK U2 |  | CPSES_UNIT2 | SOMERVELL | NUCLEAR | NORTH | 1993 | 1195
6 | SOUTH TEXAS U1 | 20INR0287 | STP_STP_G1 | MATAGORDA | NUCLEAR | COASTAL | 1988 | 1293.2
7 | SOUTH TEXAS U2 |  | STP_STP_G2 | MATAGORDA | NUCLEAR | COASTAL | 1989 | 1280
8 | COLETO CREEK |  | COLETO_COLETOG1 | GOLIAD | COAL | SOUTH | 1980 | 655
9 | FAYETTE POWER U1 |  | FPPYD1_FPP_G1 | FAYETTE | COAL | SOUTH | 1979 | 604
10 | FAYETTE POWER U2 |  | FPPYD1_FPP_G2 | FAYETTE | COAL | SOUTH | 1980 | 599
11 | FAYETTE POWER U3 |  | FPPYD2_FPP_G3 | FAYETTE | COAL | SOUTH | 1988 | 437
12 | J K SPRUCE U1 |  | CALAVERS_JKS1 | BEXAR | COAL | SOUTH | 1992 | 560
13 | J K SPRUCE U2 |  | CALAVERS_JKS2 | BEXAR | COAL | SOUTH | 2010 | 785
14 | LIMESTONE U1 |  | LEG_LEG_G1 | LIMESTONE | COAL | NORTH | 1985 | 824
15 | LIMESTONE U2 |  | LEG_LEG_G2 | LIMESTONE | COAL | NORTH | 1986 | 836
16 | MARTIN LAKE U1 |  | MLSES_UNIT1 | RUSK | COAL | NORTH | 1977 | 800
17 | MARTIN LAKE U2 |  | MLSES_UNIT2 | RUSK | COAL | NORTH | 1978 | 805
18 | MARTIN LAKE U3 |  | MLSES_UNIT3 | RUSK | COAL | NORTH | 1979 | 805
19 | OAK GROVE SES U1 |  | OGSES_UNIT1A | ROBERTSON | COAL | NORTH | 2010 | 855
20 | OAK GROVE SES U2 |  | OGSES_UNIT2 | ROBERTSON | COAL | NORTH | 2011 | 855
21 | OKLAUNION U1 |  | OKLA_OKLA_G1 | WILBARGER | COAL | WEST | 1986 | 650
22 | SAN MIGUEL U1 |  | SANMIGL_G1 | ATASCOSA | COAL | SOUTH | 1982 | 391
23 | SANDY CREEK U1 |  | SCES_UNIT1 | MCLENNAN | COAL | NORTH | 2013 | 940
24 | TWIN OAKS U1 |  | TNP_ONE_TNP_O_1 | ROBERTSON | COAL | NORTH | 1990 | 155
25 | TWIN OAKS U2 |  | TNP_ONE_TNP_O_2 | ROBERTSON | COAL | NORTH | 1991 | 155
26 | W A PARISH U5 |  | WAP_WAP_G5 | FORT BEND | COAL | HOUSTON | 1977 | 664
27 | W A PARISH U6 |  | WAP_WAP_G6 | FORT BEND | COAL | HOUSTON | 1978 | 663
28 | W A PARISH U7 |  | WAP_WAP_G7 | FORT BEND | COAL | HOUSTON | 1980 | 577
29 | W A PARISH U8 |  | WAP_WAP_G8 | FORT BEND | COAL | HOUSTON | 1982 | 610
30 | ARTHUR VON ROSENBERG 1 CTG 1 |  | BRAUNIG_AVR1_CT1 | BEXAR | GAS | SOUTH | 2000 | 164
31 | ARTHUR VON ROSENBERG 1 CTG 2 |  | BRAUNIG_AVR1_CT2 | BEXAR | GAS | SOUTH | 2000 | 164
32 | ARTHUR VON ROSENBERG 1 STG |  | BRAUNIG_AVR1_ST | BEXAR | GAS | SOUTH | 2000 | 190
33 | ATKINS CTG 7 |  | ATKINS_ATKINSG7 | BRAZOS | GAS | NORTH | 1973 | 18
34 | BARNEY M DAVIS CTG 3 |  | B_DAVIS_B_DAVIG3 | NUECES | GAS | COASTAL | 2010 | 157
35 | BARNEY M DAVIS CTG 4 |  | B_DAVIS_B_DAVIG4 | NUECES | GAS | COASTAL | 2010 | 157
36 | BARNEY M DAVIS STG 1 |  | B_DAVIS_B_DAVIG1 | NUECES | GAS | COASTAL | 1974 | 300
37 | BARNEY M DAVIS STG 2 |  | B_DAVIS_B_DAVIG2 | NUECES | GAS | COASTAL | 1976 | 319
38 | BASTROP ENERGY CENTER CTG 1 |  | BASTEN_GTG1100 | BASTROP | GAS | SOUTH | 2002 | 150
39 | BASTROP ENERGY CENTER CTG 2 |  | BASTEN_GTG2100 | BASTROP | GAS | SOUTH | 2002 | 150
40 | BASTROP ENERGY CENTER STG |  | BASTEN_ST0100 | BASTROP | GAS | SOUTH | 2002 | 233
41 | BOSQUE ENERGY CENTER CTG 1 |  | BOSQUESW_BSQSU_1 | BOSQUE | GAS | NORTH | 2000 | 143
42 | BOSQUE ENERGY CENTER CTG 2 |  | BOSQUESW_BSQSU_2 | BOSQUE | GAS | NORTH | 2000 | 143
43 | BOSQUE ENERGY CENTER CTG 3 |  | BOSQUESW_BSQSU_3 | BOSQUE | GAS | NORTH | 2001 | 145
44 | BOSQUE ENERGY CENTER STG 4 |  | BOSQUESW_BSQSU_4 | BOSQUE | GAS | NORTH | 2001 | 79.5
45 | BOSQUE ENERGY CENTER STG 5 |  | BOSQUESW_BSQSU_5 | BOSQUE | GAS | NORTH | 2009 | 213.5
46 | BRAZOS VALLEY CTG 1 |  | BVE_UNIT1 | FORT BEND | GAS | HOUSTON | 2003 | 149.7
47 | BRAZOS VALLEY CTG 2 |  | BVE_UNIT2 | FORT BEND | GAS | HOUSTON | 2003 | 149.7
48 | BRAZOS VALLEY STG 3 |  | BVE_UNIT3 | FORT BEND | GAS | HOUSTON | 2003 | 257.9
49 | CALENERGY-FALCON SEABOARD CTG 1 |  | FLCNS_UNIT1 | HOWARD | GAS | WEST | 1987 | 75
50 | CALENERGY-FALCON SEABOARD CTG 2 |  | FLCNS_UNIT2 | HOWARD | GAS | WEST | 1987 | 75
51 | CALENERGY-FALCON SEABOARD STG 3 |  | FLCNS_UNIT3 | HOWARD | GAS | WEST | 1988 | 70
52 | CALHOUN (PORT COMFORT) CTG 1 |  | CALHOUN_UNIT1 | CALHOUN | GAS | COASTAL | 2017 | 44
53 | CALHOUN (PORT COMFORT) CTG 2 |  | CALHOUN_UNIT2 | CALHOUN | GAS | COASTAL | 2017 | 44
54 | CASTLEMAN CHAMON CTG 1 |  | CHAMON_CTG_0101 | HARRIS | GAS | HOUSTON | 2017 | 44
55 | CASTLEMAN CHAMON CTG 2 |  | CHAMON_CTG_0301 | HARRIS | GAS | HOUSTON | 2017 | 44
56 | CEDAR BAYOU 4 CTG 1 |  | CBY4_CT41 | CHAMBERS | GAS | HOUSTON | 2009 | 163
57 | CEDAR BAYOU 4 CTG 2 |  | CBY4_CT42 | CHAMBERS | GAS | HOUSTON | 2009 | 163
58 | CEDAR BAYOU 4 STG |  | CBY4_ST04 | CHAMBERS | GAS | HOUSTON | 2009 | 178
59 | CEDAR BAYOU STG 1 |  | CBY_CBY_G1 | CHAMBERS | GAS | HOUSTON | 1970 | 745
60 | CEDAR BAYOU STG 2 |  | CBY_CBY_G2 | CHAMBERS | GAS | HOUSTON | 1972 | 749
61 | COLORADO BEND ENERGY CENTER CTG 1 | 20INR0301 | CBEC_GT1 | WHARTON | GAS | SOUTH | 2007 | 70
62 | COLORADO BEND ENERGY CENTER CTG 2 | 20INR0301 | CBEC_GT2 | WHARTON | GAS | SOUTH | 2007 | 62
63 | COLORADO BEND ENERGY CENTER CTG 3 | 20INR0301 | CBEC_GT3 | WHARTON | GAS | SOUTH | 2008 | 69
64 | COLORADO BEND ENERGY CENTER CTG 4 | 20INR0301 | CBEC_GT4 | WHARTON | GAS | SOUTH | 2008 | 63
65 | COLORADO BEND ENERGY CENTER STG 1 | 20INR0301 | CBEC_STG1 | WHARTON | GAS | SOUTH | 2007 | 101
66 | COLORADO BEND ENERGY CENTER STG 2 | 20INR0301 | CBEC_STG2 | WHARTON | GAS | SOUTH | 2008 | 103
67 | COLORADO BEND II CTG 7 | 18INR0077 | CBECII_CT7 | WHARTON | GAS | SOUTH | 2017 | 329.3
68 | COLORADO BEND II CTG 8 | 18INR0077 | CBECII_CT8 | WHARTON | GAS | SOUTH | 2017 | 335
69 | COLORADO BEND II STG 9 | 18INR0077 | CBECII_STG9 | WHARTON | GAS | SOUTH | 2017 | 478.4
70 | CVC CHANNELVIEW CTG 1 |  | CVC_CVC_G1 | HARRIS | GAS | HOUSTON | 2008 | 169
71 | CVC CHANNELVIEW CTG 2 |  | CVC_CVC_G2 | HARRIS | GAS | HOUSTON | 2008 | 165
72 | CVC CHANNELVIEW CTG 3 |  | CVC_CVC_G3 | HARRIS | GAS | HOUSTON | 2008 | 165
73 | CVC CHANNELVIEW STG 5 |  | CVC_CVC_G5 | HARRIS | GAS | HOUSTON | 2008 | 144
74 | DANSBY CTG 2 |  | DANSBY_DANSBYG2 | BRAZOS | GAS | NORTH | 2004 | 45
75 | DANSBY CTG 3 |  | DANSBY_DANSBYG3 | BRAZOS | GAS | NORTH | 2010 | 47
76 | DANSBY STG 1 |  | DANSBY_DANSBYG1 | BRAZOS | GAS | NORTH | 1978 | 107
77 | DECKER CREEK CTG 1 |  | DECKER_DPGT_1 | TRAVIS | GAS | SOUTH | 1989 | 48
78 | DECKER CREEK CTG 2 |  | DECKER_DPGT_2 | TRAVIS | GAS | SOUTH | 1989 | 48
79 | DECKER CREEK CTG 3 |  | DECKER_DPGT_3 | TRAVIS | GAS | SOUTH | 1989 | 48
80 | DECKER CREEK CTG 4 |  | DECKER_DPGT_4 | TRAVIS | GAS | SOUTH | 1989 | 48
81 | DECKER CREEK STG 1 |  | DECKER_DPG1 | TRAVIS | GAS | SOUTH | 1971 | 315
82 | DECKER CREEK STG 2 |  | DECKER_DPG2 | TRAVIS | GAS | SOUTH | 1978 | 420
83 | DECORDOVA CTG 1 |  | DCSES_CT10 | HOOD | GAS | NORTH | 1990 | 69
84 | DECORDOVA CTG 2 |  | DCSES_CT20 | HOOD | GAS | NORTH | 1990 | 69
85 | DECORDOVA CTG 3 |  | DCSES_CT30 | HOOD | GAS | NORTH | 1990 | 68
86 | DECORDOVA CTG 4 |  | DCSES_CT40 | HOOD | GAS | NORTH | 1990 | 69
87 | DEER PARK ENERGY CENTER CTG 1 |  | DDPEC_GT1 | HARRIS | GAS | HOUSTON | 2002 | 172
88 | DEER PARK ENERGY CENTER CTG 2 |  | DDPEC_GT2 | HARRIS | GAS | HOUSTON | 2002 | 182
89 | DEER PARK ENERGY CENTER CTG 3 |  | DDPEC_GT3 | HARRIS | GAS | HOUSTON | 2002 | 172
90 | DEER PARK ENERGY CENTER CTG 4 |  | DDPEC_GT4 | HARRIS | GAS | HOUSTON | 2002 | 182
91 | DEER PARK ENERGY CENTER CTG 6 |  | DDPEC_GT6 | HARRIS | GAS | HOUSTON | 2014 | 156
92 | DEER PARK ENERGY CENTER STG 1 |  | DDPEC_ST1 | HARRIS | GAS | HOUSTON | 2002 | 287
93 | DENTON ENERGY CENTER IC A |  | DEC_AGR_A | DENTON | GAS | NORTH | 2018 | 56.5
94 | DENTON ENERGY CENTER IC B |  | DEC_AGR_B | DENTON | GAS | NORTH | 2018 | 56.5
95 | DENTON ENERGY CENTER IC C |  | DEC_AGR_C | DENTON | GAS | NORTH | 2018 | 56.5
96 | DENTON ENERGY CENTER IC D |  | DEC_AGR_D | DENTON | GAS | NORTH | 2018 | 56.5
97 | ECTOR COUNTY ENERGY CTG 1 |  | ECEC_G1 | ECTOR | GAS | WEST | 2015 | 147
98 | ECTOR COUNTY ENERGY CTG 2 |  | ECEC_G2 | ECTOR | GAS | WEST | 2015 | 147
99 | ELK STATION IC 3 |  | AEEC_ELK_3 | HALE | GAS | PANHANDLE | 2016 | 190
100 | ENNIS POWER STATION CTG 2 | 21INR0448 | ETCCS_CT1 | ELLIS | GAS | NORTH | 2002 | 204
101 | ENNIS POWER STATION STG 1 | 21INR0448 | ETCCS_UNIT1 | ELLIS | GAS | NORTH | 2002 | 115
102 | EXTEX LAPORTE GEN STN CTG 1 |  | AZ_AZ_G1 | HARRIS | GAS | HOUSTON | 2009 | 36
103 | EXTEX LAPORTE GEN STN CTG 2 |  | AZ_AZ_G2 | HARRIS | GAS | HOUSTON | 2009 | 36
104 | EXTEX LAPORTE GEN STN CTG 3 |  | AZ_AZ_G3 | HARRIS | GAS | HOUSTON | 2009 | 36
105 | EXTEX LAPORTE GEN STN CTG 4 |  | AZ_AZ_G4 | HARRIS | GAS | HOUSTON | 2009 | 36
106 | FERGUSON REPLACEMENT CTG 1 |  | FERGCC_FERGGT1 | LLANO | GAS | SOUTH | 2014 | 169
107 | FERGUSON REPLACEMENT CTG 2 |  | FERGCC_FERGGT2 | LLANO | GAS | SOUTH | 2014 | 169
108 | FERGUSON REPLACEMENT STG 1 |  | FERGCC_FERGST1 | LLANO | GAS | SOUTH | 2014 | 182
109 | FORNEY ENERGY CENTER CTG 11 |  | FRNYPP_GT11 | KAUFMAN | GAS | NORTH | 2003 | 165
110 | FORNEY ENERGY CENTER CTG 12 |  | FRNYPP_GT12 | KAUFMAN | GAS | NORTH | 2003 | 157
111 | FORNEY ENERGY CENTER CTG 13 |  | FRNYPP_GT13 | KAUFMAN | GAS | NORTH | 2003 | 157
112 | FORNEY ENERGY CENTER CTG 21 |  | FRNYPP_GT21 | KAUFMAN | GAS | NORTH | 2003 | 165
113 | FORNEY ENERGY CENTER CTG 22 |  | FRNYPP_GT22 | KAUFMAN | GAS | NORTH | 2003 | 157
114 | FORNEY ENERGY CENTER CTG 23 |  | FRNYPP_GT23 | KAUFMAN | GAS | NORTH | 2003 | 157
115 | FORNEY ENERGY CENTER STG 10 |  | FRNYPP_ST10 | KAUFMAN | GAS | NORTH | 2003 | 406
116 | FORNEY ENERGY CENTER STG 20 |  | FRNYPP_ST20 | KAUFMAN | GAS | NORTH | 2003 | 406
117 | FREESTONE ENERGY CENTER CTG 1 |  | FREC_GT1 | FREESTONE | GAS | NORTH | 2002 | 147
118 | FREESTONE ENERGY CENTER CTG 2 |  | FREC_GT2 | FREESTONE | GAS | NORTH | 2002 | 147
119 | FREESTONE ENERGY CENTER CTG 4 |  | FREC_GT4 | FREESTONE | GAS | NORTH | 2002 | 145
120 | FREESTONE ENERGY CENTER CTG 5 |  | FREC_GT5 | FREESTONE | GAS | NORTH | 2002 | 145
121 | FREESTONE ENERGY CENTER STG 3 |  | FREC_ST3 | FREESTONE | GAS | NORTH | 2002 | 169
122 | FREESTONE ENERGY CENTER STG 6 |  | FREC_ST6 | FREESTONE | GAS | NORTH | 2002 | 168
123 | FRIENDSWOOD G |  | FEGC_UNIT1 | HARRIS | GAS | HOUSTON | 2018 | 119
124 | GRAHAM STG 1 |  | GRSES_UNIT1 | YOUNG | GAS | WEST | 1960 | 234
125 | GRAHAM STG 2 |  | GRSES_UNIT2 | YOUNG | GAS | WEST | 1969 | 390
126 | GREENS BAYOU CTG 73 |  | GBY_GBYGT73 | HARRIS | GAS | HOUSTON | 1976 | 56
127 | GREENS BAYOU CTG 74 |  | GBY_GBYGT74 | HARRIS | GAS | HOUSTON | 1976 | 56
128 | GREENS BAYOU CTG 81 |  | GBY_GBYGT81 | HARRIS | GAS | HOUSTON | 1976 | 56
129 | GREENS BAYOU CTG 82 |  | GBY_GBYGT82 | HARRIS | GAS | HOUSTON | 1976 | 50
130 | GREENS BAYOU CTG 83 |  | GBY_GBYGT83 | HARRIS | GAS | HOUSTON | 1976 | 56
131 | GREENS BAYOU CTG 84 |  | GBY_GBYGT84 | HARRIS | GAS | HOUSTON | 1976 | 56
132 | GREENVILLE IC ENGINE PLANT IC 1 |  | STEAM_ENGINE_1 | HUNT | GAS | NORTH | 2010 | 8.2
133 | GREENVILLE IC ENGINE PLANT IC 2 |  | STEAM_ENGINE_2 | HUNT | GAS | NORTH | 2010 | 8.2
134 | GREENVILLE IC ENGINE PLANT IC 3 |  | STEAM_ENGINE_3 | HUNT | GAS | NORTH | 2010 | 8.2
135 | GUADALUPE ENERGY CENTER CTG 1 |  | GUADG_GAS1 | GUADALUPE | GAS | SOUTH | 2000 | 143
136 | GUADALUPE ENERGY CENTER CTG 2 |  | GUADG_GAS2 | GUADALUPE | GAS | SOUTH | 2000 | 143
137 | GUADALUPE ENERGY CENTER CTG 3 |  | GUADG_GAS3 | GUADALUPE | GAS | SOUTH | 2000 | 141
138 | GUADALUPE ENERGY CENTER CTG 4 |  | GUADG_GAS4 | GUADALUPE | GAS | SOUTH | 2000 | 141
139 | GUADALUPE ENERGY CENTER STG 5 |  | GUADG_STM5 | GUADALUPE | GAS | SOUTH | 2000 | 198
140 | GUADALUPE ENERGY CENTER STG 6 |  | GUADG_STM6 | GUADALUPE | GAS | SOUTH | 2000 | 198
141 | HANDLEY STG 3 |  | HLSES_UNIT3 | TARRANT | GAS | NORTH | 1963 | 395
142 | HANDLEY STG 4 |  | HLSES_UNIT4 | TARRANT | GAS | NORTH | 1976 | 435
143 | HANDLEY STG 5 |  | HLSES_UNIT5 | TARRANT | GAS | NORTH | 1977 | 435
144 | HAYS ENERGY FACILITY CSG 1 |  | HAYSEN_HAYSENG1 | HAYS | GAS | SOUTH | 2002 | 210
145 | HAYS ENERGY FACILITY CSG 2 |  | HAYSEN_HAYSENG2 | HAYS | GAS | SOUTH | 2002 | 211
146 | HAYS ENERGY FACILITY CSG 3 |  | HAYSEN_HAYSENG3 | HAYS | GAS | SOUTH | 2002 | 210
147 | HAYS ENERGY FACILITY CSG 4 |  | HAYSEN_HAYSENG4 | HAYS | GAS | SOUTH | 2002 | 213
148 | HIDALGO ENERGY CENTER CTG 1 |  | DUKE_DUKE_GT1 | HIDALGO | GAS | SOUTH | 2000 | 149
149 | HIDALGO ENERGY CENTER CTG 2 |  | DUKE_DUKE_GT2 | HIDALGO | GAS | SOUTH | 2000 | 149
150 | HIDALGO ENERGY CENTER STG 1 |  | DUKE_DUKE_ST1 | HIDALGO | GAS | SOUTH | 2000 | 168
151 | JACK COUNTY GEN FACILITY CTG 1 |  | JACKCNTY_CT1 | JACK | GAS | NORTH | 2006 | 155
152 | JACK COUNTY GEN FACILITY CTG 2 |  | JACKCNTY_CT2 | JACK | GAS | NORTH | 2006 | 155
153 | JACK COUNTY GEN FACILITY CTG 3 |  | JCKCNTY2_CT3 | JACK | GAS | NORTH | 2011 | 150
154 | JACK COUNTY GEN FACILITY CTG 4 |  | JCKCNTY2_CT4 | JACK | GAS | NORTH | 2011 | 150
155 | JACK COUNTY GEN FACILITY STG 1 |  | JACKCNTY_STG | JACK | GAS | NORTH | 2006 | 295
156 | JACK COUNTY GEN FACILITY STG 2 |  | JCKCNTY2_ST2 | JACK | GAS | NORTH | 2011 | 295
157 | JOHNSON COUNTY GEN FACILITY CTG 1 |  | TEN_CT1 | JOHNSON | GAS | NORTH | 1997 | 163
158 | JOHNSON COUNTY GEN FACILITY STG 1 |  | TEN_STG | JOHNSON | GAS | NORTH | 1997 | 106
159 | LAKE HUBBARD STG 1 |  | LHSES_UNIT1 | DALLAS | GAS | NORTH | 1970 | 392
160 | LAKE HUBBARD STG 2 |  | LHSES_UNIT2A | DALLAS | GAS | NORTH | 1973 | 523
161 | LAMAR ENERGY CENTER CTG 11 |  | LPCCS_CT11 | LAMAR | GAS | NORTH | 2000 | 153
162 | LAMAR ENERGY CENTER CTG 12 |  | LPCCS_CT12 | LAMAR | GAS | NORTH | 2000 | 145
163 | LAMAR ENERGY CENTER CTG 21 |  | LPCCS_CT21 | LAMAR | GAS | NORTH | 2000 | 145
164 | LAMAR ENERGY CENTER CTG 22 |  | LPCCS_CT22 | LAMAR | GAS | NORTH | 2000 | 153
165 | LAMAR ENERGY CENTER STG 1 |  | LPCCS_UNIT1 | LAMAR | GAS | NORTH | 2000 | 204
166 | LAMAR ENERGY CENTER STG 2 |  | LPCCS_UNIT2 | LAMAR | GAS | NORTH | 2000 | 204
167 | LAREDO CTG 4 |  | LARDVFTN_G4 | WEBB | GAS | SOUTH | 2008 | 90.1
168 | LAREDO CTG 5 |  | LARDVFTN_G5 | WEBB | GAS | SOUTH | 2008 | 87.3
169 | LEON CREEK PEAKER CTG 1 |  | LEON_CRK_LCPCT1 | BEXAR | GAS | SOUTH | 2004 | 46
170 | LEON CREEK PEAKER CTG 2 |  | LEON_CRK_LCPCT2 | BEXAR | GAS | SOUTH | 2004 | 46
171 | LEON CREEK PEAKER CTG 3 |  | LEON_CRK_LCPCT3 | BEXAR | GAS | SOUTH | 2004 | 46
172 | LEON CREEK PEAKER CTG 4 |  | LEON_CRK_LCPCT4 | BEXAR | GAS | SOUTH | 2004 | 46
173 | LOST PINES POWER CTG 1 |  | LOSTPI_LOSTPGT1 | BASTROP | GAS | SOUTH | 2001 | 170
174 | LOST PINES POWER CTG 2 |  | LOSTPI_LOSTPGT2 | BASTROP | GAS | SOUTH | 2001 | 170
175 | LOST PINES POWER STG 1 |  | LOSTPI_LOSTPST1 | BASTROP | GAS | SOUTH | 2001 | 188
176 | MAGIC VALLEY STATION CTG 1 |  | NEDIN_NEDIN_G1 | HIDALGO | GAS | SOUTH | 2001 | 215
177 | MAGIC VALLEY STATION CTG 2 |  | NEDIN_NEDIN_G2 | HIDALGO | GAS | SOUTH | 2001 | 215
178 | MAGIC VALLEY STATION STG 3 |  | NEDIN_NEDIN_G3 | HIDALGO | GAS | SOUTH | 2001 | 236
179 | MIDLOTHIAN ENERGY FACILITY CTG 1 |  | MDANP_CT1 | ELLIS | GAS | NORTH | 2001 | 229
180 | MIDLOTHIAN ENERGY FACILITY CTG 2 |  | MDANP_CT2 | ELLIS | GAS | NORTH | 2001 | 227
181 | MIDLOTHIAN ENERGY FACILITY CTG 3 |  | MDANP_CT3 | ELLIS | GAS | NORTH | 2001 | 227
182 | MIDLOTHIAN ENERGY FACILITY CTG 4 |  | MDANP_CT4 | ELLIS | GAS | NORTH | 2001 | 227
183 | MIDLOTHIAN ENERGY FACILITY CTG 5 |  | MDANP_CT5 | ELLIS | GAS | NORTH | 2002 | 241
184 | MIDLOTHIAN ENERGY FACILITY CTG 6 |  | MDANP_CT6 | ELLIS | GAS | NORTH | 2002 | 243
185 | MORGAN CREEK CTG 1 |  | MGSES_CT1 | MITCHELL | GAS | WEST | 1988 | 66
186 | MORGAN CREEK CTG 2 |  | MGSES_CT2 | MITCHELL | GAS | WEST | 1988 | 65
187 | MORGAN CREEK CTG 3 |  | MGSES_CT3 | MITCHELL | GAS | WEST | 1988 | 65
188 | MORGAN CREEK CTG 4 |  | MGSES_CT4 | MITCHELL | GAS | WEST | 1988 | 67
189 | MORGAN CREEK CTG 5 |  | MGSES_CT5 | MITCHELL | GAS | WEST | 1988 | 67
190 | MORGAN CREEK CTG 6 |  | MGSES_CT6 | MITCHELL | GAS | WEST | 1988 | 67
191 | MOUNTAIN CREEK STG 6 |  | MCSES_UNIT6 | DALLAS | GAS | NORTH | 1956 | 122
192 | MOUNTAIN CREEK STG 7 |  | MCSES_UNIT7 | DALLAS | GAS | NORTH | 1958 | 118
193 | MOUNTAIN CREEK STG 8 |  | MCSES_UNIT8 | DALLAS | GAS | NORTH | 1967 | 568
194 | NUECES BAY REPOWER CTG 8 |  | NUECES_B_NUECESG8 | NUECES | GAS | COASTAL | 2010 | 157
195 | NUECES BAY REPOWER CTG 9 |  | NUECES_B_NUECESG9 | NUECES | GAS | COASTAL | 2010 | 157
196 | NUECES BAY REPOWER STG 7 |  | NUECES_B_NUECESG7 | NUECES | GAS | COASTAL | 1972 | 319
197 | O W SOMMERS STG 1 |  | CALAVERS_OWS1 | BEXAR | GAS | SOUTH | 1972 | 420
198 | O W SOMMERS STG 2 |  | CALAVERS_OWS2 | BEXAR | GAS | SOUTH | 1974 | 410
199 | ODESSA-ECTOR POWER CTG 11 |  | OECCS_CT11 | ECTOR | GAS | WEST | 2001 | 166.7
200 | ODESSA-ECTOR POWER CTG 12 |  | OECCS_CT12 | ECTOR | GAS | WEST | 2001 | 158.2
201 | ODESSA-ECTOR POWER CTG 21 | 20INR0282 | OECCS_CT21 | ECTOR | GAS | WEST | 2001 | 166.7
202 | ODESSA-ECTOR POWER CTG 22 | 20INR0282 | OECCS_CT22 | ECTOR | GAS | WEST | 2001 | 158.2
203 | ODESSA-ECTOR POWER STG 1 |  | OECCS_UNIT1 | ECTOR | GAS | WEST | 2001 | 206
204 | ODESSA-ECTOR POWER STG 2 | 20INR0282 | OECCS_UNIT2 | ECTOR | GAS | WEST | 2001 | 206
205 | PANDA SHERMAN POWER CTG 1 |  | PANDA_S_SHER1CT1 | GRAYSON | GAS | NORTH | 2014 | 196
206 | PANDA SHERMAN POWER CTG 2 |  | PANDA_S_SHER1CT2 | GRAYSON | GAS | NORTH | 2014 | 195
207 | PANDA SHERMAN POWER STG 1 |  | PANDA_S_SHER1ST1 | GRAYSON | GAS | NORTH | 2014 | 326
208 | PANDA TEMPLE I POWER CTG 1 |  | PANDA_T1_TMPL1CT1 | BELL | GAS | NORTH | 2014 | 195
209 | PANDA TEMPLE I POWER CTG 2 |  | PANDA_T1_TMPL1CT2 | BELL | GAS | NORTH | 2014 | 195
210 | PANDA TEMPLE I POWER STG 1 |  | PANDA_T1_TMPL1ST1 | BELL | GAS | NORTH | 2014 | 312
211 | PANDA TEMPLE II POWER CTG 1 |  | PANDA_T2_TMPL2CT1 | BELL | GAS | NORTH | 2015 | 191.2
212 | PANDA TEMPLE II POWER CTG 2 |  | PANDA_T2_TMPL2CT2 | BELL | GAS | NORTH | 2015 | 191.2
213 | PANDA TEMPLE II POWER STG 1 |  | PANDA_T2_TMPL2ST1 | BELL | GAS | NORTH | 2015 | 334.7
214 | PARIS ENERGY CENTER CTG 1 |  | TNSKA_GT1 | LAMAR | GAS | NORTH | 1989 | 76
215 | PARIS ENERGY CENTER CTG 2 |  | TNSKA_GT2 | LAMAR | GAS | NORTH | 1989 | 76
216 | PARIS ENERGY CENTER STG 1 |  | TNSKA_STG | LAMAR | GAS | NORTH | 1990 | 87
217 | PASADENA COGEN FACILITY CTG 2 |  | PSG_PSG_GT2 | HARRIS | GAS | HOUSTON | 2000 | 164.5
218 | PASADENA COGEN FACILITY CTG 3 |  | PSG_PSG_GT3 | HARRIS | GAS | HOUSTON | 2000 | 164.5
219 | PASADENA COGEN FACILITY STG 2 |  | PSG_PSG_ST2 | HARRIS | GAS | HOUSTON | 2000 | 170.4
220 | PEARSALL ENGINE PLANT IC A |  | PEARSAL2_AGR_A | FRIO | GAS | SOUTH | 2012 | 50.6
221 | PEARSALL ENGINE PLANT IC B |  | PEARSAL2_AGR_B | FRIO | GAS | SOUTH | 2012 | 50.6
222 | PEARSALL ENGINE PLANT IC C |  | PEARSAL2_AGR_C | FRIO | GAS | SOUTH | 2012 | 50.6
223 | PEARSALL ENGINE PLANT IC D |  | PEARSAL2_AGR_D | FRIO | GAS | SOUTH | 2012 | 50.6
224 | PERMIAN BASIN CTG 1 |  | PB2SES_CT1 | WARD | GAS | WEST | 1988 | 63
225 | PERMIAN BASIN CTG 2 |  | PB2SES_CT2 | WARD | GAS | WEST | 1988 | 64
226 | PERMIAN BASIN CTG 3 |  | PB2SES_CT3 | WARD | GAS | WEST | 1988 | 64
227 | PERMIAN BASIN CTG 4 |  | PB2SES_CT4 | WARD | GAS | WEST | 1990 | 64
228 | PERMIAN BASIN CTG 5 |  | PB2SES_CT5 | WARD | GAS | WEST | 1990 | 65
229 | PHR PEAKERS (BAC) CTG 1 |  | BAC_CTG1 | GALVESTON | GAS | HOUSTON | 2018 | 59
230 | PHR PEAKERS (BAC) CTG 2 |  | BAC_CTG2 | GALVESTON | GAS | HOUSTON | 2018 | 61
231 | PHR PEAKERS (BAC) CTG 3 |  | BAC_CTG3 | GALVESTON | GAS | HOUSTON | 2018 | 49
232 | PHR PEAKERS (BAC) CTG 4 |  | BAC_CTG4 | GALVESTON | GAS | HOUSTON | 2018 | 54
233 | PHR PEAKERS (BAC) CTG 5 |  | BAC_CTG5 | GALVESTON | GAS | HOUSTON | 2018 | 54
234 | PHR PEAKERS (BAC) CTG 6 |  | BAC_CTG6 | GALVESTON | GAS | HOUSTON | 2018 | 52
235 | POWERLANE PLANT STG 1 |  | STEAM1A_STEAM_1 | HUNT | GAS | NORTH | 1966 | 17.5
236 | POWERLANE PLANT STG 2 |  | STEAM_STEAM_2 | HUNT | GAS | NORTH | 1967 | 23.5
237 | POWERLANE PLANT STG 3 |  | STEAM_STEAM_3 | HUNT | GAS | NORTH | 1978 | 39.5
238 | QUAIL RUN ENERGY CTG 1 |  | QALSW_GT1 | ECTOR | GAS | WEST | 2007 | 74
239 | QUAIL RUN ENERGY CTG 2 |  | QALSW_GT2 | ECTOR | GAS | WEST | 2007 | 74
240 | QUAIL RUN ENERGY CTG 3 |  | QALSW_GT3 | ECTOR | GAS | WEST | 2008 | 72
241 | QUAIL RUN ENERGY CTG 4 |  | QALSW_GT4 | ECTOR | GAS | WEST | 2008 | 72
242 | QUAIL RUN ENERGY STG 1 |  | QALSW_STG1 | ECTOR | GAS | WEST | 2007 | 98
243 | QUAIL RUN ENERGY STG 2 |  | QALSW_STG2 | ECTOR | GAS | WEST | 2008 | 98
244 | R W MILLER CTG 4 |  | MIL_MILLERG4 | PALO PINTO | GAS | NORTH | 1994 | 100
245 | R W MILLER CTG 5 |  | MIL_MILLERG5 | PALO PINTO | GAS | NORTH | 1994 | 100
246 | R W MILLER STG 1 |  | MIL_MILLERG1 | PALO PINTO | GAS | NORTH | 1968 | 70
247 | R W MILLER STG 2 |  | MIL_MILLERG2 | PALO PINTO | GAS | NORTH | 1972 | 118
248 | R W MILLER STG 3 |  | MIL_MILLERG3 | PALO PINTO | GAS | NORTH | 1975 | 208
249 | RAY OLINGER CTG 4 |  | OLINGR_OLING_4 | COLLIN | GAS | NORTH | 2001 | 75
250 | RAY OLINGER STG 1 |  | OLINGR_OLING_1 | COLLIN | GAS | NORTH | 1967 | 78
251 | RAY OLINGER STG 2 |  | OLINGR_OLING_2 | COLLIN | GAS | NORTH | 1971 | 107
252 | RAY OLINGER STG 3 |  | OLINGR_OLING_3 | COLLIN | GAS | NORTH | 1975 | 146
253 | REDGATE IC A |  | REDGATE_AGR_A | HIDALGO | GAS | SOUTH | 2016 | 56.3
254 | REDGATE IC B |  | REDGATE_AGR_B | HIDALGO | GAS | SOUTH | 2016 | 56.3
255 | REDGATE IC C |  | REDGATE_AGR_C | HIDALGO | GAS | SOUTH | 2016 | 56.3
256 | REDGATE IC D |  | REDGATE_AGR_D | HIDALGO | GAS | SOUTH | 2016 | 56.3
257 | RIO NOGALES POWER CTG 1 |  | RIONOG_CT1 | GUADALUPE | GAS | SOUTH | 2002 | 163
258 | RIO NOGALES POWER CTG 2 | 21INR0328 | RIONOG_CT2 | GUADALUPE | GAS | SOUTH | 2002 | 148
259 | RIO NOGALES POWER CTG 3 | 20INR0272 | RIONOG_CT3 | GUADALUPE | GAS | SOUTH | 2002 | 163
260 | RIO NOGALES POWER STG 4 |  | RIONOG_ST1 | GUADALUPE | GAS | SOUTH | 2002 | 305
261 | SAM RAYBURN POWER CTG 1 |  | RAYBURN_RAYBURG1 | VICTORIA | GAS | SOUTH | 1963 | 11
262 | SAM RAYBURN POWER CTG 2 |  | RAYBURN_RAYBURG2 | VICTORIA | GAS | SOUTH | 1963 | 11
263 | SAM RAYBURN POWER CTG 7 |  | RAYBURN_RAYBURG7 | VICTORIA | GAS | SOUTH | 2003 | 50
264 | SAM RAYBURN POWER CTG 8 |  | RAYBURN_RAYBURG8 | VICTORIA | GAS | SOUTH | 2003 | 50
265 | SAM RAYBURN POWER CTG 9 |  | RAYBURN_RAYBURG9 | VICTORIA | GAS | SOUTH | 2003 | 50
266 | SAM RAYBURN POWER STG 10 |  | RAYBURN_RAYBURG10 | VICTORIA | GAS | SOUTH | 2003 | 40
267 | SAN JACINTO SES CTG 1 |  | SJS_SJS_G1 | HARRIS | GAS | HOUSTON | 1995 | 80
268 | SAN JACINTO SES CTG 2 |  | SJS_SJS_G2 | HARRIS | GAS | HOUSTON | 1995 | 80
269 | SANDHILL ENERGY CENTER CTG 1 |  | SANDHSYD_SH1 | TRAVIS | GAS | SOUTH | 2001 | 47
270 | SANDHILL ENERGY CENTER CTG 2 |  | SANDHSYD_SH2 | TRAVIS | GAS | SOUTH | 2001 | 47
271 | SANDHILL ENERGY CENTER CTG 3 |  | SANDHSYD_SH3 | TRAVIS | GAS | SOUTH | 2001 | 47
272 | SANDHILL ENERGY CENTER CTG 4 |  | SANDHSYD_SH4 | TRAVIS | GAS | SOUTH | 2001 | 47
273 | SANDHILL ENERGY CENTER CTG 5A |  | SANDHSYD_SH_5A | TRAVIS | GAS | SOUTH | 2004 | 142
274 | SANDHILL ENERGY CENTER CTG 6 |  | SANDHSYD_SH6 | TRAVIS | GAS | SOUTH | 2010 | 47
275 | SANDHILL ENERGY CENTER CTG 7 |  | SANDHSYD_SH7 | TRAVIS | GAS | SOUTH | 2010 | 47
276 | SANDHILL ENERGY CENTER STG 5C |  | SANDHSYD_SH_5C | TRAVIS | GAS | SOUTH | 2004 | 139
277 | SILAS RAY CTG 10 |  | SILASRAY_SILAS_10 | CAMERON | GAS | COASTAL | 2004 | 46
278 | SILAS RAY POWER CTG 9 |  | SILASRAY_SILAS_9 | CAMERON | GAS | COASTAL | 1996 | 38
279 | SILAS RAY POWER STG 6 |  | SILASRAY_SILAS_6 | CAMERON | GAS | COASTAL | 1962 | 20
280 | SIM GIDEON STG 1 |  | GIDEON_GIDEONG1 | BASTROP | GAS | SOUTH | 1965 | 130
281 | SIM GIDEON STG 2 |  | GIDEON_GIDEONG2 | BASTROP | GAS | SOUTH | 1968 | 135
282 | SIM GIDEON STG 3 |  | GIDEON_GIDEONG3 | BASTROP | GAS | SOUTH | 1972 | 336
283 | SKY GLOBAL POWER ONE IC A |  | SKY1_SKY1A | COLORADO | GAS | SOUTH | 2016 | 26.7
284 | SKY GLOBAL POWER ONE IC B |  | SKY1_SKY1B | COLORADO | GAS | SOUTH | 2016 | 26.7
285 | STRYKER CREEK STG 1 |  | SCSES_UNIT1A | CHEROKEE | GAS | NORTH | 1958 | 167
286 | STRYKER CREEK STG 2 |  | SCSES_UNIT2 | CHEROKEE | GAS | NORTH | 1965 | 502
287 | T H WHARTON CTG 1 |  | THW_THWGT_1 | HARRIS | GAS | HOUSTON | 1967 | 13
288 | T H WHARTON POWER CTG 31 |  | THW_THWGT31 | HARRIS | GAS | HOUSTON | 1972 | 54
289 | T H WHARTON POWER CTG 32 |  | THW_THWGT32 | HARRIS | GAS | HOUSTON | 1972 | 54
290 | T H WHARTON POWER CTG 33 |  | THW_THWGT33 | HARRIS | GAS | HOUSTON | 1972 | 54
291 | T H WHARTON POWER CTG 34 |  | THW_THWGT34 | HARRIS | GAS | HOUSTON | 1972 | 54
292 | T H WHARTON POWER CTG 41 |  | THW_THWGT41 | HARRIS | GAS | HOUSTON | 1972 | 54
293 | T H WHARTON POWER CTG 42 |  | THW_THWGT42 | HARRIS | GAS | HOUSTON | 1972 | 54
294 | T H WHARTON POWER CTG 43 |  | THW_THWGT43 | HARRIS | GAS | HOUSTON | 1974 | 54
295 | T H WHARTON POWER CTG 44 |  | THW_THWGT44 | HARRIS | GAS | HOUSTON | 1974 | 54
296 | T H WHARTON POWER CTG 51 |  | THW_THWGT51 | HARRIS | GAS | HOUSTON | 1975 | 56
297 | T H WHARTON POWER CTG 52 |  | THW_THWGT52 | HARRIS | GAS | HOUSTON | 1975 | 56
298 | T H WHARTON POWER CTG 53 |  | THW_THWGT53 | HARRIS | GAS | HOUSTON | 1975 | 56
299 | T H WHARTON POWER CTG 54 |  | THW_THWGT54 | HARRIS | GAS | HOUSTON | 1975 | 56
300 | T H WHARTON POWER CTG 55 |  | THW_THWGT55 | HARRIS | GAS | HOUSTON | 1975 | 56
301 | T H WHARTON POWER CTG 56 |  | THW_THWGT56 | HARRIS | GAS | HOUSTON | 1975 | 56
302 | T H WHARTON POWER STG 3 |  | THW_THWST_3 | HARRIS | GAS | HOUSTON | 1974 | 110
303 | T H WHARTON POWER STG 4 |  | THW_THWST_4 | HARRIS | GAS | HOUSTON | 1974 | 110
304 | TEXAS CITY POWER CTG A |  | TXCTY_CTA | GALVESTON | GAS | HOUSTON | 2000 | 80.3
305 | TEXAS CITY POWER CTG B |  | TXCTY_CTB | GALVESTON | GAS | HOUSTON | 2000 | 80.3
306 | TEXAS CITY POWER CTG C |  | TXCTY_CTC | GALVESTON | GAS | HOUSTON | 2000 | 80.3
307 | TEXAS CITY POWER STG |  | TXCTY_ST | GALVESTON | GAS | HOUSTON | 2000 | 124.9
308 | TEXAS GULF SULPHUR CTG 1 |  | TGF_TGFGT_1 | WHARTON | GAS | SOUTH | 1985 | 69
309 | TRINIDAD STG 6 |  | TRSES_UNIT6 | HENDERSON | GAS | NORTH | 1965 | 235
310 | V H BRAUNIG CTG 5 |  | BRAUNIG_VHB6CT5 | BEXAR | GAS | SOUTH | 2009 | 48
311 | V H BRAUNIG CTG 6 |  | BRAUNIG_VHB6CT6 | BEXAR | GAS | SOUTH | 2009 | 48
312 | V H BRAUNIG CTG 7 |  | BRAUNIG_VHB6CT7 | BEXAR | GAS | SOUTH | 2009 | 48
313 | V H BRAUNIG CTG 8 |  | BRAUNIG_VHB6CT8 | BEXAR | GAS | SOUTH | 2009 | 47
314 | V H BRAUNIG STG 1 |  | BRAUNIG_VHB1 | BEXAR | GAS | SOUTH | 1966 | 217
315 | V H BRAUNIG STG 2 |  | BRAUNIG_VHB2 | BEXAR | GAS | SOUTH | 1968 | 230
316 | V H BRAUNIG STG 3 |  | BRAUNIG_VHB3 | BEXAR | GAS | SOUTH | 1970 | 412
317 | VICTORIA CITY (CITYVICT) CTG 1 |  | CITYVICT_CTG01 | VICTORIA | GAS | SOUTH | 2020 | 44
318 | VICTORIA CITY (CITYVICT) CTG 2 |  | CITYVICT_CTG02 | VICTORIA | GAS | SOUTH | 2020 | 44
319 | VICTORIA PORT (VICTPORT) CTG 1 |  | VICTPORT_CTG01 | VICTORIA | GAS | SOUTH | 2019 | 44
320 | VICTORIA PORT (VICTPORT) CTG 2 |  | VICTPORT_CTG02 | VICTORIA | GAS | SOUTH | 2019 | 44
321 | VICTORIA POWER CTG 6 |  | VICTORIA_VICTORG6 | VICTORIA | GAS | SOUTH | 2009 | 160
322 | VICTORIA POWER STG 5 |  | VICTORIA_VICTORG5 | VICTORIA | GAS | SOUTH | 1963 | 125
323 | W A PARISH CTG 1 |  | WAP_WAPGT_1 | FORT BEND | GAS | HOUSTON | 1967 | 13
324 | W A PARISH STG 1 |  | WAP_WAP_G1 | FORT BEND | GAS | HOUSTON | 1958 | 169
325 | W A PARISH STG 2 |  | WAP_WAP_G2 | FORT BEND | GAS | HOUSTON | 1958 | 169
326 | W A PARISH STG 3 |  | WAP_WAP_G3 | FORT BEND | GAS | HOUSTON | 1961 | 240
327 | W A PARISH STG 4 |  | WAP_WAP_G4 | FORT BEND | GAS | HOUSTON | 1968 | 527
328 | WICHITA FALLS CTG 1 |  | WFCOGEN_UNIT1 | WICHITA | GAS | WEST | 1987 | 20
329 | WICHITA FALLS CTG 2 |  | WFCOGEN_UNIT2 | WICHITA | GAS | WEST | 1987 | 20
330 | WICHITA FALLS CTG 3 |  | WFCOGEN_UNIT3 | WICHITA | GAS | WEST | 1987 | 20
331 | WICHITA FALLS STG 4 |  | WFCOGEN_UNIT4 | WICHITA | GAS | WEST | 1987 | 17
332 | WINCHESTER POWER PARK CTG 1 |  | WIPOPA_WPP_G1 | FAYETTE | GAS | SOUTH | 2009 | 44
333 | WINCHESTER POWER PARK CTG 2 |  | WIPOPA_WPP_G2 | FAYETTE | GAS | SOUTH | 2009 | 44
334 | WINCHESTER POWER PARK CTG 3 |  | WIPOPA_WPP_G3 | FAYETTE | GAS | SOUTH | 2009 | 44
335 | WINCHESTER POWER PARK CTG 4 |  | WIPOPA_WPP_G4 | FAYETTE | GAS | SOUTH | 2009 | 44
336 | WISE-TRACTEBEL POWER CTG 1 | 20INR0286 | WCPP_CT1 | WISE | GAS | NORTH | 2004 | 241.4
337 | WISE-TRACTEBEL POWER CTG 2 | 20INR0286 | WCPP_CT2 | WISE | GAS | NORTH | 2004 | 241.4
338 | WISE-TRACTEBEL POWER STG 1 | 20INR0286 | WCPP_ST1 | WISE | GAS | NORTH | 2004 | 298
339 | WOLF HOLLOW 2 CTG 4 | 18INR0076 | WHCCS2_CT4 | HOOD | GAS | NORTH | 2017 | 327.8
340 | WOLF HOLLOW 2 CTG 5 | 18INR0076 | WHCCS2_CT5 | HOOD | GAS | NORTH | 2017 | 329.3
341 | WOLF HOLLOW 2 STG 6 | 18INR0076 | WHCCS2_STG6 | HOOD | GAS | NORTH | 2017 | 458.3
342 | WOLF HOLLOW POWER CTG 1 |  | WHCCS_CT1 | HOOD | GAS | NORTH | 2002 | 212.5
343 | WOLF HOLLOW POWER CTG 2 |  | WHCCS_CT2 | HOOD | GAS | NORTH | 2002 | 212.5
344 | WOLF HOLLOW POWER STG |  | WHCCS_STG | HOOD | GAS | NORTH | 2002 | 280
345 | NACOGDOCHES POWER |  | NACPW_UNIT1 | NACOGDOCHES | BIOMASS | NORTH | 2012 | 105
346 | BIOENERGY AUSTIN WALZEM RD LFG |  | DG_WALZE_4UNITS | BEXAR | BIOMASS | SOUTH | 2002 | 9.8
347 | BIOENERGY TEXAS COVEL GARDENS LFG |  | DG_MEDIN_1UNIT | BEXAR | BIOMASS | SOUTH | 2005 | 9.6
348 | FARMERS BRANCH LANDFILL GAS TO ENERGY |  | DG_HBR_2UNITS | DENTON | BIOMASS | NORTH | 2011 | 3.2
349 | GRAND PRAIRIE LFG |  | DG_TRIRA_1UNIT | DALLAS | BIOMASS | NORTH | 2015 | 4
350 | NELSON GARDENS LFG |  | DG_78252_4UNITS | BEXAR | BIOMASS | SOUTH | 2013 | 4.2
351 | SKYLINE LFG |  | DG_FERIS_4 UNITS | DALLAS | BIOMASS | NORTH | 2007 | 6.4
352 | WM RENEWABLE-AUSTIN LFG |  | DG_SPRIN_4UNITS | TRAVIS | BIOMASS | SOUTH | 2007 | 6.4
353 | WM RENEWABLE-BIOENERGY PARTNERS LFG |  | DG_BIOE_2UNITS | DENTON | BIOMASS | NORTH | 1988 | 6.2
354 | WM RENEWABLE-DFW GAS RECOVERY LFG |  | DG_BIO2_4UNITS | DENTON | BIOMASS | NORTH | 2009 | 6.4
355 | WM RENEWABLE-MESQUITE CREEK LFG |  | DG_FREIH_2UNITS | COMAL | BIOMASS | SOUTH | 2011 | 3.2
356 | WM RENEWABLE-WESTSIDE LFG |  | DG_WSTHL_3UNITS | PARKER | BIOMASS | NORTH | 2010 | 4.8
357 | Operational Capacity Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 64755.2
358
359 | Operational Resources (Hydro)
360 | AMISTAD HYDRO 1 |  | AMISTAD_AMISTAG1 | VAL VERDE | HYDRO | WEST | 1983 | 37.9
361 | AMISTAD HYDRO 2 |  | AMISTAD_AMISTAG2 | VAL VERDE | HYDRO | WEST | 1983 | 37.9
362 | AUSTIN HYDRO 1 |  | AUSTPL_AUSTING1 | TRAVIS | HYDRO | SOUTH | 1940 | 8
363 | AUSTIN HYDRO 2 |  | AUSTPL_AUSTING2 | TRAVIS | HYDRO | SOUTH | 1940 | 9
364 | BUCHANAN HYDRO 1 |  | BUCHAN_BUCHANG1 | LLANO | HYDRO | SOUTH | 1938 | 16
365 | BUCHANAN HYDRO 2 |  | BUCHAN_BUCHANG2 | LLANO | HYDRO | SOUTH | 1938 | 16
366 | BUCHANAN HYDRO 3 |  | BUCHAN_BUCHANG3 | LLANO | HYDRO | SOUTH | 1950 | 17
367 | DENISON DAM 1 |  | DNDAM_DENISOG1 | GRAYSON | HYDRO | NORTH | 1944 | 40
368 | DENISON DAM 2 |  | DNDAM_DENISOG2 | GRAYSON | HYDRO | NORTH | 1948 | 40
369 | EAGLE PASS HYDRO |  | EAGLE_HY_EAGLE_HY1 | MAVERICK | HYDRO | SOUTH | 2005 | 9.6
370 | FALCON HYDRO 1 |  | FALCON_FALCONG1 | STARR | HYDRO | SOUTH | 1954 | 12
371 | FALCON HYDRO 2 |  | FALCON_FALCONG2 | STARR | HYDRO | SOUTH | 1954 | 12
372 | FALCON HYDRO 3 |  | FALCON_FALCONG3 | STARR | HYDRO | SOUTH | 1954 | 12
373 | GRANITE SHOALS HYDRO 1 |  | WIRTZ_WIRTZ_G1 | BURNET | HYDRO | SOUTH | 1951 | 29
374 | GRANITE SHOALS HYDRO 2 |  | WIRTZ_WIRTZ_G2 | BURNET | HYDRO | SOUTH | 1951 | 29
375 | GUADALUPE BLANCO RIVER AUTH-CANYON |  | CANYHY_CANYHYG1 | COMAL | HYDRO | SOUTH | 1989 | 6
376 | INKS HYDRO 1 |  | INKSDA_INKS_G1 | LLANO | HYDRO | SOUTH | 1938 | 14
377 | MARBLE FALLS HYDRO 1 |  | MARBFA_MARBFAG1 | BURNET | HYDRO | SOUTH | 1951 | 21
378 | MARBLE FALLS HYDRO 2 |  | MARBFA_MARBFAG2 | BURNET | HYDRO | SOUTH | 1951 | 20
379 | MARSHALL FORD HYDRO 1 |  | MARSFO_MARSFOG1 | TRAVIS | HYDRO | SOUTH | 1941 | 36
380 | MARSHALL FORD HYDRO 2 |  | MARSFO_MARSFOG2 | TRAVIS | HYDRO | SOUTH | 1941 | 36
381 | MARSHALL FORD HYDRO 3 |  | MARSFO_MARSFOG3 | TRAVIS | HYDRO | SOUTH | 1941 | 36
382 | WHITNEY DAM HYDRO |  | WND_WHITNEY1 | BOSQUE | HYDRO | NORTH | 1953 | 22
383 | WHITNEY DAM HYDRO 2 |  | WND_WHITNEY2 | BOSQUE | HYDRO | NORTH | 1953 | 22
384 | Operational Capacity Total (Hydro) | [6 empty] | 538.4
385 | Hydro Capacity Contribution (Top 20 Hours) |  | HYDRO_CAP_CONT |  |  |  |  | 457.5
386
387 | Operational Hydro Resources, Settlement Only Distributed Generators (SODGs)
388 | ARLINGTON OUTLET HYDROELECTRIC FACILITY |  | DG_OAKHL_1UNIT | TARRANT | HYDRO | NORTH | 2014 | 1.4
389 | GUADALUPE BLANCO RIVER AUTH-LAKEWOOD TAP |  | DG_LKWDT_2UNITS | GONZALES | HYDRO | SOUTH | 1931 | 4.8
390 | GUADALUPE BLANCO RIVER AUTH-MCQUEENEY |  | DG_MCQUE_5UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 7.7
391 | GUADALUPE BLANCO RIVER AUTH-SCHUMANSVILLE |  | DG_SCHUM_2UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 3.6
392 | LEWISVILLE HYDRO-CITY OF GARLAND |  | DG_LWSVL_1UNIT | DENTON | HYDRO | NORTH | 1991 | 2.2
393 | Operational Hydro Resources Total, Settlement Only Distributed Generators (SODGs) | [6 empty] | 19.7
394 | Hydro SODG Capacity Contribution (Highest 20 Peak Load Hours) | [6 empty] | 16.7399
395
396 | Operational Capacity Unavailable due to Extended Outage or Derate |  | OPERATION_UNAVAIL |  |  |  |  | -5.0984
397 | Operational Capacity Total (Including Hydro) |  | OPERATION_TOTAL |  |  |  |  | 65224.3414
398
399 | Operational Resources (Switchable)
400 | ANTELOPE IC 1 |  | AEEC_ANTLP_1 | HALE | GAS | PANHANDLE | 2016 | 54
401 | ANTELOPE IC 2 |  | AEEC_ANTLP_2 | HALE | GAS | PANHANDLE | 2016 | 54
402 | ANTELOPE IC 3 |  | AEEC_ANTLP_3 | HALE | GAS | PANHANDLE | 2016 | 54
403 | ELK STATION CTG 1 |  | AEEC_ELK_1 | HALE | GAS | PANHANDLE | 2016 | 190
404 | ELK STATION CTG 2 |  | AEEC_ELK_2 | HALE | GAS | PANHANDLE | 2016 | 190
405 | TENASKA FRONTIER STATION CTG 1 |  | FTR_FTR_G1 | GRIMES | GAS | NORTH | 2000 | 160
406 | TENASKA FRONTIER STATION CTG 2 |  | FTR_FTR_G2 | GRIMES | GAS | NORTH | 2000 | 160
407 | TENASKA FRONTIER STATION CTG 3 |  | FTR_FTR_G3 | GRIMES | GAS | NORTH | 2000 | 160
408 | TENASKA FRONTIER STATION STG 4 |  | FTR_FTR_G4 | GRIMES | GAS | NORTH | 2000 | 400
409 | TENASKA GATEWAY STATION CTG 1 |  | TGCCS_CT1 | RUSK | GAS | NORTH | 2001 | 156
410 | TENASKA GATEWAY STATION CTG 2 |  | TGCCS_CT2 | RUSK | GAS | NORTH | 2001 | 135
411 | TENASKA GATEWAY STATION CTG 3 |  | TGCCS_CT3 | RUSK | GAS | NORTH | 2001 | 153
412 | TENASKA GATEWAY STATION STG 4 |  | TGCCS_UNIT4 | RUSK | GAS | NORTH | 2001 | 402
413 | TENASKA KIAMICHI STATION 1CT101 |  | KMCHI_1CT101 | FANNIN | GAS | NORTH | 2003 | 151
414 | TENASKA KIAMICHI STATION 1CT201 |  | KMCHI_1CT201 | FANNIN | GAS | NORTH | 2003 | 148
415 | TENASKA KIAMICHI STATION 1ST |  | KMCHI_1ST | FANNIN | GAS | NORTH | 2003 | 310
416 | TENASKA KIAMICHI STATION 2CT101 |  | KMCHI_2CT101 | FANNIN | GAS | NORTH | 2003 | 150
417 | TENASKA KIAMICHI STATION 2CT201 |  | KMCHI_2CT201 | FANNIN | GAS | NORTH | 2003 | 152
418 | TENASKA KIAMICHI STATION 2ST |  | KMCHI_2ST | FANNIN | GAS | NORTH | 2003 | 311
419 | Switchable Capacity Total | [6 empty] | 3490
420
421 | Switchable Capacity Unavailable to ERCOT
422 | ANTELOPE IC 1 |  | AEEC_ANTLP_1_UNAVAIL | HALE | GAS | PANHANDLE | 2017 | -54
423 | ANTELOPE IC 2 |  | AEEC_ANTLP_2_UNAVAIL | HALE | GAS | PANHANDLE | 2017 | 0
424 | ANTELOPE IC 3 |  | AEEC_ANTLP_3_UNAVAIL | HALE | GAS | PANHANDLE | 2017 | 0
425 | ELK STATION CTG 1 |  | AEEC_ELK_1_UNAVAIL | HALE | GAS | PANHANDLE | 2017 | -190
426 | ELK STATION CTG 2 |  | AEEC_ELK_2_UNAVAIL | HALE | GAS | PANHANDLE | 2017 | -190
427 | TENASKA FRONTIER STATION |  | FTR_FTR_UNAVAIL | GRIMES | GAS | NORTH | 2016 | -300
428 | Switchable Capacity Unavailable to ERCOT |  | SWITCH_UNAVAIL |  |  |  |  | -734
429
430 | Available Mothball Capacity based on Owner's Return Probability |  | MOTH_AVAIL |  |  |  |  | 483
431
432 | Private-Use Network Capacity Contribution (Top 20 Hours) |  | PUN_CAP_CONT |  | GAS |  |  | 3134.5454
433 | Private-Use Network Forecast Adjustment (per Protocol 10.3.2.4) |  | PUN_CAP_ADJUST |  | GAS |  |  | 41
434
435 | Operational Resources (Wind)
436 | BAFFIN WIND UNIT1 |  | BAFFIN_UNIT1 | KENEDY | WIND-C | COASTAL | 2016 | 100
437 | BAFFIN WIND UNIT2 |  | BAFFIN_UNIT2 | KENEDY | WIND-C | COASTAL | 2016 | 102
438 | BRUENNING'S BREEZE A |  | BBREEZE_UNIT1 | WILLACY | WIND-C | COASTAL | 2017 | 120
439 | BRUENNING'S BREEZE B |  | BBREEZE_UNIT2 | WILLACY | WIND-C | COASTAL | 2017 | 108
440 | CAMERON COUNTY WIND |  | CAMWIND_UNIT1 | CAMERON | WIND-C | COASTAL | 2016 | 165
441 | CHAPMAN RANCH WIND IA (SANTA CRUZ) |  | SANTACRU_UNIT1 | NUECES | WIND-C | COASTAL | 2017 | 150.6
442 | CHAPMAN RANCH WIND IB (SANTA CRUZ) |  | SANTACRU_UNIT2 | NUECES | WIND-C | COASTAL | 2017 | 98.4
443 | GULF WIND I |  | TGW_T1 | KENEDY | WIND-C | COASTAL | 2009 | 141.6
444 | GULF WIND II |  | TGW_T2 | KENEDY | WIND-C | COASTAL | 2009 | 141.6
445 | KARANKAWA WIND 1A |  | KARAKAW1_UNIT1 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 103.3
446 | KARANKAWA WIND 1B |  | KARAKAW1_UNIT2 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 103.3
447 | KARANKAWA WIND 2 |  | KARAKAW2_UNIT3 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 100.4
448 | LOS VIENTOS WIND I |  | LV1_LV1A | WILLACY | WIND-C | COASTAL | 2013 | 200.1
449 | LOS VIENTOS WIND II |  | LV1_LV1B | WILLACY | WIND-C | COASTAL | 2013 | 201.6
450 | MAGIC VALLEY WIND (REDFISH) 1A |  | REDFISH_MV1A | WILLACY | WIND-C | COASTAL | 2012 | 99.8
451 | MAGIC VALLEY WIND (REDFISH) 1B |  | REDFISH_MV1B | WILLACY | WIND-C | COASTAL | 2012 | 103.5
452 | MIDWAY WIND |  | MIDWIND_UNIT1 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 162.8
453 | PAPALOTE CREEK WIND |  | PAP1_PAP1 | SAN PATRICIO | WIND-C | COASTAL | 2009 | 179.9
454 | PAPALOTE CREEK WIND II |  | COTTON_PAP2 | SAN PATRICIO | WIND-C | COASTAL | 2010 | 200.1
455 | PENASCAL WIND 1 |  | PENA_UNIT1 | KENEDY | WIND-C | COASTAL | 2009 | 160.8
456 | PENASCAL WIND 2 |  | PENA_UNIT2 | KENEDY | WIND-C | COASTAL | 2009 | 141.6
457 | PENASCAL WIND 3 |  | PENA3_UNIT3 | KENEDY | WIND-C | COASTAL | 2011 | 100.8
458 | SAN ROMAN WIND |  | SANROMAN_WIND_1 | CAMERON | WIND-C | COASTAL | 2017 | 95.2
459 | STELLA WIND |  | STELLA_UNIT1 | KENEDY | WIND-C | COASTAL | 2018 | 201
460 | HARBOR WIND |  | DG_NUECE_6UNITS | NUECES | WIND-C | COASTAL | 2012 | 9
461 | BRISCOE WIND |  | BRISCOE_WIND | BRISCOE | WIND-P | PANHANDLE | 2015 | 149.8
462 | CANADIAN BREAKS WIND |  | CN_BRKS_UNIT_1 | OLDHAM | WIND-P | PANHANDLE | 2019 | 210.1
463 | COTTON PLAINS WIND |  | COTPLNS_COTTONPL | FLOYD | WIND-P | PANHANDLE | 2017 | 50.4
464 | DOUG COLBECK'S CORNER (CONWAY) B |  | GRANDVW1_COLB | CARSON | WIND-P | PANHANDLE | 2016 | 100.2
465 | DOUG COLBECK'S CORNER (CONWAY) A |  | GRANDVW1_COLA | CARSON | WIND-P | PANHANDLE | 2016 | 100.2
466 | FALVEZ ASTRA WIND |  | ASTRA_UNIT1 | RANDALL | WIND-P | PANHANDLE | 2017 | 163.2
467 | GRANDVIEW WIND 1 (CONWAY) GV1A |  | GRANDVW1_GV1A | CARSON | WIND-P | PANHANDLE | 2014 | 107.4
468 | GRANDVIEW WIND 1 (CONWAY) GV1B |  | GRANDVW1_GV1B | CARSON | WIND-P | PANHANDLE | 2014 | 103.8
469 | HEREFORD WIND G |  | HRFDWIND_WIND_G | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 99.9
470 | HEREFORD WIND V |  | HRFDWIND_WIND_V | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 100
471 | JUMBO ROAD WIND 1 |  | HRFDWIND_JRDWIND1 | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 146.2
472 | JUMBO ROAD WIND 2 |  | HRFDWIND_JRDWIND2 | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 153.6
473 | LONGHORN WIND NORTH U1 |  | LHORN_N_UNIT1 | FLOYD | WIND-P | PANHANDLE | 2015 | 100
474 | LONGHORN WIND NORTH U2 |  | LHORN_N_UNIT2 | FLOYD | WIND-P | PANHANDLE | 2015 | 100
475 | MARIAH DEL NORTE 1 |  | MARIAH_NORTE1 | PARMER | WIND-P | PANHANDLE | 2017 | 115.2
476 | MARIAH DEL NORTE 2 |  | MARIAH_NORTE2 | PARMER | WIND-P | PANHANDLE | 2017 | 115.2
477 | MCADOO WIND |  | MWEC_G1 | DICKENS | WIND-P | PANHANDLE | 2008 | 150
478 | MIAMI WIND G1 |  | MIAM1_G1 | GRAY | WIND-P | PANHANDLE | 2014 | 144.3
479 | MIAMI WIND G2 |  | MIAM1_G2 | GRAY | WIND-P | PANHANDLE | 2014 | 144.3
480 | OLD SETTLER WIND |  | COTPLNS_OLDSETLR | FLOYD | WIND-P | PANHANDLE | 2017 | 151.2
481 | PANHANDLE WIND 1 U1 |  | PH1_UNIT1 | CARSON | WIND-P | PANHANDLE | 2014 | 109.2
482 | PANHANDLE WIND 1 U2 |  | PH1_UNIT2 | CARSON | WIND-P | PANHANDLE | 2014 | 109.2
483 | PANHANDLE WIND 2 U1 |  | PH2_UNIT1 | CARSON | WIND-P | PANHANDLE | 2014 | 94.2
484 | PANHANDLE WIND 2 U2 |  | PH2_UNIT2 | CARSON | WIND-P | PANHANDLE | 2014 | 96.6
485 | ROUTE 66 WIND |  | ROUTE_66_WIND1 | CARSON | WIND-P | PANHANDLE | 2015 | 150
486 | SALT FORK 1 WIND U1 |  | SALTFORK_UNIT1 | DONLEY | WIND-P | PANHANDLE | 2017 | 64
487 | SALT FORK 1 WIND U2 |  | SALTFORK_UNIT2 | DONLEY | WIND-P | PANHANDLE | 2017 | 110
488 | SOUTH PLAINS WIND 1 U1 |  | SPLAIN1_WIND1 | FLOYD | WIND-P | PANHANDLE | 2015 | 102
489 | SOUTH PLAINS WIND 1 U2 |  | SPLAIN1_WIND2 | FLOYD | WIND-P | PANHANDLE | 2015 | 98
490 | SOUTH PLAINS WIND 2 U1 |  | SPLAIN2_WIND21 | FLOYD | WIND-P | PANHANDLE | 2016 | 148.5
491 | SOUTH PLAINS WIND 2 U2 |  | SPLAIN2_WIND22 | FLOYD | WIND-P | PANHANDLE | 2016 | 151.8
492 | SPINNING SPUR WIND TWO A |  | SSPURTWO_WIND_1 | OLDHAM | WIND-P | PANHANDLE | 2014 | 161
493 | SPINNING SPUR WIND TWO B |  | SSPURTWO_SS3WIND2 | OLDHAM | WIND-P | PANHANDLE | 2015 | 98
494 | SPINNING SPUR WIND TWO C |  | SSPURTWO_SS3WIND1 | OLDHAM | WIND-P | PANHANDLE | 2015 | 96
495 | WAKE WIND 1 |  | WAKEWE_G1 | DICKENS | WIND-P | PANHANDLE | 2016 | 114.9
496 | WAKE WIND 2 |  | WAKEWE_G2 | DICKENS | WIND-P | PANHANDLE | 2016 | 142.3
497 | WHIRLWIND ENERGY |  | WEC_WECG1 | FLOYD | WIND-P | PANHANDLE | 2007 | 57
498 | WOLF FLATS WIND (WIND MGT) |  | DG_TURL_UNIT1 | HALL | WIND-P | PANHANDLE | 2007 | 1
499 | ANACACHO WIND |  | ANACACHO_ANA | KINNEY | WIND-O | SOUTH | 2012 | 99.8
500 | BARTON CHAPEL WIND |  | BRTSW_BCW1 | JACK | WIND-O | NORTH | 2007 | 120
501 | BLUE SUMMIT WIND 1 A | 18INR0072 | BLSUMMIT_BLSMT1_5 | WILBARGER | WIND-O | WEST | 2013 | 8.8
502 | BLUE SUMMIT WIND 1 B | 18INR0072 | BLSUMMIT_BLSMT1_6 | WILBARGER | WIND-O | WEST | 2013 | 124.3
503 | BLUE SUMMIT WIND 2 A |  | BLSUMMIT_UNIT2_25 | WILBARGER | WIND-O | WEST | 2020 | 89.7
504 | BLUE SUMMIT WIND 2 B |  | BLSUMMIT_UNIT2_17 | WILBARGER | WIND-O | WEST | 2020 | 6.7
505 | BOBCAT BLUFF WIND |  | BCATWIND_WIND_1 | ARCHER | WIND-O | WEST | 2012 | 162
506 | BUCKTHORN WIND 1 A |  | BUCKTHRN_UNIT1 | ERATH | WIND-O | NORTH | 2017 | 44.9
507 | BUCKTHORN WIND 1 B |  | BUCKTHRN_UNIT2 | ERATH | WIND-O | NORTH | 2017 | 55.7
508 | BUFFALO GAP WIND 1 |  | BUFF_GAP_UNIT1 | TAYLOR | WIND-O | WEST | 2006 | 120.6
509 | BUFFALO GAP WIND 2_1 |  | BUFF_GAP_UNIT2_1 | TAYLOR | WIND-O | WEST | 2007 | 115.5
510 | BUFFALO GAP WIND 2_2 |  | BUFF_GAP_UNIT2_2 | TAYLOR | WIND-O | WEST | 2007 | 117
511 | BUFFALO GAP WIND 3 |  | BUFF_GAP_UNIT3 | TAYLOR | WIND-O | WEST | 2008 | 170.2
512 | BULL CREEK WIND U1 |  | BULLCRK_WND1 | BORDEN | WIND-O | WEST | 2009 | 88
513 | BULL CREEK WIND U2 |  | BULLCRK_WND2 | BORDEN | WIND-O | WEST | 2009 | 90
514 | CABEZON WIND (RIO BRAVO I WIND) 1 A |  | CABEZON_WIND1 | STARR | WIND-O | SOUTH | 2019 | 115.2
515 | CABEZON WIND (RIO BRAVO I WIND) 1 B |  | CABEZON_WIND2 | STARR | WIND-O | SOUTH | 2019 | 122.4
516 | CALLAHAN WIND |  | CALLAHAN_WND1 | CALLAHAN | WIND-O | WEST | 2004 | 114
517 | CAMP SPRINGS WIND 1 |  | CSEC_CSECG1 | SCURRY | WIND-O | WEST | 2007 | 130.5
518 | CAMP SPRINGS WIND 2 |  | CSEC_CSECG2 | SCURRY | WIND-O | WEST | 2007 | 120
519 | CAPRICORN RIDGE WIND 1 | 17INR0054 | CAPRIDGE_CR1 | STERLING | WIND-O | WEST | 2007 | 214.5
520 | CAPRICORN RIDGE WIND 2 | 17INR0054 | CAPRIDGE_CR2 | STERLING | WIND-O | WEST | 2007 | 149.5
521 | CAPRICORN RIDGE WIND 3 | 17INR0054 | CAPRIDGE_CR3 | STERLING | WIND-O | WEST | 2008 | 186
522 | CAPRICORN RIDGE WIND 4 | 17INR0061 | CAPRIDG4_CR4 | COKE | WIND-O | WEST | 2008 | 121.5
523 | CEDRO HILL WIND 1 |  | CEDROHIL_CHW1 | WEBB | WIND-O | SOUTH | 2010 | 75
524 | CEDRO HILL WIND 2 |  | CEDROHIL_CHW2 | WEBB | WIND-O | SOUTH | 2010 | 75
525 | CHAMPION WIND |  | CHAMPION_UNIT1 | NOLAN | WIND-O | WEST | 2008 | 126.5
526 | DERMOTT WIND 1_1 |  | DERMOTT_UNIT1 | SCURRY | WIND-O | WEST | 2017 | 126.5
527 | DERMOTT WIND 1_2 |  | DERMOTT_UNIT2 | SCURRY | WIND-O | WEST | 2017 | 126.5
528 | DESERT SKY WIND 1 | 17INR0070 | INDNENR_INDNENR | PECOS | WIND-O | WEST | 2002 | 85.1
529 | DESERT SKY WIND 2 | 17INR0070 | INDNENR_INDNENR_2 | PECOS | WIND-O | WEST | 2002 | 85.1
530 | ELBOW CREEK WIND |  | ELB_ELBCREEK | HOWARD | WIND-O | WEST | 2008 | 118.7
531 | ELECTRA WIND 1 |  | DIGBY_UNIT1 | WILBARGER | WIND-O | WEST | 2017 | 98.9
532 | ELECTRA WIND 2 |  | DIGBY_UNIT2 | WILBARGER | WIND-O | WEST | 2017 | 131.1
533 | FLAT TOP WIND I |  | FTWIND_UNIT_1 | MILLS | WIND-O | NORTH | 2018 | 200
534 | FLUVANNA RENEWABLE 1 A |  | FLUVANNA_UNIT1 | SCURRY | WIND-O | WEST | 2017 | 79.8
535 | FLUVANNA RENEWABLE 1 B |  | FLUVANNA_UNIT2 | SCURRY | WIND-O | WEST | 2017 | 75.6
536 | FOARD CITY WIND 1 A |  | FOARDCTY_UNIT1 | FOARD | WIND-O | WEST | 2019 | 186.5
537 | FOARD CITY WIND 1 B |  | FOARDCTY_UNIT2 | FOARD | WIND-O | WEST | 2019 | 163.8
538 | FOREST CREEK WIND |  | MCDLD_FCW1 | GLASSCOCK | WIND-O | WEST | 2007 | 124.2
539 | GOAT WIND |  | GOAT_GOATWIND | STERLING | WIND-O | WEST | 2008 | 80
540 | GOAT WIND 2 |  | GOAT_GOATWIN2 | STERLING | WIND-O | WEST | 2010 | 69.6
541 | GOLDTHWAITE WIND 1 |  | GWEC_GWEC_G1 | MILLS | WIND-O | NORTH | 2014 | 148.6
542 | GOPHER CREEK WIND 1 |  | GOPHER_UNIT1 | BORDEN | WIND-O | WEST | 2020 | 82
543 | GOPHER CREEK WIND 2 |  | GOPHER_UNIT2 | BORDEN | WIND-O | WEST | 2020 | 76
544 | GREEN MOUNTAIN WIND (BRAZOS) U1 |  | BRAZ_WND_WND1 | SCURRY | WIND-O | WEST | 2003 | 99
545 | GREEN MOUNTAIN WIND (BRAZOS) U2 |  | BRAZ_WND_WND2 | SCURRY | WIND-O | WEST | 2003 | 61
546 | GREEN PASTURES WIND I |  | GPASTURE_WIND_I | BAYLOR | WIND-O | WEST | 2015 | 150
547 | VERTIGO WIND (FORMERLY GREEN PASTURES WIND 2) |  | VERTIGO_WIND_I | BAYLOR | WIND-O | WEST | 2015 | 150
548 | GUNSIGHT MOUNTAIN WIND |  | GUNMTN_G1 | HOWARD | WIND-O | WEST | 2016 | 119.9
549 | HACKBERRY WIND |  | HWF_HWFG1 | SHACKELFORD | WIND-O | WEST | 2008 | 163.5
550 | HICKMAN (SANTA RITA WIND) 1 |  | HICKMAN_G1 | REGAN AND IRION | WIND-O | WEST | 2018 | 152.5
551 | HICKMAN (SANTA RITA WIND) 2 |  | HICKMAN_G2 | REGAN AND IRION | WIND-O | WEST | 2018 | 147.5
552 | HIDALGO & STARR WIND 11 |  | MIRASOLE_MIR11 | HIDALGO | WIND-O | SOUTH | 2016 | 52
553 | HIDALGO & STARR WIND 12 |  | MIRASOLE_MIR12 | HIDALGO | WIND-O | SOUTH | 2016 | 98
554 | HIDALGO & STARR WIND 21 |  | MIRASOLE_MIR21 | HIDALGO | WIND-O | SOUTH | 2016 | 100
555 | HORSE CREEK WIND 1 |  | HORSECRK_UNIT1 | HASKELL | WIND-O | WEST | 2017 | 131.1
556 | HORSE CREEK WIND 2 |  | HORSECRK_UNIT2 | HASKELL | WIND-O | WEST | 2017 | 98.9
557 | HORSE HOLLOW WIND 1 | 17INR0052 | H_HOLLOW_WND1 | TAYLOR | WIND-O | WEST | 2005 | 230
558 | HORSE HOLLOW WIND 2 | 17INR0052 | HHOLLOW2_WIND1 | TAYLOR | WIND-O | WEST | 2006 | 184
559 | HORSE HOLLOW WIND 3 | 17INR0052 | HHOLLOW3_WND_1 | TAYLOR | WIND-O | WEST | 2006 | 241.4
560 | HORSE HOLLOW WIND 4 | 17INR0052 | HHOLLOW4_WND1 | TAYLOR | WIND-O | WEST | 2006 | 115
561 | INADALE WIND 1 |  | INDL_INADALE1 | NOLAN | WIND-O | WEST | 2008 | 95
562 | INADALE WIND 2 |  | INDL_INADALE2 | NOLAN | WIND-O | WEST | 2008 | 102
563 | INDIAN MESA WIND |  | INDNNWP_INDNNWP2 | PECOS | WIND-O | WEST | 2001 | 91.9
564 | JAVELINA I WIND 18 |  | BORDAS_JAVEL18 | WEBB | WIND-O | SOUTH | 2015 | 19.7
565 | JAVELINA I WIND 20 |  | BORDAS_JAVEL20 | WEBB | WIND-O | SOUTH | 2015 | 230
566 | JAVELINA II WIND 1 |  | BORDAS2_JAVEL2_A | WEBB | WIND-O | SOUTH | 2017 | 96
567 | JAVELINA II WIND 2 |  | BORDAS2_JAVEL2_B | WEBB | WIND-O | SOUTH | 2017 | 74
568 | JAVELINA II WIND 3 |  | BORDAS2_JAVEL2_C | WEBB | WIND-O | SOUTH | 2017 | 30
569 | KEECHI WIND |  | KEECHI_U1 | JACK | WIND-O | NORTH | 2015 | 110
570 | KING MOUNTAIN WIND (NE) |  | KING_NE_KINGNE | UPTON | WIND-O | WEST | 2001 | 79.7
571 | KING MOUNTAIN WIND (NW) |  | KING_NW_KINGNW | UPTON | WIND-O | WEST | 2001 | 79.7
572 | KING MOUNTAIN WIND (SE) |  | KING_SE_KINGSE | UPTON | WIND-O | WEST | 2001 | 40.5
573 | KING MOUNTAIN WIND (SW) |  | KING_SW_KINGSW | UPTON | WIND-O | WEST | 2001 | 79.7
574 | LANGFORD WIND POWER |  | LGD_LANGFORD | TOM GREEN | WIND-O | WEST | 2009 | 155
575 | LOCKETT WIND FARM |  | LOCKETT_UNIT1 | WILBARGER | WIND-O | WEST | 2019 | 183.7
576 | LOGANS GAP WIND I U1 |  | LGW_UNIT1 | COMANCHE | WIND-O | NORTH | 2015 | 106.3
577 | LOGANS GAP WIND I U2 |  | LGW_UNIT2 | COMANCHE | WIND-O | NORTH | 2015 | 103.8
578 | LONE STAR WIND 1 (MESQUITE) |  | LNCRK_G83 | SHACKELFORD | WIND-O | WEST | 2006 | 194
579 | LONE STAR WIND 2 (POST OAK) U1 |  | LNCRK2_G871 | SHACKELFORD | WIND-O | WEST | 2007 | 98
580 | LONE STAR WIND 2 (POST OAK) U2 |  | LNCRK2_G872 | SHACKELFORD | WIND-O | WEST | 2007 | 100
581 | LORAINE WINDPARK I |  | LONEWOLF_G1 | MITCHELL | WIND-O | WEST | 2010 | 49.5
582 | LORAINE WINDPARK II |  | LONEWOLF_G2 | MITCHELL | WIND-O | WEST | 2010 | 51
583 | LORAINE WINDPARK III |  | LONEWOLF_G3 | MITCHELL | WIND-O | WEST | 2011 | 25.5
584 | LORAINE WINDPARK IV |  | LONEWOLF_G4 | MITCHELL | WIND-O | WEST | 2011 | 24
585 | LOS VIENTOS III WIND |  | LV3_UNIT_1 | STARR | WIND-O | SOUTH | 2015 | 200
586 | LOS VIENTOS IV WIND |  | LV4_UNIT_1 | STARR | WIND-O | SOUTH | 2016 | 200
587 | LOS VIENTOS V WIND |  | LV5_UNIT_1 | STARR | WIND-O | SOUTH | 2016 | 110
588 | MESQUITE CREEK WIND 1 |  | MESQCRK_WND1 | DAWSON | WIND-O | WEST | 2015 | 105.6
589 | MESQUITE CREEK WIND 2 |  | MESQCRK_WND2 | DAWSON | WIND-O | WEST | 2015 | 105.6
590 | NIELS BOHR WIND A (BEARKAT WIND A) |  | NBOHR_UNIT1 | GLASSCOCK | WIND-O | WEST | 2018 | 196.6
591 | NOTREES WIND 1 |  | NWF_NWF1 | WINKLER | WIND-O | WEST | 2009 | 92.6
592 | NOTREES WIND 2 |  | NWF_NWF2 | WINKLER | WIND-O | WEST | 2009 | 60
593 | OCOTILLO WIND |  | OWF_OWF | HOWARD | WIND-O | WEST | 2008 | 58.8
594 | PANTHER CREEK WIND 1 |  | PC_NORTH_PANTHER1 | HOWARD | WIND-O | WEST | 2008 | 142.5
595 | PANTHER CREEK WIND 2 |  | PC_SOUTH_PANTHER2 | HOWARD | WIND-O | WEST | 2019 | 115.5
596 | PANTHER CREEK WIND 3 | 21INR0449 | PC_SOUTH_PANTHER3 | HOWARD | WIND-O | WEST | 2009 | 199.5
597 | PECOS WIND 1 (WOODWARD) |  | WOODWRD1_WOODWRD1 | PECOS | WIND-O | WEST | 2001 | 91.9
598 | PECOS WIND 2 (WOODWARD) |  | WOODWRD2_WOODWRD2 | PECOS | WIND-O | WEST | 2001 | 86
599 | PYRON WIND 1 |  | PYR_PYRON1 | SCURRY | WIND-O | WEST | 2008 | 121.5
600 | PYRON WIND 2 |  | PYR_PYRON2 | SCURRY AND FISHER | WIND-O | WEST | 2008 | 127.5
601 | RANCHERO WIND |  | RANCHERO_UNIT1 | CROCKETT | WIND-O | WEST | 2020 | 150
602 | RANCHERO WIND |  | RANCHERO_UNIT2 | CROCKETT | WIND-O | WEST | 2020 | 150
603 | RATTLESNAKE I WIND ENERGY CENTER G1 |  | RSNAKE_G1 | GLASSCOCK | WIND-O | WEST | 2015 | 104.3
604 | RATTLESNAKE I WIND ENERGY CENTER G2 |  | RSNAKE_G2 | GLASSCOCK | WIND-O | WEST | 2015 | 103
605 | RED CANYON WIND |  | RDCANYON_RDCNY1 | BORDEN | WIND-O | WEST | 2006 | 89.6
606 | ROCK SPRINGS VAL VERDE WIND (FERMI) 1 |  | FERMI_WIND1 | VAL VERDE | WIND-O | WEST | 2017 | 121.9
607 | ROCK SPRINGS VAL VERDE WIND (FERMI) 2 |  | FERMI_WIND2 | VAL VERDE | WIND-O | WEST | 2017 | 27.4
608 | ROSCOE WIND |  | TKWSW1_ROSCOE | NOLAN | WIND-O | WEST | 2008 | 114
609 | ROSCOE WIND 2A |  | TKWSW1_ROSCOE2A | NOLAN | WIND-O | WEST | 2008 | 95
610 | RTS WIND |  | RTS_U1 | MCCULLOCH | WIND-O | SOUTH | 2018 | 160
611 | SAND BLUFF WIND | 20INR0296 | MCDLD_SBW1 | GLASSCOCK | WIND-O | WEST | 2008 | 90
612 | SENDERO WIND ENERGY |  | EXGNSND_WIND_1 | JIM HOGG | WIND-O | SOUTH | 2015 | 76
613 | SEYMOUR HILLS WIND (S_HILLS WIND) |  | S_HILLS_UNIT1 | BAYLOR | WIND-O | WEST | 2019 | 30.2
614 | SENATE WIND |  | SENATEWD_UNIT1 | JACK | WIND-O | NORTH | 2012 | 150
615 | SHANNON WIND |  | SHANNONW_UNIT_1 | CLAY | WIND-O | WEST | 2015 | 204.1
616 | SHERBINO 1 WIND | 19INR0120 | KEO_KEO_SM1 | PECOS | WIND-O | WEST | 2008 | 150
617 | SHERBINO 2 WIND | 19INR0120 | KEO_SHRBINO2 | PECOS | WIND-O | WEST | 2011 | 145
618 | SILVER STAR WIND | 18INR0064 | FLTCK_SSI | ERATH | WIND-O | NORTH | 2008 | 52.8
619 | SNYDER WIND | 20INR0257 | ENAS_ENA1 | SCURRY | WIND-O | WEST | 2007 | 63
620 | SOUTH TRENT WIND |  | STWF_T1 | NOLAN | WIND-O | WEST | 2008 | 98.2
621 | STANTON WIND ENERGY |  | SWEC_G1 | MARTIN | WIND-O | WEST | 2008 | 120
622 | STEPHENS RANCH WIND 1 |  | SRWE1_UNIT1 | BORDEN | WIND-O | WEST | 2014 | 211.2
623 | STEPHENS RANCH WIND 2 |  | SRWE1_SRWE2 | BORDEN | WIND-O | WEST | 2015 | 164.7
624 | SWEETWATER WIND 1 | 18INR0073 | SWEETWND_WND1 | NOLAN | WIND-O | WEST | 2003 | 42.5
625 | SWEETWATER WIND 2A | 17INR0068 | SWEETWN2_WND24 | NOLAN | WIND-O | WEST | 2006 | 16.8
626 | SWEETWATER WIND 2B | 17INR0068 | SWEETWN2_WND2 | NOLAN | WIND-O | WEST | 2004 | 110.8
627 | SWEETWATER WIND 3A |  | SWEETWN3_WND3A | NOLAN | WIND-O | WEST | 2011 | 33.6
628 | SWEETWATER WIND 3B |  | SWEETWN3_WND3B | NOLAN | WIND-O | WEST | 2011 | 118.6
629 | SWEETWATER WIND 4-5 |  | SWEETWN4_WND5 | NOLAN | WIND-O | WEST | 2007 | 85
630 | SWEETWATER WIND 4-4B |  | SWEETWN4_WND4B | NOLAN | WIND-O | WEST | 2007 | 112
631 | SWEETWATER WIND 4-4A |  | SWEETWN4_WND4A | NOLAN | WIND-O | WEST | 2007 | 125
632 | TAHOKA WIND 1 |  | TAHOKA_UNIT_1 | LYNN | WIND-O | WEST | 2019 | 150
633 | TAHOKA WIND 2 |  | TAHOKA_UNIT_2 | LYNN | WIND-O | WEST | 2019 | 150
634 | TEXAS BIG SPRING WIND A |  | SGMTN_SIGNALMT | HOWARD | WIND-O | WEST | 1999 | 27.7
635 | TEXAS BIG SPRING WIND B |  | SGMTN_SIGNALM2 | HOWARD | WIND-O | WEST | 1999 | 6.6
636 | TORRECILLAS WIND 1 |  | TORR_UNIT1_25 | WEBB | WIND-O | SOUTH | 2019 | 150
637 | TORRECILLAS WIND 2 |  | TORR_UNIT2_23 | WEBB | WIND-O | SOUTH | 2019 | 23
638 | TORRECILLAS WIND 3 |  | TORR_UNIT2_25 | WEBB | WIND-O | SOUTH | 2019 | 127.5
639 | TRENT WIND | 17INR0069 | TRENT_TRENT | NOLAN | WIND-O | WEST | 2001 | 150
640 | TRINITY HILLS WIND 1 | 20INR0019 | TRINITY_TH1_BUS1 | ARCHER | WIND-O | WEST | 2012 | 103.4
641 | TRINITY HILLS WIND 2 | 20INR0019 | TRINITY_TH1_BUS2 | ARCHER | WIND-O | WEST | 2012 | 94.6
642 | TURKEY TRACK WIND |  | TTWEC_G1 | NOLAN | WIND-O | WEST | 2008 | 169.5
643 | TYLER BLUFF WIND |  | TYLRWIND_UNIT1 | COOKE | WIND-O | NORTH | 2017 | 125.6
644 | WHITETAIL WIND |  | EXGNWTL_WIND_1 | WEBB | WIND-O | SOUTH | 2012 | 92.3
645 | WINDTHORST 2 WIND |  | WNDTHST2_UNIT1 | ARCHER | WIND-O | WEST | 2014 | 67.6
646 | WKN MOZART WIND |  | MOZART_WIND_1 | KENT | WIND-O | WEST | 2012 | 30
647 | WILLOW SPRINGS WIND A |  | SALVTION_UNIT1 | HASKELL | WIND-O | WEST | 2017 | 125
648 | WILLOW SPRINGS WIND B |  | SALVTION_UNIT2 | HASKELL | WIND-O | WEST | 2017 | 125
649 | WILSON RANCH (INFINITY LIVE OAK WIND) |  | WL_RANCH_UNIT1 | SCHLEICHER | WIND-O | WEST | 2020 | 199.5
650 | WOLF RIDGE WIND |  | WHTTAIL_WR1 | COOKE | WIND-O | NORTH | 2008 | 112.5
651 | TSTC WEST TEXAS WIND |  | DG_ROSC2_1UNIT | NOLAN | WIND-O | WEST | 2008 | 2
652 | Operational Capacity Total (Wind) | [6 empty] | 24593.3
653
654 | Operational Wind Capacity Sub-total (Coastal Counties) |  | WIND_OPERATIONAL_C |  |  |  |  | 3290.4
655 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PEAK_PCT_C | % |  |  |  | 63
656
657 | Operational Wind Capacity Sub-total (Panhandle Counties) |  | WIND_OPERATIONAL_P |  |  |  |  | 4408.7
658 | Wind Peak Average Capacity Percentage (Panhandle) |  | WIND_PEAK_PCT_P |  |  |  |  | 29
659
660 | Operational Wind Capacity Sub-total (Other Counties) |  | WIND_OPERATIONAL_O |  |  |  |  | 16894.2
661 | Wind Peak Average Capacity Percentage (Other) |  | WIND_PEAK_PCT_O |  |  |  |  | 16
662
663 | Operational Resources (Solar)
664 | ACACIA SOLAR |  | ACACIA_UNIT_1 | PRESIDIO | SOLAR | WEST | 2012 | 10
665 | BHE SOLAR PEARL PROJECT (SIRIUS 2) |  | SIRIUS_UNIT2 | PECOS | SOLAR | WEST | 2017 | 49.1
666 | BLUEBELL SOLAR (CAPRICORN RIDGE SOLAR) |  | CAPRIDG4_BB_PV | STERLING | SOLAR | WEST | 2019 | 30
667 | BNB LAMESA SOLAR (PHASE I) |  | LMESASLR_UNIT1 | DAWSON | SOLAR | WEST | 2018 | 101.6
668 | BNB LAMESA SOLAR (PHASE II) |  | LMESASLR_IVORY | DAWSON | SOLAR | WEST | 2018 | 50
669 | CASTLE GAP SOLAR |  | CASL_GAP_UNIT1 | UPTON | SOLAR | WEST | 2018 | 180
670 | FS BARILLA SOLAR-PECOS |  | HOVEY_UNIT1 | PECOS | SOLAR | WEST | 2015 | 22
671 | FS EAST PECOS SOLAR |  | BOOTLEG_UNIT1 | PECOS | SOLAR | WEST | 2017 | 121.1
672 | OCI ALAMO 1 SOLAR |  | OCI_ALM1_UNIT1 | BEXAR | SOLAR | SOUTH | 2013 | 39.2
673 | OCI ALAMO 4 SOLAR-BRACKETVILLE |  | ECLIPSE_UNIT1 | KINNEY | SOLAR | SOUTH | 2014 | 37.6
674 | OCI ALAMO 5 (DOWNIE RANCH) |  | HELIOS_UNIT1 | UVALDE | SOLAR | SOUTH | 2015 | 95
675 | OCI ALAMO 6 (SIRIUS/WEST TEXAS) |  | SIRIUS_UNIT1 | PECOS | SOLAR | WEST | 2017 | 110.2
676 | OCI ALAMO 7 (PAINT CREEK) |  | SOLARA_UNIT1 | HASKELL | SOLAR | WEST | 2016 | 112
677 | PHOEBE SOLAR 1 |  | PHOEBE_UNIT1 | WINKLER | SOLAR | WEST | 2019 | 125.1
678 | PHOEBE SOLAR 2 |  | PHOEBE_UNIT2 | WINKLER | SOLAR | WEST | 2019 | 128.1
679 | QUEEN SOLAR PHASE I |  | QUEEN_SL_SOLAR1 | UPTON | SOLAR | WEST | 2020 | 102.5
680 | QUEEN SOLAR PHASE I |  | QUEEN_SL_SOLAR2 | UPTON | SOLAR | WEST | 2020 | 102.5
681 | RE ROSEROCK SOLAR 1 |  | REROCK_UNIT1 | PECOS | SOLAR | WEST | 2016 | 78.8
682 | RE ROSEROCK SOLAR 2 |  | REROCK_UNIT2 | PECOS | SOLAR | WEST | 2016 | 78.8
683 | RIGGINS (SE BUCKTHORN WESTEX SOLAR) |  | RIGGINS_UNIT1 | PECOS | SOLAR | WEST | 2018 | 150
684 | SOLAIREHOLMAN 1 |  | LASSO_UNIT1 | BREWSTER | SOLAR | WEST | 2018 | 50
685 | SP-TX-12-PHASE B |  | SPTX12B_UNIT1 | UPTON | SOLAR | WEST | 2017 | 157.5
686 | WAYMARK SOLAR |  | WAYMARK_UNIT1 | UPTON | SOLAR | WEST | 2018 | 182
687 | WEBBERVILLE SOLAR |  | WEBBER_S_WSP1 | TRAVIS | SOLAR | SOUTH | 2011 | 26.7
688 | WEST OF PECOS SOLAR |  | W_PECOS_UNIT1 | REEVES | SOLAR | WEST | 2019 | 101
689 | ALEXIS SOLAR |  | DG_ALEXIS_ALEXIS | BROOKS | SOLAR | SOUTH | 2019 | 10
690 | BECK 1 |  | DG_CECSOLAR_DG_BECK1 | BEXAR | SOLAR | SOUTH | 2016 | 1
691 | BLUE WING 1 SOLAR |  | DG_BROOK_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.6
692 | BLUE WING 2 SOLAR |  | DG_ELMEN_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.3
693 | BOVINE SOLAR LLC |  | DG_BOVINE_BOVINE | AUSTIN | SOLAR | SOUTH | 2018 | 5
694 | BOVINE SOLAR LLC |  | DG_BOVINE2_BOVINE2 | AUSTIN | SOLAR | SOUTH | 2018 | 5
695 | BRONSON SOLAR I |  | DG_BRNSN_BRNSN | FORT BEND | SOLAR | HOUSTON | 2018 | 5
696 | BRONSON SOLAR II |  | DG_BRNSN2_BRNSN2 | FORT BEND | SOLAR | HOUSTON | 2018 | 5
697 | CASCADE SOLAR I |  | DG_CASCADE_CASCADE | WHARTON | SOLAR | SOUTH | 2018 | 5
698 | CASCADE SOLAR II |  | DG_CASCADE2_CASCADE2 | WHARTON | SOLAR | SOUTH | 2018 | 5
699 | CHISUM SOLAR |  | DG_CHISUM_CHISUM | LAMAR | SOLAR | NORTH | 2018 | 10
700 | COMMERCE_SOLAR |  | DG_ X443PV1_SWRI_PV1 | BEXAR | SOLAR | SOUTH | 2019 | 5
701 | EDDY SOLAR II |  | DG_EDDYII_EDDYII | MCLENNAN | SOLAR | NORTH | 2018 | 10
702 | FIFTH GENERATION SOLAR 1 |  | DG_FIFTHGS1_FGSOLAR1 | TRAVIS | SOLAR | SOUTH | 2016 | 1.6
703 | GRIFFIN SOLAR |  | DG_GRIFFIN_GRIFFIN | MCLEENNAN | SOLAR | NORTH | 2019 | 5
704 | HIGHWAY 56 |  | DG_HWY56_HWY56 | GRAYSON | SOLAR | NORTH | 2017 | 5.3
705 | HM SEALY SOLAR 1 |  | DG_SEALY_1UNIT | AUSTIN | SOLAR | SOUTH | 2015 | 1.6
706 | LAMPWICK SOLAR |  | DG_LAMPWICK_LAMPWICK | MENARD | SOLAR | SOUTH | 2019 | 7.5
707 | LEON |  | DG_LEON_LEON | HUNT | SOLAR | NORTH | 2017 | 10
708 | MARLIN |  | DG_MARLIN_MARLIN | FALLS | SOLAR | NORTH | 2017 | 5.3
709 | MARS SOLAR (DG) |  | DG_MARS_MARS | WEBB | SOLAR | SOUTH | 2019 | 10
710 | NORTH GAINESVILLE |  | DG_NGNSVL_NGAINESV | COOKE | SOLAR | NORTH | 2017 | 5.2
711 | OCI ALAMO 2 SOLAR-ST. HEDWIG |  | DG_STHWG_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 4.4
712 | OCI ALAMO 3-WALZEM SOLAR |  | DG_WALZM_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 5.5
713 | POWERFIN KINGSBERY |  | DG_PFK_PFKPV | TRAVIS | SOLAR | SOUTH | 2017 | 2.6
714 | RENEWABLE ENERGY ALTERNATIVES-CCS1 |  | DG_COSERVSS_CSS1 | DENTON | SOLAR | NORTH | 2015 | 2
715 | STERLING |  | DG_STRLING_STRLING | HUNT | SOLAR | NORTH | 2018 | 10
716 | SUNEDISON RABEL ROAD SOLAR |  | DG_VALL1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9
717 | SUNEDISON VALLEY ROAD SOLAR |  | DG_VALL2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9
718 | SUNEDISON CPS3 SOMERSET 1 SOLAR |  | DG_SOME1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5.6
719 | SUNEDISON SOMERSET 2 SOLAR |  | DG_SOME2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5
720 | WALNUT SPRINGS |  | DG_WLNTSPRG_1UNIT | BOSQUE | SOLAR | NORTH | 2016 | 10
721 | WEST MOORE II |  | DG_WMOOREII_WMOOREII | GRAYSON | SOLAR | NORTH | 2018 | 5
722 | WHITESBORO |  | DG_WBORO_WHTSBORO | GRAYSON | SOLAR | NORTH | 2017 | 5
723 | WHITESBORO II |  | DG_WBOROII_WHBOROII | GRAYSON | SOLAR | NORTH | 2017 | 5
724 | WHITEWRIGHT |  | DG_WHTRT_WHTRGHT | FANNIN | SOLAR | NORTH | 2017 | 10
725 | WHITNEY SOLAR |  | DG_WHITNEY_SOLAR1 | BOSQUE | SOLAR | NORTH | 2017 | 10
726 | YELLOW JACKET SOLAR |  | DG_YLWJACKET_YLWJACKET | BOSQUE | SOLAR | NORTH | 2018 | 5
727 | Operational Capacity Total (Solar) | [6 empty] | 2478.1
728 | Solar Peak Average Capacity Percentage |  | SOLAR_PEAK_PCT | % |  |  |  | 76
729
730 | Operational Resources (Storage)
731 | BLUE SUMMIT BATTERY |  | BLSUMMIT_BATTERY | WILBARGER | STORAGE | WEST | 2017 | 30
732 | CASTLE GAP BATTERY |  | CASL_GAP_BATTERY1 | UPTON | STORAGE | WEST | 2019 | 9.9
733 | INADALE ESS |  | INDL_ESS | NOLAN | STORAGE | WEST | 2018 | 9.9
734 | NOTREES BATTERY FACILITY |  | NWF_NBS | WINKLER | STORAGE | WEST | 2013 | 33.7
735 | OCI ALAMO 1 |  | OCI_ALM1_ASTRO1 | BEXAR | STORAGE | SOUTH | 2016 | 1
736 | PORT LAVACA BATTERY |  | PTLBES_BESS1 | CALHOUN | STORAGE | SOUTH | 2019 | 9.9
737 | PROSPECT STORAGE |  | WCOLLDG_BSS_U1 | BRAZORIA | STORAGE | HOUSTON | 2019 | 9.9
738 | PYRON ESS |  | PYR_ESS | SCURRY | STORAGE | WEST | 2018 | 9.9
739 | RABBIT HILL ENERGY STORAGE PROJECT |  | RHESS2_ESS_1 | WILLIAMSON | STORAGE | SOUTH | 2020 | 9.9
740 | WORSHAM BATTERY |  | WRSBES_BESS1 | REEVES | STORAGE | WEST | 2020 | 9.9
741 | YOUNICOS FACILITY |  | DG_YOUNICOS_YINC1_1 | TRAVIS | STORAGE | SOUTH | 2015 | 2
742 | KINGSBERY ENERGY STORAGE SYSTEM |  | DG_KB_ESS_KB_ESS | TRAVIS | STORAGE | SOUTH | 2017 | 1.5
743 | MU ENERGY STORAGE SYSTEM |  | DG_MU_ESS_MU_ESS | TRAVIS | STORAGE | SOUTH | 2018 | 1.5
744 | TOS BATTERY STORAGE |  | DG_TOSBATT_UNIT1 | MIDLAND | STORAGE | WEST | 2017 | 2
745 | Operational Capacity Total (Storage) | [6 empty] | 141
746 | Storage Peak Average Capacity Percentage |  | STORAGE_PEAK_PCT | % |  |  |  | 0
747
748 | Reliability Must-Run (RMR) Capacity |  | RMR_CAP_CONT |  | GAS |  |  | 0
749
750 | Capacity Pending Retirement |  | PENDRETIRE_CAP |  |  |  |  | 0
751
752 | Non-Synchronous Tie Resources
753 | EAST TIE |  | DC_E | FANNIN | OTHER | NORTH |  | 600
754 | NORTH TIE |  | DC_N | WILBARGER | OTHER | WEST |  | 220
755 | LAREDO VFT TIE |  | DC_L | WEBB | OTHER | SOUTH |  | 100
756 | SHARYLAND RAILROAD TIE |  | DC_R | HIDALGO | OTHER | SOUTH |  | 300
757 | Non-Synchronous Ties Total | [6 empty] | 1220
758 | Non-Synchronous Ties Peak Average Capacity Percentage |  | DCTIE_PEAK_PCT | % |  |  |  | 69.67
759
760 | Planned Thermal Resources with Executed SGIA, Air Permit, GHG Permit and Proof of Adequate Water Supplies
761 | FRIENDSWOOD II | 19INR0180 |  | BRAZORIA | GAS | COASTAL | 2021 | 0
762 | GIBBONS CREEK TEERP | 20INR0308 |  | GRIMES | COAL | NORTH | 2020 | 0
763 | HUDSON (BRAZORIA ENERGY G) | 16INR0076 |  | BRAZORIA | GAS | COASTAL | 2020 | 90
764 | MIRAGE | 17INR0022 |  | HARRIS | GAS | HOUSTON | 2020 | 0
765 | PES1 | 20INR0206 |  | HARRIS | GAS | HOUSTON | 2020 | 0
766 | Planned Capacity Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 90
767
768 | Planned Wind Resources with Executed SGIA
769 | CHALUPA WIND | 20INR0042 |  | CAMERON | WIND-C | COASTAL | 2020 | 0
770 | CHOCOLATE BAYOU W | 16INR0074 |  | BRAZORIA | WIND-C | COASTAL | 2021 | 0
771 | CRANEL WIND | 19INR0112 |  | REFUGIO | WIND-C | COASTAL | 2020 | 0
772 | EAST RAYMOND WIND | 18INR0059 |  | WILLACY | WIND-C | COASTAL | 2020 | 0
773 | EL ALGODON ALTO W | 15INR0034 |  | SAN PATRICIO | WIND-C | COASTAL | 2021 | 0
774 | ESPIRITU WIND | 17INR0031 |  | CAMERON | WIND-C | COASTAL | 2020 | 0
775 | LAS MAJADAS WIND | 17INR0035 |  | WILLACY | WIND-C | COASTAL | 2020 | 0
776 | MONTE ALTO I | 19INR0022 |  | WILLACY | WIND-C | COASTAL | 2021 | 0
777 | PALMAS ALTAS WIND | 17INR0037 |  | CAMERON | WIND-C | COASTAL | 2020 | 144.9
778 | PEYTON CREEK WIND | 18INR0018 |  | MATAGORDA | WIND-C | COASTAL | 2020 | 151.2
779 | SHAFFER (PATRIOT WIND/PETRONILLA) | 11INR0062 |  | NUECES | WIND-C | COASTAL | 2020 | 0
780 | WEST RAYMOND (EL TRUENO) WIND | 20INR0088 |  | WILLACY | WIND-C | COASTAL | 2020 | 0
781 | GOODNIGHT WIND | 14INR0033 |  | ARMSTRONG | WIND-P | PANHANDLE | 2021 | 0
782 | HART WIND | 16INR0033 |  | CASTRO | WIND-P | PANHANDLE | 2021 | 0
783 | PUMPKIN FARM WIND | 16INR0037c |  | FLOYD | WIND-P | PANHANDLE | 2020 | 0
784 | APOGEE WIND | 21INR0467 |  | HASKELL | WIND-O | WEST | 2021 | 0
785 | AVIATOR WIND | 19INR0156 |  | COKE | WIND-O | WEST | 2020 | 0
786 | BAIRD NORTH WIND | 20INR0083 |  | CALLAHAN | WIND-O | WEST | 2021 | 0
787 | BARROW RANCH (JUMBO HILL WIND) | 18INR0038 |  | ANDREWS | WIND-O | WEST | 2020 | 160
788 | BIG SAMPSON WIND | 16INR0104 |  | CROCKETT | WIND-O | WEST | 2021 | 0
789 | BLACKJACK CREEK WIND | 20INR0068 |  | BEE | WIND-O | SOUTH | 2021 | 0
790 | BLUE SUMMIT WIND 3 | 19INR0182 |  | WILBARGER | WIND-O | WEST | 2020 | 200
791 | CACTUS FLATS WIND | 16INR0086 |  | CONCHO | WIND-O | WEST | 2020 | 148.4
792 | CANYON WIND | 18INR0030 |  | SCURRY | WIND-O | WEST | 2021 | 0
793 | COYOTE WIND | 17INR0027b |  | SCURRY | WIND-O | WEST | 2020 | 0
794 | EDMONDSON RANCH WIND | 18INR0043 |  | GLASSCOCK | WIND-O | WEST | 2021 | 0
795 | GRIFFIN TRAIL WIND | 20INR0052 |  | KNOX | WIND-O | WEST | 2020 | 0
796 | HARALD (BEARKAT WIND B) | 15INR0064b |  | GLASSCOCK | WIND-O | WEST | 2020 | 0
797 | HIDALGO II WIND | 19INR0053 |  | HIDALGO | WIND-O | SOUTH | 2020 | 51
798 | HIGH LONESOME W | 19INR0038 |  | CROCKETT | WIND-O | WEST | 2020 | 449.5
799 | HIGH LONESOME WIND PHASE II | 20INR0262 |  | CROCKETT | WIND-O | WEST | 2020 | 50.6
800 | KAISER CREEK WIND | 18INR0042 |  | CALLAHAN | WIND-O | WEST | 2021 | 0
801 | KONTIKI 1 WIND (ERIK) | 19INR0099a |  | GLASSCOCK | WIND-O | WEST | 2021 | 0
802 | KONTIKI 2 WIND (ERNEST) | 19INR0099b |  | GLASSCOCK | WIND-O | WEST | 2022 | 0
803 | LAS LOMAS WIND | 16INR0111 |  | STARR | WIND-O | SOUTH | 2020 | 0
804 | LORAINE WINDPARK PHASE III | 18INR0068 |  | MITCHELL | WIND-O | WEST | 2021 | 0
805 | MARYNEAL WINDPOWER | 18INR0031 |  | NOLAN | WIND-O | WEST | 2021 | 0
806 | MAVERICK CREEK I | 20INR0045 |  | CONCHO | WIND-O | WEST | 2020 | 0
807 | MAVERICK CREEK II | 20INR0046 |  | CONCHO | WIND-O | WEST | 2020 | 0
808 | MESTENO WIND | 16INR0081 |  | STARR | WIND-O | SOUTH | 2020 | 201.6
809 | OVEJA WIND | 18INR0033 |  | IRION | WIND-O | WEST | 2020 | 300
810 | PRAIRIE HILL WIND | 19INR0100 |  | MCLENNAN | WIND-O | NORTH | 2020 | 0
811 | RELOJ DEL SOL WIND | 17INR0025 |  | ZAPATA | WIND-O | SOUTH | 2020 | 0
812 | ROADRUNNER CROSSING WIND 1 | 19INR0117 |  | EASTLAND | WIND-O | NORTH | 2021
813 | RTS 2 WIND (HEART OF TEXAS WIND) | 18INR0016 |  | MCCULLOCH | WIND-O | SOUTH | 2020 | 179.91
814 | SAGE DRAW WIND | 19INR0163 |  | LYNN | WIND-O | WEST | 2020 | 338
815 | TG EAST WIND | 19INR0052 |  | KNOX | WIND-O | WEST | 2021 | 0
816 | VERA WIND | 19INR0051 |  | KNOX | WIND-O | WEST | 2020 | 0
817 | VERA WIND V110 | 20INR0305 |  | KNOX | WIND-O | WEST | 2020 | 0
818 | WHITE MESA WIND | 19INR0128 |  | CROCKETT | WIND-O | WEST | 2021 | 0
819 | WHITEHORSE WIND | 19INR0080 |  | FISHER | WIND-O | WEST | 2020 | 418.9
820 | WILDWIND | 20INR0033 |  | COOKE | WIND-O | NORTH | 2020 | 0
821 | WKN AMADEUS WIND | 14INR0009 |  | FISHER | WIND-O | WEST | 2020 | 0
822 | Planned Capacity Total (Wind) | [6 empty] | 2794.01
823
824 | Planned Wind Capacity Sub-total (Coastal Counties) |  | WIND_PLANNED_C |  |  |  |  | 296.1
825 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PL_PEAK_PCT_C | % |  |  |  | 63
826
827 | Planned Wind Capacity Sub-total (Panhandle Counties) |  | WIND_PLANNED_P |  |  |  |  | 0
828 | Wind Peak Average Capacity Percentage (Panhandle) |  | WIND_PL_PEAK_PCT_P |  |  |  |  | 29
829
830 | Planned Wind Capacity Sub-total (Other counties) |  | WIND_PLANNED_O |  |  |  |  | 2497.91
831 | Wind Peak Average Capacity Percentage (Other) |  | WIND_PL_PEAK_PCT_O |  |  |  |  | 16
832
833 | Planned Solar Resources with Executed SGIA
834 | ANSON SOLAR | 19INR0081 |  | JONES | SOLAR | WEST | 2020 | 0
835 | ARAGORN SOLAR | 19INR0088 |  | CULBERSON | SOLAR | WEST | 2021 | 0
836 | AZURE SKY SOLAR | 21INR0477 |  | HASKELL | SOLAR | WEST | 2021 | 0
837 | BLUEBELL SOLAR II | 20INR0204 |  | STERLING | SOLAR | WEST | 2021 | 0
838 | BRAVEPOST SOLAR | 20INR0053 |  | TOM GREEN | SOLAR | WEST | 2021 | 0
839 | CONIGLIO SOLAR | 20INR0037 |  | FANNIN | SOLAR | NORTH | 2021 | 0
840 | CORAZON SOLAR | 15INR0044 |  | WEBB | SOLAR | SOUTH | 2021 | 0
841 | COTTONWOOD BAYOU | 19INR0134 |  | BRAZORIA | SOLAR | COASTAL | 2021 | 0
842 | CROWDED STAR SOLAR | 20INR0241 |  | JONES | SOLAR | WEST | 2021 | 0
843 | CROWDED STAR SOLAR II | 22INR0274 |  | JONES | SOLAR | WEST | 2022 | 0
844 | DANCIGER SOLAR | 20INR0098 |  | BRAZORIA | SOLAR | COASTAL | 2021 | 0
845 | DANISH FIELDS SOLAR I | 20INR0069 |  | WHARTON | SOLAR | SOUTH | 2021 | 0
846 | DANISH FIELDS SOLAR II | 21INR0016 |  | WHARTON | SOLAR | SOUTH | 2021 | 0
847 | DANISH FIELDS SOLAR III | 21INR0017 |  | WHARTON | SOLAR | SOUTH | 2021 | 0
848 | ELARA SOLAR | 21INR0276 |  | FRIO | SOLAR | SOUTH | 2021 | 0
849 | EMERALD GROVE SOLAR (PECOS SOLAR POWER I) | 15INR0059 |  | PECOS | SOLAR | WEST | 2021 | 0
850 | EUNICE SOLAR | 20INR0219 |  | ANDREWS | SOLAR | WEST | 2020 | 0
851 | FORT BEND SOLAR | 18INR0053 |  | FORT BEND | SOLAR | HOUSTON | 2021 | 0
852 | FOWLER RANCH | 18INR0039 |  | CRANE | SOLAR | WEST | 2020 | 0
853 | GALLOWAY 1 SOLAR | 19INR0121 |  | CONCHO | SOLAR | WEST | 2021 | 0
854 | GALLOWAY 2 SOLAR | 21INR0431 |  | CONCHO | SOLAR | WEST | 2021 | 0
855 | GREASEWOOD SOLAR | 19INR0034 |  | PECOS | SOLAR | WEST | 2020 | 0
856 | HOLSTEIN SOLAR | 19INR0009 |  | NOLAN | SOLAR | WEST | 2020 | 204.5
857 | HORIZON SOLAR | 21INR0261 |  | FRIO | SOLAR | SOUTH | 2021 | 0
858 | IMPACT SOLAR | 19INR0151 |  | LAMAR | SOLAR | NORTH | 2020 | 0
859 | IP TITAN | 20INR0032 |  | CULBERSON | SOLAR | WEST | 2021 | 0
860 | JUNO SOLAR PHASE I | 21INR0026 |  | BORDEN | SOLAR | WEST | 2021 | 0
861 | JUNO SOLAR PHASE II | 21INR0501 |  | BORDEN | SOLAR | WEST | 2021 | 0
862 | KELLAM SOLAR | 20INR0261 |  | VAN ZANDT | SOLAR | NORTH | 2020 | 0
863 | LAPETUS SOLAR | 19INR0185 |  | ANDREWS | SOLAR | WEST | 2020 | 100
864 | LILY SOLAR | 19INR0044 |  | KAUFMAN | SOLAR | NORTH | 2021 | 0
865 | LONG DRAW SOLAR | 18INR0055 |  | BORDEN | SOLAR | WEST | 2020 | 0
866 | LONG POINT SOLAR | 19INR0042 |  | BRAZORIA | SOLAR | COASTAL | 2021 | 0
867 | MISAE SOLAR | 18INR0045 |  | CHILDRESS | SOLAR | PANHANDLE | 2020 | 240.8
868 | MISAE SOLAR II | 20INR0091 |  | CHILDRESS | SOLAR | PANHANDLE | 2022 | 0
869 | MORROW LAKE SOLAR | 19INR0155 |  | FRIO | SOLAR | SOUTH | 2022 | 0
870 | MUSTANG CREEK SOLAR | 18INR0050 |  | JACKSON | SOLAR | SOUTH | 2021 | 0
871 | MYRTLE SOLAR | 19INR0041 |  | BRAZORIA | SOLAR | COASTAL | 2021 | 0
872 | NAZARETH SOLAR | 16INR0049 |  | CASTRO | SOLAR | PANHANDLE | 2022 | 0
873 | NORTON SOLAR | 19INR0035 |  | RUNNELS | SOLAR | WEST | 2021 | 0
874 | OBERON SOLAR | 19INR0083 |  | ECTOR | SOLAR | WEST | 2020 | 180
875 | OLD 300 SOLAR CENTER | 21INR0406 |  | FORT BEND | SOLAR | HOUSTON | 2021 | 0
876 | OXY SOLAR | 19INR0184 |  | ECTOR | SOLAR | WEST | 2020 | 16.2
877 | PFLUGERVILLE SOLAR | 15INR0090 |  | TRAVIS | SOLAR | SOUTH | 2020 | 0
878 | PHOENIX SOLAR | 19INR0091 |  | FANNIN | SOLAR | NORTH | 2021 | 0
879 | PROSPERO SOLAR | 19INR0092 |  | ANDREWS | SOLAR | WEST | 2020 | 300
880 | PROSPERO SOLAR II | 21INR0229 |  | ANDREWS | SOLAR | WEST | 2021 | 0
881 | QUEEN SOLAR PHASE II | 20INR0298 |  | UPTON | SOLAR | WEST | 2020 | 200
882 | RAMBLER SOLAR | 19INR0114 |  | TOM GREEN | SOLAR | WEST | 2020 | 200
883 | RAYOS DEL SOL | 19INR0045 |  | CAMERON | SOLAR | COASTAL | 2021 | 0
884 | RE MAPLEWOOD 2A SOLAR | 17INR0020a |  | PECOS | SOLAR | WEST | 2021 | 0
885 | RE MAPLEWOOD 2B SOLAR | 17INR0020b |  | PECOS | SOLAR | WEST | 2020 | 0
886 | RE MAPLEWOOD 2C SOLAR | 17INR0020c |  | PECOS | SOLAR | WEST | 2021 | 0
887 | RIPPEY SOLAR | 20INR0031 |  | COOKE | SOLAR | NORTH | 2020 | 0
888 | RODEO SOLAR | 19INR0103 |  | ANDREWS | SOLAR | WEST | 2021 | 0
889 | SHAKES SOLAR | 19INR0073 |  | ZAVALA | SOLAR | SOUTH | 2021 | 0
890 | SODA LAKE SOLAR 1 | 18INR0040 |  | CRANE | SOLAR | WEST | 2021 | 0
891 | SODA LAKE SOLAR 2 | 20INR0143 |  | CRANE | SOLAR | WEST | 2021 | 0
892 | STRATEGIC ENERGY | 20INR0081 |  | ELLIS | SOLAR | NORTH | 2021 | 0
893 | TAYGETE II SOLAR | 21INR0233 |  | PECOS | SOLAR | WEST | 2021 | 0
894 | TAYGETE SOLAR | 20INR0054 |  | PECOS | SOLAR | WEST | 2021 | 0
895 | TEXAS SOLAR NOVA | 19INR0001 |  | KENT | SOLAR | WEST | 2022 | 0
896 | TIMBERWOLF POI A | 20INR0226 |  | UPTON | SOLAR | WEST | 2021 | 0
897 | UPTON SOLAR | 16INR0114 |  | UPTON | SOLAR | WEST | 2020 | 0
898 | WAGYU SOLAR | 18INR0062 |  | BRAZORIA | SOLAR | COASTAL | 2020 | 0
899 | WESTORIA SOLAR | 20INR0101 |  | BRAZORIA | SOLAR | COASTAL | 2021 | 0
900 | Planned Capacity Total (Solar) | [6 empty] | 1441.5
901 | Solar Peak Average Capacity Percentage |  | SOLAR_PL_PEAK_PCT | % |  |  |  | 76
902
903 | Planned Storage Resources with Executed SGIA
904 | AZURE SKY BESS | 21INR0476 |  | HASKELL | STORAGE | WEST | 2021 | 0
905 | BAT CAVE | 21INR0365 |  | MASON | STORAGE | SOUTH | 2021 | 0
906 | CHISHOLM GRID | 20INR0089 |  | TARRANT | STORAGE | NORTH | 2021 | 0
907 | EUNICE STORAGE | 20INR0220 |  | ANDREWS | STORAGE | WEST | 2020 | 0
908 | MADERO GRID | 21INR0244 |  | HIDALGO | STORAGE | SOUTH | 2021 | 0
909 | NORTH FORK | 20INR0276 |  | WILLIAMSON | STORAGE | SOUTH | 2021 | 0
910 | SILICON HILL STORAGE | 20INR0291 |  | TRAVIS | STORAGE | SOUTH | 2021 | 0
911 | BRP ALVIN |  | BRPALVIN_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2020 | 0
912 | BRP ANGELTON |  | BRPANGLE_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2020 | 0
913 | BRP BRAZORIA |  | BRP_BRAZ_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2020 | 0
914 | BRP DICKINSON |  | BRP_DIKN_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2020 | 0
915 | BRP HEIGHTS |  | BRHEIGHT_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2020 | 0
916 | BRP MAGNOLIA |  | BRPMAGNO_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2020 | 0
917 | BRP ODESSA SW |  | BRPODESA_UNIT1 | ECTOR | STORAGE | WEST | 2020 | 0
918 | COMMERCE ST ESS |  | X443ESS1_SWRI | BEXAR | STORAGE | SOUTH | 2019 | 10
919 | FLAT TOP BATTERY |  | FLTBES_BESS1 | REEVES | STORAGE | WEST | 2019 | 9.9
920 | JOHNSON CITY BESS |  | JC_BAT_UNIT_1 | BLANCO | STORAGE | SOUTH | 2020 | 0
921 | Planned Capacity Total (Storage) | [6 empty] | 19.9
922 | Storage Peak Average Capacity Percentage |  | STORAGE_PL_PEAK_PCT | % |  |  |  | 0
923
924 | Inactive Planned Resources
925 | HALYARD WHARTON ENERGY CENTER | 16INR0044 |  | WHARTON | GAS | SOUTH | 2021 | 0
926 | MARIAH DEL ESTE | 13INR0010a |  | PARMER | WIND-P | PANHANDLE | 2020 | 0
927 | NORTHDRAW WIND | 13INR0025 |  | RANDALL | WIND-P | PANHANDLE | 2020 | 0
928 | PANHANDLE WIND 3 | 14INR0030c |  | CARSON | WIND-P | PANHANDLE | 2022 | 0
929 | WILDROSE WIND (SWISHER WIND) | 13INR0038 |  | SWISHER | WIND-P | PANHANDLE | 2021 | 0
930 | LOMA PINTA WIND | 16INR0112 |  | LA SALLE | WIND-O | SOUTH | 2021 | 0
931 | AGATE SOLAR | 20INR0023 |  | ELLIS | SOLAR | NORTH | 2020 | 0
932 | GARNET SOLAR | 20INR0021 |  | WILLIAMSON | SOLAR | SOUTH | 2020 | 0
933 | HOVEY (BARILLA SOLAR 1B) | 12INR0059b |  | PECOS | SOLAR | WEST | 2020 | 7.4
934 | SPINEL SOLAR | 20INR0025 |  | MEDINA | SOLAR | SOUTH | 2020 | 0
935 | SUN VALLEY | 19INR0169 |  | HILL | SOLAR | NORTH | 2021 | 0
936 | Inactive Planned Capacity Total | [6 empty] | 7.4
937
938 | Seasonal Mothballed Resources
939 | GREGORY POWER PARTNERS GT1 (AS OF 10/17/2019, AVAILABLE 5/1 THROUGH 9/30) |  | LGE_LGE_GT1 | SAN PATRICIO | GAS | COASTAL | 2000 | 145
940 | GREGORY POWER PARTNERS GT2 (AS OF 10/17/2019, AVAILABLE 5/1 THROUGH 9/30) |  | LGE_LGE_GT2 | SAN PATRICIO | GAS | COASTAL | 2000 | 145
941 | GREGORY POWER PARTNERS STG (AS OF 10/17/2019,AVAILABLE 5/1 THROUGH 9/30) |  | LGE_LGE_STG | SAN PATRICIO | GAS | COASTAL | 2000 | 75
942 | SPENCER STG U4 (AS OF 10/3/2018, AVAILABLE 5/20 THROUGH 10/10) |  | SPNCER_SPNCE_4 | DENTON | GAS | NORTH | 1966 | 57
943 | SPENCER STG U5 (AS OF 10/3/2018, AVAILABLE 5/20 THROUGH 10/10) |  | SPNCER_SPNCE_5 | DENTON | GAS | NORTH | 1973 | 61
944 | Total Seasonal Mothballed Capacity | [6 empty] | 483
945
946 | Mothballed Resources
947 | J T DEELY U1 (AS OF 12/31/2018) |  | CALAVERS_JTD1_M | BEXAR | COAL | SOUTH | 1977 | 420
948 | J T DEELY U2 (AS OF 12/31/2018) |  | CALAVERS_JTD2_M | BEXAR | COAL | SOUTH | 1978 | 420
949 | Total Mothballed Capacity | [6 empty] | 840
950
951 | Retiring Resources Unavailable to ERCOT (since last CDR/SARA)
952 | EAGLE PASS TIE (AS OF 4/9/2020) |  | DC_S | MAVERICK | OTHER | SOUTH |  | 30
953 | CITY OF GONZALES HYDRO (AS OF 3/1/2020) |  | DG_GONZ_HYDRO_GONZ_HYDRO | GONZALES | HYDRO | SOUTH | 1986 | 1.5
954 | Total Retiring Capacity | [6 empty] | 31.5
Notes:
Capacity changes due to planned repower/upgrade projects are reflected in the operational units' ratings upon (1) receipt and ERCOT approval of a new Resource Asset Registration Form (RARF). Projects associated with interconnection change requests that change the MW capacity are indicated with a code in the “Generation Interconnection Project Code” column of operational units.
Although seasonal capacity ratings for battery energy storage systems are reported above, the ratings are not included in the operational/planned capacity formulae. These resources are assumed to provide regulation reserves rather than sustained capacity available to meet system peak loads.
The projects listed in the 'Planned Storage Resources with Executed SGIA' section with UNIT CODE entries are Distributed Generation Resources (DGRs). Since they are 10 MW or less, they are not going through the GINR application process.
The retiring hydro unit (CITY OF GONZALES HYDRO) has been removed from the settlement system and is now treated as a load reduction by LCRA
Note on I396: Constitutes the Schumansville DG hydro plant (3.6 MW) and 2.4 MW of the 4.8 MW Lakewood Tap DG hydro plant (DG_LKWT_2UNITS)

## Background
Release Date: May 13, 2020
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Background
The Seasonal Assessment of Resource Adequacy (SARA) report is a deterministic approach to considering the impact of potential variables that may affect the sufficiency of installed resources to meet the peak electrical demand on the ERCOT System during a particular season.
The standard approach to assessing resource adequacy for one or more years into the future is to account for projected load and resources on a normalized basis and to require sufficient reserves (resources in excess of peak demand, on this normalized basis) to cover the uncertainty in peak demand and resource availability to meet a probabilistic reliability standard.
For seasonal assessments that look ahead less than a year, specific information may be available (such as seasonal climate forecasts or anticipated common-mode events such as drought) which can be used to consider the range of resource adequacy in a more deterministic manner.
The SARA report focuses on the availability of sufficient operating reserves to avoid emergency actions such as deployment of voluntary load reduction resources. It uses an operating reserve threshold of 2,300 MW to indicate the risk that an Energy Emergency Alert Level 1 (EEA1) may be triggered during the time of the forecasted seasonal peak load. This threshold level is intended to be roughly analogous to the 2,300 MW Physical Responsive Capability (PRC) threshold for EEA1. However, PRC is a real-time capability measure for Resources that can quickly respond to system disturbances. In contrast, the SARA operating reserve reflects additional capability assumed to be available before energy emergency procedures are initiated, such as from Resources qualified to provide non-spinning reserves. Additionally, the amount of operating reserves available may increase relative to what is included in the SARA report due to the market responding to wholesale market price increases and anticipated capacity scarcity conditions. Given these considerations, ERCOT believes that the 2,300 MW reserve capacity threshold is a reasonable indicator for the risk of Energy Emergency Alerts given the uncertainties in predicting system conditions months in advance.
The SARA report is intended to illustrate the range of resource adequacy outcomes that might occur. It serves as a situational awareness tool for ERCOT operational planning purposes, and helps fulfill the "extreme weather" resource adequacy assessment requirement per Public Utility Commission of Texas rule 25.362(i)(2)(H). In addition to a base scenario, several other scenarios are developed by varying the value of load forecast and resource availability parameters. The variation in these parameters is based on historic ranges of the parameter values or known changes expected in the near-term. The SARA report is not intended to indicate the likelihood of any of these scenario outcomes.