## Slide 1
Temporary Moves of DGRs/DESRs
DGR Workshop VII
Sai Moorty
May 19, 2020

## Slide 2: Terminology
SODG – Settlement Only Distribution Generation
  Do not actively participate (no bids/offers) in the ERCOT wholesale markets
  Self-deployed (can chase prices)
  Can reduce demand charges (4CP) if behind a Load meter on 4CP tariff
  Any technology (including storage) that can inject into the Point of Common Coupling (PCC) on the DSP system
DGR – Distribution Generation Resource
DESR-Distribution Energy Storage Resource (NPRR 995 in flight)
  “R”esource that actively participates (submits bids/offers, telemetry, COP,..etc.) in ERCOT wholesale markets
  Will have Resource Node Settlement Point on the modeled transmission grid
  Any technology (including storage) that can inject into the Point of Common Coupling (PCC) on the DSP system
Examples of SODG, DGR and DESR technologies:
  Reciprocating Engines (Diesel or Natural Gas)
  Community or commercial Solar
  Li-Ion Battery

## Slide 3: DGR/DESR Representation in ERCOT Systems
ERCOT Model
CIM Load A
CIM Load B
DSP grid
EB-A
EB-B
DGR/DESR
EB-A, EB-B: Electrical Buses
RN-A: Resource Node Settlement Point
DGR/DESR participates in DAM,RUC, and Real-Time Markets (SCED/RTC) just as any transmission connected “R”esource
Shift Factor at RN-A (=EB-A) used to dispatch DGR/DESR
DGR/DESR
RN-A
EPS
meter

## Slide 4: DSP Topology Changes That Move DGR/DESR
NPRRs 1016 and 1017 provide the means to address long term / permanent DSP topology changes that impact DGR/DESR Resource Node Settlement Point location
  NPRR 1016: If a DSP topology change that affects the “mapping” of a DGR/DESR to an ERCOT CIM Load is expected to last for more than 60 days, the Resource Entity will submit NOMCR to ERCOT and update with mapping to the new CIM Load
  NPRR 1017: Allows for up to two moves of a Resource Node Settlement Point per year
This presentation describes how ERCOT market systems will process temporary move scenarios
  Temporary moves or switching will probably be infrequent

## Slide 5: Scenario 1: Temporary Move of DGR/DESR with Resource Node Outaged/De-Energized
ERCOT Model
CIM Load A
CIM Load B
DSP grid
EB-A
EB-B
DGR/DESR
EB-A, EB-B: Electrical Buses
RN-A: Resource Node Settlement Point
TSP takes outage that outages EB-A and RN-A
DSP reconfigures DGR/DESR feeder to connect to CIM Load B
ERCOT Systems not aware of DSP topology change
DAM :
  DGR/DESR cannot participate in energy market as Resource Node outaged/de-energized
  DGR/DESR can participate in AS market, same as Load Resource under similar circumstances
RUC: DGR/DESR is considered only for AS if COP status is On-line or Off-Line available
Real-Time: If DGR/DESR telemeters a status of On-Line:
  SCED/RTC will dispatch energy using Shift Factor of zero (or shift factor of appropriate electrical bus if known in advance) and, under RTC, will allow participation in AS markets
  Resource Node LMP will use the same shift factor as used for DGR/DESR dispatch to align price/dispatch for settlements
DGR/DESR
DGR/DESR
RN-A
EPS
meter

## Slide 6: Scenario 2: Temporary Move of DGR/DESR and Resource Node Remains Energized
ERCOT Model
CIM Load A
CIM Load B
DSP grid
EB-A
EB-B
DGR/DESR
EB-A, EB-B: Electrical Buses
RN-A: Resource Node Settlement Point
DSP reconfigures DGR/DESR feeder to connect to CIM Load B
ERCOT Systems not aware of DSP topology change
DAM, RUC, and Real-Time:
  ERCOT systems will consider the DGR/DESR as connected to CIM Load A and dispatch for energy and Ancillary Service
DGR/DESR
DGR/DESR
RN-A
EPS
meter

## Slide 7: Discussion
Congestion Management when DGR/DESR has been moved temporarily:
  With a temporary move, there can be scenarios where SCED dispatch to relieve overloads is inaccurate due to assumption on shift factor of DGR/DESR
    Acceptable error for low penetration of DGR/DESR (at a constraint level)
    ERCOT Operator situational awareness is impacted as ERCOT systems are not aware of the move. This impact is felt when SCED cannot resolve a congestion and the reason is due to an incorrect shift factor; ERCOT staff/systems may not be able to diagnose the root cause as ERCOT has no information on the changed location of the DGR/DESR (Also an issue for high penetration levels of SODG/SOESS)
  Situational awareness and analytics can be improved if information on the changed location of DGR/DESR (Electrical Bus/CIM Load) is provided to ERCOT. This is also applicable to SODG/SOESS.
Current process to determine the energization status of distribution-connected Load Resources (LR) offering to sell Ancillary Services in the DAM will need to be revisited
  Extending this process to cover DGR/DESR participation in the DAM AS market will be cumbersome
  Proposal: For DAM, default energization status for consideration of AS Offers from LR and DGR/DESR is “Energized” if the QSE has submitted Resource-specific AS offers.
    Responsibility of QSE to ensure that their distribution connected Resources (LR,DGR,DESR) are energized for the Operating Day/Hours before submitting AS offers in the DAM