## PGRR Comments
Author | Section | Section Name | TDSP Comments | ERCOT Comments
Oncor | 5.1(1)(e) | Introduction | change and to "or" | agree
Oncor | 5.2.1 | Applicability | Does process apply to SODG | Yes - discussed at the DGR Workshop III
Oncor | 5.2.1(a) | Applicability | Does "any generator" include unregistered DG > 1 MW | Need to discuss
Oncor | 5.2.1(a) | Applicability | Oncor would like export not nameplate | ERCOT will be following existing protocols for 1 MW nameplate
Oncor/CNP | 5.2.1(1)(b) | Applicability | Why no size threshold for SOG? | SOG <1 MW have the option to register with ERCOT
Oncor | 5.2.1(1)(c) | Applicability | If DGR increases by < 10 MW, but jumps from small to a large gen, no review? | Will be adding clarification in the language.
Oncor | 5.2.1(3) | Applicability | Oncor would like export not nameplate | ERCOT will be following existing protocols for 1 MW nameplate
Oncor | 5.2.1(4) | Applicability | Oncor would like section to apply to non-affilliates | ERCOT does not have justification for such a requirement. This was already discussed at DGR Workshop IV
Oncor | original 5.1.2 | Responsibilities | Where did section go | Deleted as redundant
Oncor | 5.2.2(2) | Initiation of the Generator Interconnection or Modification Process | Related to 5.2.1 comment above. Does is relate to all >1MW | Need to discuss
Oncor | 5.2.2(10) | Initiation of the Generator Interconnection or Modification Process | Suggest using Phases instead of stages | agree
Oncor | 5.2.4 | Duty to Update Project Information and Respond to ERCOT and TDSP Requests for Information | suggest defining "Main Power Transformer" | addressed by NPRR973
Oncor | 5.2.4(3) | Duty to Update Project Information and Respond to ERCOT and TDSP Requests for Information | interconnecting or lead TSP | May be able to change reference to say 'lead TSP'
Oncor | 5.2.4(5), 5.2.5(5) | Duty to Update Project Information and Respond to ERCOT and TDSP Requests for Information | Suggest change TSP notified by RIOO to TDSP | Need to resolve/clarify with RIOO team
Oncor | 5.2.5(3) | Inactive Status | What does "discontinue any process" mean? | Will add clarifying language - 'interconnection process'
Oncor | 5.2.7 | Voluntary Project Cancellation | The RIOO will notify ERCOT and TDSPs… Will DSPs be notified? | Need to resolve/clarify with RIOO team
Oncor | 5.2.8.2 | Other Arrangements for Transmission Service | IS paragraph still needed? | Need to discuss
Oncor | 5.2.8.3 | Interconnection Agreement for Distribution-Connected Generators | Change to Resource so it wont apply to SODG? | Disagree--needs to apply to all
Oncor | 5.2.8.3(1) | Interconnection Agreement for Distribution-Connected Generators | Oncor feels IA is confidential.--Will provide notification of completion. | Language has been adjusted to allow an attestation of an IA for small gen
Oncor | 5.3.1(1) | Security Screening Study | Clarify that this applies to Large generators | Doesn’t seem necessary
Oncor | 5.3.1(2) | Security Screening Study | Include all GR, ESR and SOG | agree. Will change to 'generator' as opposed to a list
Oncor | 5.3.1(7) | Security Screening Study | what does "and does not, as proposed, violate the DSP’s tariff or any other applicable authority administered by the DSP." mean? | Revisions have been made
Oncor | 5.3.2(1) | Full Interconnection Study | change to "stability" from dynamic | agree
Oncor | 5.3.2.2(1) | Full Interconnection Study | Language to be revised--Does ERCOT select lead TSP? | Need to discuss. May be room for clarification.
Oncor | 5.3.2.2(2) | Full Interconnection Study | Language needs work, and may not be needed. | Need to discuss. May be room for clarification.
Oncor | 5.3.2.3(4) | Full Interconnection Study | add "and any other distribution connected resource" | Need to discuss. Doesn't seem necessary, but if so, would also add transmission connected resource.
Oncor | 5.3.2.4.3(6)(c) | Dynamic Stability Analysis | add ESR | may already be added by BESTF
Oncor | 5.4.1(1) | Small Generator Review Meetings | Questions about the process | Edits will be made to clarify
CNP | 5.1(1)(a) | Introduction | Does removing "directly" now mean that TDSPs can sponsor projects to relieve thermal overload concerns? | No, the meaning has not changed. All generators must go through an interconnection process
CNP | 5.2.1(1)(c) | Applicability | If a DGR increases size by 9 MW, it won't need to go through this process. | If a generator added capacity to hit 10 MW or more, it would then go through the large generator process.
CNP | 5.2.1(1)(c')(i) | Applicability | change "by" to "to" | Unnecessary, that would trigger every change for a large generator
CNP | 5.2.1(4) | Applicability | Is the capacity based on nameplate or based on DSP imposed limitation? | Nameplate for simplicity
CNP | 5.2.1(4) | Applicability | How will ERCOT keep track of the aggregates? Is there a threshold for non-affiliate aggregation? | New RIOO type tool. No, ERCOT would need to receive much more detailed reports to be able to track non-affiliated small generation at a substation
CNP | 5.2.2(2) | Initiation of the Generator Interconnection or Modification Process | How is DSP imposed limitations captured? Is RE required to submit these in RIOO? | Captured in RARF HRL if possible.
CNP | 5.2.5(1) | Inactive Status | Why two years? They only have 180 days to sign SGIA and they should have another 6 months to provide notice to proceed rather than a total of 2 years. | The 180 days for the SGIA is a requirement, but the other items needed to meet 6.9(1) are not. The two year period is used for the validity of studies.
CNP | 5.2.8.3 | Interconnection Agreement for Distribution-Connected Generators | Edits for Distribution-connected IA wording | Agree
CNP | 5.3.2.1(1) | Proof of Site Control | Can multiple resources show the leasehold interest in the same piece of land? Another scenario is, if the resource has a leasehold interest for 100 acres and another resource shows a leasehold for another 100 acres which is close by but has some area which encompasses the first resource area. How does ERCOT tackle this situation? | ERCOT does not compare site control documents from one INR to another. It would be possible with more staff and more accurate data.
CNP | 5.3.2.2(2)(b) | Full Interconnection Study Scoping Process | IE agreement to upgrades should be applied for small generators (distribution) as well | Agree
CNP | 5.3.2.2(7)(a) | Full Interconnection Study Scoping Process | Why do we require IE approval to proceed with different phases of the study when a study scope is finalized and signed by the IE? The TSP should be able to perform any study as deemed necessary to interconnect the generator reliably to the system. | The division into study phases would be covered in the scope document. The IE giving approval for each phase would also be in the scope document. The TDSP is able to perform needed studies.
CNP | 5.3.2.4.4(1) | Facility Study | addition of "unless transmission facilities are required to be constructed" | Agree
CNP | 5.4.2(b)and(c') | Submission of Interconnection Agreement and TSP and/or DSP Studies and Technical Requirements | Add "Upon ERCOT's request" | ERCOT should not have to request it
CNP | 5.4.3 | Reviews and Approval to Submit Model Information | What type of information is needed? | The TDSP would provide what is detailed in the Conditions document. The IE would then provide what is needed to ERCOT.
CNP | 5.7.5(3) | Interconnection Process Timetables | Why was the table removed? | We can put the table in the Resource Interconnection Handbook
CNP | 6.9(2) | Addition of Proposed Generation to the Planning Models | 60 days seems excessive | The requirement has not changed due to DGR
CNP | 6.9(3) | Addition of Proposed Generation to the Planning Models | How will this be modeled? | There is no detailed model but could be a model that shows the generator under the distribution transformer
LCRA | 5.1(1)(a) | Introduction | re-inserting directly | The meaning has not changed. All generators must go through an interconnection process
LCRA | 5.2.2(1) | Initiation of the Generator Interconnection or Modification Process | Replace Generation Interconnection or Modification Request (GINR) with Generation Interconnection or Modification Process. | We are still using the GINR term
LCRA | 5.2.2(1) | Initiation of the Generator Interconnection or Modification Process | Is the plan to keep GINR as the acronym even though the name has changed? | We are still using the GINR term
LCRA | 5.2.2(11) | Initiation of the Generator Interconnection or Modification Process | Change 'physical transmission interconntion' to 'POI' | Due to terminology concerns around distribution-connected generators, we will change to 'physical interconnection'
LCRA | 5.2.5 (5) | Inactive Status | Remove paragraph 5 because of duplication | The next draft will have several paragraphs within 5.2.5 reworked for clarity
LCRA | 5.2.8.2 | Other Arrangements for Transmission Service | Is there a history around why the section 'Other Arrangements for Transmission Service' is included? | Need to discuss. We may have edits to this section to better reflect the current process.
LCRA | 5.2.8.3 | Interconnection Agreement for Distribution-Connected Generators | Insert 'This interconnection agreement shall also be provided to the appropriate TSP | The next draft will have some edits to capture that idea
LCRA | 5.3.2.1(3) | Proof of Site Control | Change 'execution of an SGIA' to 'energization date' | agree
LCRA | 5.3.2.2(2)(a) | Full Interconnection Study Scoping Process | Delete 'and/or transmission' | agree, but should discuss with other TDSPs
LCRA | 5.3.2.4.4 | Facility Study | Delete 'detailed' | agree
LCRA | 5.4.2 | Submission of Interconnection Agreement and TSP and/or DSP Studies and Technical Requirements | Delete 'with the TDSP, if' | Disagree. However, the next draft will have an edit to also include an attestation option