## Slide 1: Collector System Templates
Introduction to
Zach Reich / Jonathan Rose
5/22/2020

## Slide 2: Background
ERCOT groups have developed tools to build System Protection and other planning models based on the Collector System tabular data. This is used in conjunction with other RARF data.
It was discovered that there were a lot of inconsistencies and data quality issues with the Collector System Data in the RARF.
As a result, the Collector System Template was developed to ensure the accuracy of the Collection System.
NOTE: This template will be required to be embedded in the RARF to meet P.G. 6.9 and the QSA requirements starting on August 1, 2020!

## Slide 3: Overview
RARF will be replaced by RIOO-RS system.
Currently there is no web interface for collector system data that will be part of MVP of RIOO-RS.
  Collector system data will still be submitted via an Excel upload
  Good News! Excel Template now has built in data checking
  Format similar to current RARF Dynamic Data Template
Before full RIOO-RS implementation this template will still need to be embedded in the RARF.

## Slide 4: Recommended Sequence For New RARFs
Start filling out the Collector System data in the template first.
Validate the data within the template.
Copy validated data from the template to the two RARF Collector System tabs.
Embed template in the Collector System – RENEWABLE tab in the RARF.

## Slide 5
How to Use the Tool
Examples:

## Slide 6
Examples Continued:

## Slide 7: Home Sheet
Enter basic info about resource
Buttons to check data

## Slide 8: Cable and Segments Sheets
Identical to RARF forms

## Slide 9: Validations
Several Validations are performed:
  Island Checks: Are any segments missing?
  Data consistency:
    Are cable types correctly defined?
    Are turbines/inverters numbered correctly?
  “Loop Backs”: Is the layout radial in nature or are there parallel paths caused by mistakes in the connectivity?
A
B
C
D
E
F G
Island 1
Island 2
Missing!
Island Check: Segment E‐F is missing, incorrectly causing a second island.

## Slide 10: Island Checking
This site with two independent 34.5 kV SUB buses will appear to have two islands.
– Because transformers are not entered into the Segments sheet, there will be two groups of collector segments that are not connected to each other. “Island 1” and “Island 2”.
However, if the validation step reports three islands, then you know a mistake was made
– A segment is probably missing
POI
SUB1
B
C
D
A 1
3
2
1
E
4
F
H
I
3
G
2
1
3
Resource1
Resource2
SUB2
Island 1
Island 2

## Slide 11: Turbine Segment Numbering
The segments leaving the SUB node should indicate the total number of turbines / inverters in the farm. Here, there are 4.
Segments are numbered to indicate the number of turbines/inverters they support.
POI
Origin Bus
SUB
B
C
A 1
3
2
D
1
E
4
Cable | FROM | TO | CKT | # Turb
XLR | SUB | A | 101 | 4
XLR | A | B | 102 | 1
XLR | A | C | 103 | 3
XLR | C | D | 104 | 2
XLR | D | E | 105 | 1

## Slide 12: Turbine Segment Numbering
Most wind farms have only one turbine per node.
– Can’t put two turbines in the same spot!
Below, the Validation step has found a node with 7 turbines.
This could be caused by a segment that is mis-numbered missing.
– The error is probably near Node F07.

## Slide 13: Sites with Mixed Turbines
New form can accommodate mixed sites.
POI
SUB1
B
C
D
A 1
3
2
1
E
4
F
H
I
3
G
2
1
3
Resource1
Resource2
SUB2
Island 1
Island 2
Resource3
Resource | Cable | FROM | TO | CKT | # Turb
Resource1 | XLR | SUB1 | A | 101 | 4
Resource1 | XLR | A | B | 102 | 1
Resource1 | XLR | A | C | 103 | 3
Resource1 | XLR | C | D | 104 | 2
Resource1 | XLR | D | E | 105 | 1
(Mixed) | XLR | SUB2 | F | 201 | 3
(Mixed) | XLR | F | G | 202 | 3
(Mixed) | XLR | G | H | 203 | 2
(Mixed) | XLR | H | I | 204 | 1
See Help sheet for details.

## Slide 14: Validation
Here’s what you want to see before submitting to ERCOT:
Some warning messages may be okay for your particular system
  For example, some solar farms have more than one inverter per Node.
  There may be rare situations were a collector system actually does loop- back upon itself and is not a truly radial system.
  Exercise judgment.
Also providing ERCOT a good RAW file that solves out-of-the-box will help us greatly.

## Slide 15: Questions??