## Slide 1
Final Summer 2020 Seasonal Assessment of Resource Adequacy (SARA) and May 2020 Capacity, Demand and Reserves Report (CDR)
Supply Analysis Working Group
Pete Warnken
Resource Adequacy
May 28, 2020

## Slide 2: Scenario Results: Final Summer SARA
Summer 2020 | Forecasted Season Peak Load1 | Forecasted Season Peak Load / Extreme Generation Outages2 | Forecasted Season Peak Load / Low Wind Output3 | Extreme Peak Load4 / Typical Generation Outages
Total Resources | 82,199 MW |  |  | 
Peak Load | 75,200 |  |  | 78,416
Unavailable Capacity | 4,069 | 7,001 | 9,088 | 7,285
Capacity Available for Operating Reserves | 2,930 | (2) | (2,089) | (286)
1 Based on normal weather from 2004 - 2018
2 Based on typical generation outages (average historical planned and
forced outages during peak hours for June-September weekdays,
starting in 2017), plus additional forced outages at 95th percentile
3 Based on 5th percentile of wind output during 100 highest Net Load
hours for the 2015-2019 summer seasons (1,622 MW)
4 Based on 2011 summer weather

## Slide 3: CDR Changes
NPRR980:
  Removal of Inactive GINR projects from the reserve margin calculations
  Explicit exclusion of extended outage unit capacity from the reserve margin calculations, and identification of outaged units
Separate section and capacity contribution calculations for hydro Settlement-Only Distributed Generators (SODGs)
New Supplemental Information:
  Potential long-term impacts of COVID-19 on customer demand and Reserve Margins (2021-2024)
  List of fossil-fuel SODGs, totaling 485.6 MW (not included in the CDR calculations)
  Rooftop Solar Penetration Scenarios: three potential growth scenarios for the ERCOT region provided (not included in the CDR calculations)

## Slide 4: CDR Summer Results
Megawatts Expected for Peak Demand Hour | 2021 | 2022 | 2023 | 2024 | 2025
Peak Load Forecast | 78,299 | 80,108 | 81,593 | 82,982 | 84,193
Demand Response Resources | 2,201 | 2,201 | 2,201 | 2,201 | 2,201
Firm Peak Load Forecast | 76,098 | 77,907 | 79,393 | 80,781 | 81,993
Existing Resources | 80,002 | 79,797 | 79,792 | 79,747 | 79,707
Planned Resources | 9,248 | 13,422 | 13,856 | 13,856 | 13,856
Total Resources | 89,250 | 93,219 | 93,648 | 93,603 | 93,563
Reserve Margin (Resources – Firm Peak Load)/Firm Peak Load | 17.3% | 19.7% | 18.0% | 15.9% | 14.1%
Megawatts Expected for Peak Demand Hour | 2021 | 2022 | 2023 | 2024 | 2025
Reserve Margin | 18.2% | 17.3% | 15.2% | 12.9% | 11.3%
May 2020 CDR
December 2019 CDR
Latest in-service summer for CDR-Eligible Planned Resources