## Slide 1
Corpus Christi North Shore Regional Planning Group Projects
Shun Hsien (Fred) Huang
Manager, Regional Planning
Technical Advisory Committee Meeting
ERCOT Public
May 27, 2020

## Slide 2: Overview
American Electric Power (AEP) submitted the Corpus Christi North Shore project for Regional Planning Group review
This is a Tier 1 project that was estimated to cost $291 Million
Addresses reliability needs resulting from new confirmed industrial load of 1,085 MW which is anticipated to come online before 2024

## Slide 3: Tier 1 Project Requirement
Pursuant to Protocol Section 3.11.4.7 (Tier 1)
  Projects with an estimated capital cost of $100 Million or greater are Tier 1 projects
  Tier 1 projects require ERCOT Board endorsement
Pursuant to Protocol Section 3.11.4.9
  ERCOT shall present the Tier 1 project to the Technical Advisory Committee (TAC) for review and comment
  Comments from TAC shall be included in the presentation to the ERCOT Board

## Slide 4: Project Need
ERCOT’s independent review indicated thermal and voltage criteria violations
System improvement is needed to meet reliability criteria
 | Thermal Overloads | Bus Voltage Violation
Total | 10 miles 69-kV 80 miles 138-kV | 17 buses 69-kV

## Slide 5: Assumed Reactive Power Compensation
Assumed reactive compensation devices were included as placeholders in this independent review
The future reactive upgrades are not expected to materially affect nor be affected by the preferred option identified by this independent review
ERCOT and AEP agreed to re-visit the reactive compensation needs, as short lead-time projects, at a later time when load dynamic characteristics information becomes available
Focus of this independent review is to identify any necessary long lead-time transmission upgrades

## Slide 6: Comparison of Project Options
ERCOT short-listed two options
Option 3 would serve the new confirmed industrial load through a double-circuit 345-kV loop while Option 4 would serve the Corpus Christi load through a radial double-circuit 345-kV line
 | Option 3 | Option 4
Met ERCOT and NERC Reliability Criteria | Yes | Yes
Improved Operational Flexibility (Planned Maintenance Outages) | Yes | Yes
Load Serving Capability (Thermal limited) | -- | Better
Capital Cost Estimates | $291 M | $215 M

## Slide 7: Congestion Analysis
ERCOT concluded that Option 4 did not cause new or additional congestion
Upgrade of Pelican to Whitepoint 138-kV line was found to meet economic planning criteria and was added to ERCOT preferred Option 4

## Slide 8: ERCOT Recommendation:
Based on the review, ERCOT will recommend the Board endorse Option 4 to address the reliability need in the study region
Estimated Capital Cost: $218.5 Million
ERCOT will recommend that the Board deems the Option 4 project critical to reliability

## Slide 9: ERCOT Recommendation: Option 4
A new Angstrom 345-kV substation tapped into the 345-kV line from Whitepoint to STP
A new 345/138-kV Naismith substation
Two new 345/138-kV transformers at Naismith
Two new 138-kV circuits on a double-circuit tower from Naismith to Resnik (~3 miles)
One new 345-kV line on a double-circuit tower from Grissom to Angstrom (~17 miles)
One new 345-kV line on a double-circuit tower from Angstrom to Naismith (~19 miles)
A new second 345/138-kV transformer at the Whitepoint substation
Upgrade the 4.7-mile, 138-kV transmission line from Pelican to Whitepoint.

## Slide 10: Option 4 One-Line Diagram