ERCOT Nodal Operating Guides

Section 11:  Constraint Management Plans and

Remedial Action Schemes

March 1, 2020

11  CONSTRAINT MANAGEMENT PLANS AND REMEDIAL ACTION SCHEMES	11-1

11.1 	Introduction	11-1

11.2 	Remedial Action Schemes	11-1

11.2.1 	Reporting of RAS Operations	11-11

11.3	Automatic Mitigation Plans	11-12

11.4	Remedial Action Plan	11-14

11.4.1	Remedial Action Plan Process	11-15

11.5	Mitigation Plan	11-16

11.6	Pre-Contingency Action Plans	11-16

11.6.1	Pre-Contingency Action Plan Process	11-17

11.7	Temporary Outage Action Plan	11-18

- 11	CONSTRAINT MANAGEMENT PLANS AND REMEDIAL ACTION SCHEMES

- 11.1 	Introduction

(1)	Constraint Management Plans (CMPs) are developed in accordance to the guidelines set forth in the sections below, and are defined in Protocol Section 2.1, Definitions.  CMPs include, but are not limited to the following:

(a)	Remedial Action Plans (RAPs) which are modeled in Network Security Analysis (NSA) where practicable;

(b)	Automatic Mitigation Plans (AMPs) which are modeled in NSA where practicable;

(c)	Pre-Contingency Action Plans (PCAPs);

(d)	Temporary Outage Action Plans (TOAPs); and

(e)	Mitigation Plans.

(2)	When developing CMPs, ERCOT shall first attempt to utilize the 15-Minute Rating of the impacted Transmission Facilities, where available, to develop RAPs such that the ERCOT Transmission Grid is utilized to the fullest extent.

(3)	Remedial Action Schemes (RASs) and/or AMPs may also be implemented in order to allow Generation Resources or Transmission Facilities that would otherwise be subject to restrictions to operate to their full Rating.

(4)	ERCOT shall provide notification to the market of any approved, amended, or removed CMP or RAS.  ERCOT shall provide notification to the market of any RAP, AMP, or RAS that cannot be modeled in the Network Operations Model.  ERCOT shall post to the Market Information System (MIS) Secure Area all CMPs and RASs and any unmodeled CMPs or RASs.

(5)	ERCOT shall provide notification to the market of any proposed RASs or PCAPs on the MIS Secure Area.

(6)	ERCOT is not required to provide notification to the market of any proposed TOAPs.

(7)	All submittals related to CMPs or RASs must be emailed to ras_cmp@ercot.com.

- 11.2 	Remedial Action Schemes

(1)	Remedial Action Schemes (RASs) are designed to detect abnormal predetermined ERCOT System conditions and automatically take corrective actions to maintain a secure system.

(2)	The following do not individually constitute a RAS:

(a)	Protection systems installed for the purpose of detecting faults on Transmission Elements and isolating the faulted Transmission Elements;

(b)	Schemes for automatic Under-Frequency Load Shedding (UFLS) and automatic Under-Voltage Load Shedding (UVLS) comprised of only distributed relays;

(c)	Out-of-step tripping and power swing blocking;

(d)	Automatic reclosing schemes;

(e)	Schemes applied on a Transmission Element for non-fault condition, such as, but not limited to, generator loss-of-field, transformer top-oil temperature, overvoltage or overload to protect the Transmission Element against damage by removing it from service;

(f)	Controllers that switch or regulate one or more of the following: series or shunt reactive devices, flexible alternating current transmission system (FACTS) devices, phase-shifting transformers, variable-frequency transformers, or tap-changing transformers; and that are located at and monitor quantities solely at the same station as the Transmission Element being switched or regulated;

(g)	FACTS controllers that remotely switch static shunt reactive devices located at other stations to regulate the output of a single FACTS device;

(h)	Schemes or controllers that remotely switch shunt reactors and shunt capacitors for voltage regulation that would otherwise be manually switched;

(i)	Schemes that automatically de-energize a line for a non-faults operation when one end of the line is open;

(j)	Schemes that provide anti-islanding protection (e.g. protect Load from effects of being isolated with generation that may not be capable of maintaining acceptable frequency and voltage);

(k)	Automatic sequences that proceed when manually initiated solely by a System Operator;

(l)	Modulation of high voltage, direct current (HVDC) or FACTS via supplementary controls, such as angle damping or frequency damping applied to damp local or inter-area oscillation;

(m)	Sub-synchronous resonance protection schemes that directly detect sub-synchronous quantities (e.g. currents or torsional oscillations); or

(n)	Generation controls such as, but not limited to, Automatic Generation Control (AGC), generation excitation (e.g. Automatic Voltage Regulation (AVR) and Power System Stabilizers (PSSs)), fast valving, and speed governing.

(3)	In addition to the requirements in the Protocols and applicable North American Electric Reliability Corporation (NERC) Reliability Standards, RASs shall also meet the following requirements:

(a)	A RAS may be proposed by a Transmission Service Provider (TSP) or Resource Entity, and be approved by ERCOT and the TSP(s) and/or Resource Entity(ies) included in the RAS prior to implementation;

(b)	The RAS owner(s) shall coordinate the design and implementation of the RAS with the owners and operators of Facilities included in the RAS, including but not limited to Generation Resources, TSPs and Direct Current Ties (DC Ties);

(c)	The RAS shall be automatically armed when appropriate;

(d)	The RAS shall not operate unnecessarily.

(e)	To avoid unnecessary RAS operation, the RAS owner(s) may provide a Real-Time status indication to the owner of any Generation Resource controlled by the RAS to show when the flow on one or more of the RAS monitored Facilities exceeds 90% of the flow necessary to arm the RAS.  The cost necessary to provide such status indication shall be the responsibility of the RAS owner(s);

(f)	The status indication of any automatic or manual arming/activation or operation of the RAS shall be provided as Supervisory Control and Data Acquisition (SCADA) alarm inputs to the owner(s) of any Facility controlled by the RAS;

(g)	When a RAS is removed from service, the RAS owner(s) or a Designated Agent shall immediately notify ERCOT;

(h)	When a RAS is returned to service, the RAS owner or its Designated Agent shall immediately notify ERCOT.  ERCOT shall modify its reliability constraints to recognize the availability of the RAS;

(i)	The RAS owner(s) shall telemeter the status indication of the following items by SCADA to ERCOT for incorporation into ERCOT systems:

(i)	Any automatic or manual arming/activation or operation of the RAS;

(ii)	The in-service/out-of-service status of the RAS; and

(iii)	Any additional related telemetry that already exists pertinent to the monitoring of the RAS (e.g. status indication of communications links between associated RAS equipment and the owner’s control center, arming limits of associated RAS equipment).

(j)	The TSP may receive telemetry for a Resource Entity owned RAS through ERCOT or through the RAS owner(s), at the option of the TSP.  The RAS owner(s), at its own cost, must provide telemetry for Resource Entity owned RASs to the TSP upon request.

(4)	The owner(s) of an existing, modified, or proposed RAS shall submit documentation of the RAS to ERCOT for review and compilation into an ERCOT RAS database using the form in Section 8, Attachment K, Remedial Action Scheme (RAS) Template.  The documentation shall detail the design, operation, modeling, functional testing, and coordination of the RAS with other RASs, Automatic Mitigation Plans (AMPs), protection and control systems.

(a)	ERCOT shall conduct a review of each proposed RAS, each proposed modification and proposed indefinite deactivation and/or termination of an existing RAS.  Additionally, it shall conduct a review of each existing RAS at least every five years as required by changes in system conditions.  Upon receipt, ERCOT shall initiate a 30 working day review period to evaluate each proposal in accordance with paragraph (e) below.  ERCOT shall coordinate any additional time needed for the evaluation with the RAS owner(s).

(b)	The review of a proposed RAS shall be completed before the RAS is placed in service.  The timing of placing the RAS into service must be coordinated with and approved by ERCOT.  The implementation schedule must be confirmed through submission of a Network Operations Model Change Request (NOMCR) to ERCOT.

(c)	Existing RASs that have already undergone at least one review shall remain in service during any subsequent review.  Modifications to existing RASs may be implemented upon approval by ERCOT.

(d)	The schedule for placing a RAS into service must be coordinated among ERCOT and the owners of the Facility controlled by the RAS, and shall provide sufficient time to perform any necessary functional testing prior to its being placed in service.

(e)	ERCOT review of a RAS shall:

(i)	Validate that RAS mitigates the system condition(s) or contingency(ies) for which it was designed;

(ii)	Identify any conflicts with the Protocols, NERC Reliability Standards, and these Operating Guides;

(iii)	Evaluate and demonstrate that the RAS shall be designed so that  a single RAS component failure, when the RAS, was intended to operate, does not prevent the interconnected transmission system from meeting the performance requirements defined in NERC Reliability Standards;

(iv)	Evaluate and document the consequences of misoperation, incorrect operation, or unintended operation of a RAS, when considered by itself and without any other system contingency;

(v)	Evaluate and demonstrate that proposed RAS will coordinate with other RASs, AMPs, protection and control systems and applicable emergency procedures;

(vii)	Evaluate future transmission project(s) that will eliminate the need for the RAS; and

(vii)	Upon completion of ERCOT’s RAS review, ERCOT shall provide all results and underlying studies to the RAS owner(s).

(f)	If deficiencies are identified by ERCOT or other parties’ comments, the RAS owner(s) shall either submit an amended RAS proposal or withdraw the RAS proposal.  The amended RAS proposal shall undergo the review process specified in item (4)(e) above using the timeline in item (4)(a) above until the identified deficiencies have been resolved to the satisfaction of ERCOT.

(g)	As part of the ERCOT review, ERCOT may notify the Steady State Working Group (SSWG), the Dynamics Working Group (DWG), and the System Protection Working Group (SPWG) of the RAS proposal, and each working group or any member of each working group may provide any comments, questions, or issues to ERCOT.  ERCOT may work with the owner(s) of Facilities affected by the RAS as necessary to address all issues.

(h)	ERCOT shall develop a method to include the RAS where practicable in Security-Constrained Economic Dispatch (SCED), Outage coordination, and Reliability Unit Commitment (RUC).

(i)	ERCOT’s review shall provide an opportunity for and include consideration of comments submitted by Market Participants affected by the RAS.

[NOGRR183: Replace Section 11.2 above with the following upon system implementation of NPRR955:] - 11.2 Remedial Action Schemes (1) Remedial Action Schemes (RASs) are designed to detect abnormal predetermined ERCOT System conditions and automatically take corrective actions to maintain a secure system. (2) The following do not individually constitute a RAS: (a) Protection systems installed for the purpose of detecting faults on Transmission Elements and isolating the faulted Transmission Elements; (b) Schemes for automatic Under-Frequency Load Shedding (UFLS) and automatic Under-Voltage Load Shedding (UVLS) comprised of only distributed relays; (c) Out-of-step tripping and power swing blocking; (d) Automatic reclosing schemes; (e) Schemes applied on a Transmission Element for non-fault condition, such as, but not limited to, generator loss-of-field, transformer top-oil temperature, overvoltage or overload to protect the Transmission Element against damage by removing it from service; (f) Controllers that switch or regulate one or more of the following: series or shunt reactive devices, flexible alternating current transmission system (FACTS) devices, phase-shifting transformers, variable-frequency transformers, or tap-changing transformers; and that are located at and monitor quantities solely at the same station as the Transmission Element being switched or regulated; (g) FACTS controllers that remotely switch static shunt reactive devices located at other stations to regulate the output of a single FACTS device; (h) Schemes or controllers that remotely switch shunt reactors and shunt capacitors for voltage regulation that would otherwise be manually switched; (i) Schemes that automatically de-energize a line for a non-faults operation when one end of the line is open; (j) Schemes that provide anti-islanding protection (e.g. protect Load from effects of being isolated with generation that may not be capable of maintaining acceptable frequency and voltage); (k) Automatic sequences that proceed when manually initiated solely by a System Operator; (l) Modulation of high voltage, direct current (HVDC) or FACTS via supplementary controls, such as angle damping or frequency damping applied to damp local or inter-area oscillation; (m) Sub-synchronous resonance protection schemes that directly detect sub-synchronous quantities (e.g. currents or torsional oscillations); or (n) Generation controls such as, but not limited to, Automatic Generation Control (AGC), generation excitation (e.g. Automatic Voltage Regulation (AVR) and Power System Stabilizers (PSSs)), fast valving, and speed governing. (3) In addition to the requirements in the Protocols and applicable North American Electric Reliability Corporation (NERC) Reliability Standards, RASs shall also meet the following requirements: (a) A RAS may be proposed by a Transmission Service Provider (TSP) or Resource Entity, and be approved by ERCOT and the TSP(s) and/or Resource Entity(ies) included in the RAS prior to implementation; (b) The design, implementation, and testing of the RAS shall be coordinated within the RAS Entity; (c) The RAS shall be automatically armed when appropriate; (d) The RAS shall not operate unnecessarily; (e) A RAS designated as a Limited Impact RAS shall be reviewed according to the process described in paragraph (4)(e) below and subject to ERCOT approval; (f) For a RAS not designated by ERCOT as a Limited Impact RAS, the possible inadvertent operation of the RAS, resulting from any single RAS component malfunction satisfies all of the following as determined by the review process in paragraph (4)(e) below and subject to ERCOT approval: (i) The ERCOT System shall remain stable; (ii) Cascading shall not occur; (iii) Applicable Facility Ratings shall not be exceeded; (iv) ERCOT System voltages shall be within post-contingency voltage limits and post-contingency voltage deviation limits; (v) Transient voltage responses shall be within acceptable limits. (g) To avoid unnecessary RAS operation, the RAS Entity may provide a Real-Time status indication to the owner of any Generation Resource controlled by the RAS to show when the flow on one or more of the RAS monitored Facilities exceeds 90% of the flow necessary to arm the RAS. The cost necessary to provide such status indication shall be the responsibility of the RAS Entity; (h) The status indication of any automatic or manual arming/activation or operation of the RAS shall be provided as Supervisory Control and Data Acquisition (SCADA) alarm inputs to the owner(s) of any Facility controlled by the RAS; (i) When a RAS is removed from service, the RAS Entity or a Designated Agent shall immediately notify ERCOT; (j) When a RAS is returned to service, the RAS Entity or its Designated Agent shall immediately notify ERCOT. ERCOT shall modify its reliability constraints to recognize the availability of the RAS; (k) The RAS Entity shall telemeter the status indication of the following items by SCADA to ERCOT for incorporation into ERCOT systems: (i) Any automatic or manual arming/activation or operation of the RAS; (ii) The in-service/out-of-service status of the RAS; and (iii) Any additional related telemetry that already exists pertinent to the monitoring of the RAS (e.g. status indication of communications links between associated RAS equipment and the owner’s control center, arming limits of associated RAS equipment); and (l) The TSP may receive telemetry for a Resource Entity owned RAS through ERCOT or through the RAS Entity, at the option of the TSP. The RAS Entity, at its own cost, must provide telemetry for Resource Entity owned RASs to the TSP upon request. (4) The RAS Entity shall submit to ERCOT documentation of an existing, modified, proposed, or retiring RAS for review and compilation into an ERCOT RAS database using the form in Section 8, Attachment K, Remedial Action Scheme (RAS) Template. The documentation shall detail the design, operation, modeling, functional testing, and coordination of the RAS with other RASs, Automatic Mitigation Plans (AMPs), protection and control systems. (a) ERCOT shall conduct a review of each proposed RAS, each proposed modification and proposed indefinite deactivation and/or termination of an existing RAS. Additionally, it shall conduct a review of each existing RAS at least once every five years or as required by changes in system conditions. Upon receipt, ERCOT shall initiate a 30 Business Day review period to evaluate each proposal in accordance with paragraph (4)(e) below. ERCOT shall coordinate any additional time needed for the evaluation with the RAS Entity. (b) The review of a proposed RAS shall be completed before the RAS is placed in service. The timing of placing the RAS into service must be coordinated with and approved by ERCOT. The implementation schedule must be confirmed through submission of a Network Operations Model Change Request (NOMCR) to ERCOT. (c) Existing RASs that have already undergone at least one review shall remain in service during any subsequent review. Modifications to existing RASs may be implemented upon approval by ERCOT. (d) The schedule for placing a RAS into service must be coordinated among ERCOT and the RAS Entity, and shall provide sufficient time to perform any necessary functional testing prior to its being placed in service. (e) ERCOT review of a RAS shall: (i) Validate that RAS actions, designed timing, and arming conditions mitigate the system condition(s) or contingency(ies) for which it was designed; (ii) Identify any conflicts with the Protocols, NERC Reliability Standards, and this Operating Guide; (iii) Validate that transient voltage responses are within acceptable limits as established by ERCOT; (iv) Evaluate and document the consequences of misoperation, incorrect operation, unintended operation, or failure of a RAS. Additionally, validate that the RAS is designed to meet the requirements in paragraphs (3)(e) and (3)(f) above. (v) Validate that the proposed RAS facilitates periodic testing and maintenance; (vi) Determine whether or not the RAS is a Limited Impact RAS; (vii) Validate that the proposed RAS avoids adverse interactions with other RASs, AMPs, protection and control systems, and applicable emergency procedures; (viii) Evaluate the effects of future bulk electric system modifications on the design and operation of the RAS where applicable; (ix) Validate the implementation of RAS logic appropriately correlates desired actions (outputs) with events and conditions (inputs); (x) Validate the mechanism of procedure by which the RAS is armed is clearly described, and is appropriate for reliable arming and operation of the RAS for the conditions and events for which it is designated to operate; (xi) Evaluate future transmission project(s) that will eliminate the need for the RAS; and (xii) Validate that for proposed RAS retirements, system performance and security will not be affected. (f) Upon completion of ERCOT’s RAS review, ERCOT shall provide all results and underlying studies to the RAS Entity and each impacted TSP. (g) If deficiencies are identified for a new, functionally modified, or retiring RAS by ERCOT or other parties’ comments, the RAS Entity shall either submit an amended RAS proposal or withdraw the RAS proposal. The amended RAS proposal shall undergo the review process specified in paragraph (4)(e) above using the 30 Business Day RAS review timeline in paragraph (4)(a) above until the identified deficiencies have been resolved to the satisfaction of ERCOT. (h) As part of the ERCOT review, ERCOT may notify the Steady State Working Group (SSWG), the Dynamics Working Group (DWG), and the System Protection Working Group (SPWG) of the RAS proposal, and each working group or any member of each working group may provide any comments, questions, or issues to ERCOT. ERCOT may work with the owner(s) of Facilities affected by the RAS as necessary to address all issues. (i) ERCOT shall develop a method to include the RAS where practicable in Security-Constrained Economic Dispatch (SCED), Outage coordination, and Reliability Unit Commitment (RUC). (j) ERCOT’s review shall provide an opportunity for and include consideration of comments submitted by Market Participants affected by the RAS. (k) ERCOT shall update the RAS database at least once every 12 calendar months. (5) ERCOT shall conduct an evaluation of each RAS at least once every five years to determine the following: (a) The RAS mitigates the system condition(s) or contingency(ies) for which it was designed; (b) The RAS avoids adverse interactions with other RAS, and protection and control systems; and (c) The RAS meets the requirements in paragraphs (3)(e) and (3)(f) above. (6) ERCOT shall provide the results of the RAS evaluation including any identified deficiencies to the RAS Entity and impacted TSPs. Within six calendar months, the RAS Entity shall develop and submit a corrective action plan, subject to ERCOT approval, to correct the deficiencies. For each plan developed, the RAS Entity shall implement the approved plan, update the plan if actions or timetables change, and notify ERCOT via email at ras_cmp@ercot.com if plan actions or timetables change and when the plan is completed. (7) The RAS Entity shall perform a functional test of each of its RAS to verify the overall RAS performance and the proper operation of non-protection system components at least once every six calendar years for a RAS not designated as a Limited Impact RAS, and once every 12 calendar years for a RAS designated as a Limited Impact RAS. For any identified deficiencies, the RAS Entity shall develop and submit a corrective action plan within six calendar months, and subject to ERCOT approval, to correct the deficiencies. For each plan developed, the RAS Entity shall implement the approved plan, update the plan if actions or timetables change, and notify ERCOT via email at ras_cmp@ercot.com if plan actions or timetables change and when the plan is completed.

- 11.2.1 	Reporting of RAS Operations

(1)	RAS owner(s) shall notify ERCOT of all RAS operations.  Documentation of RAS failures or misoperations shall be provided to ERCOT using the Relay Misoperation Report form as an email to ras_cmp@ercot.com.  The RAS owner(s) shall conduct an analysis of all RAS operations, misoperations, and failures.  If deficiencies are identified, a plan to correct the deficiencies shall be developed by the RAS owner(s) subject to the approval of ERCOT within 180 days of being identified and implemented by the RAS owner(s).  Analysis of RAS operational performance shall include, but is not limited to:

(a)	Determination of whether system events or conditions appropriately armed or triggered the RAS;

(b)	Determination of whether the RAS responded as designed;

(c)	Determination of whether the RAS was effective in mitigating the performance issues it was designed to address; and

(d)	Determination of whether the RAS operation resulted in any unintended or adverse system response.

(2)	ERCOT shall report all RAS operations and misoperations to the Reliability Monitor for review.  RAS arming or activation that ramps generation back is not considered an operation or misoperation with respect to reporting requirements to the Reliability Monitor and the NERC Regional Entity.  A misoperation of a RAS with respect to reporting requirements to the Reliability Monitor and the NERC Regional Entity occurs when one of the items specified in paragraph (4) of Section 6.2.3, Performance Analysis Requirements for ERCOT System Facilities, occur.  Owners of RASs will provide a monthly report to ERCOT by the 15th of each month describing each instance a RAS armed/activated and reset during the previous month.  The report will include the date and time of arming/activation and reset. ERCOT shall consolidate the monthly reports and forward to the Reliability Monitor and NERC Regional Entity.

(3)	If a RAS which removes generation from service operates more than two times within a six month period and the operations are not a direct result of an ERCOT System disturbance or a contingency operation, ERCOT may require the Generation Resource owner(s) to decrease the available capability on the affected Generation Resource(s).  The amount of available capacity to be decreased shall be determined by ERCOT.  The decreased available capacity on the Generation Resource(s) shall remain until the Generation Resource owner(s) provides documentation that demonstrates the Generation Resource(s) can properly control output in a pre-contingency or normal ERCOT System condition.

(4)	For each RAS, the owner(s) shall either identify a preferred exit strategy or explain why no exit strategy is needed to ERCOT.  Once an exit strategy is complete and a RAS is no longer needed, the owner(s) of an existing RAS shall notify ERCOT, whenever the RAS is to be permanently disabled, and shall do so according to a timetable coordinated with and approved by ERCOT and the owners of all Facilities controlled by the RAS.

[NOGRR183: Replace Section 11.2.1 above with the following upon system implementation of NPRR955:] - 11.2.1 Reporting of RAS Operations (1) RAS Entity shall notify ERCOT of all RAS operations. Documentation of RAS failures or misoperations shall be provided to ERCOT using the Relay Misoperation Report form as an email to ras_cmp@ercot.com. Within 120 calendar days, the RAS Entity shall conduct an analysis of all RAS operations, misoperations, and failures. If deficiencies are identified, the RAS Entity shall develop and submit a corrective action plan within six calendar months, and subject to ERCOT approval, correct the deficiencies. For each plan developed, the RAS Entity shall implement the approved plan, update the plan if actions or timetables change, and notify ERCOT via email at ras_cmp@ercot.com if plan actions or timetables change and when the plan is completed. Analysis of RAS operational performance shall include, but is not limited to: (a) Determination of whether system events or conditions appropriately armed or triggered the RAS; (b) Determination of whether the RAS responded as designed; (c) Determination of whether the RAS was effective in mitigating the performance issues it was designed to address; and (d) Determination of whether the RAS operation resulted in any unintended or adverse system response. (2) ERCOT shall report all RAS operations and misoperations to the Reliability Monitor for review. RAS arming or activation that ramps generation back is not considered an operation or misoperation with respect to reporting requirements to the Reliability Monitor and the NERC Regional Entity. A misoperation of a RAS with respect to reporting requirements to the Reliability Monitor and the NERC Regional Entity occurs when one of the items specified in paragraph (4) of Section 6.2.3, Performance Analysis Requirements for ERCOT System Facilities, occur. RAS Entities will provide a monthly report to ERCOT by the 15th of each month describing each instance a RAS armed/activated and reset during the previous month. The report will include the date and time of arming/activation and reset. ERCOT shall consolidate the monthly reports and forward to the Reliability Monitor and NERC Regional Entity on a quarterly basis. (3) If a RAS which removes generation from service operates more than two times within a six month period and the operations are not a direct result of an ERCOT System disturbance or a contingency operation, ERCOT may require the Generation Resource Entity(ies) to decrease the available capability on the affected Generation Resource(s). The amount of available capacity to be decreased shall be determined by ERCOT. The decreased available capacity on the Generation Resource(s) shall remain until the Generation Resource Entity(ies) provides documentation that demonstrates the Generation Resource(s) can properly control output in a pre-contingency or normal ERCOT System condition. (4) For each RAS, the RAS Entity shall either identify a preferred exit strategy or explain why no exit strategy is needed to ERCOT. Once an exit strategy is complete and a RAS is no longer needed, the RAS Entity shall notify ERCOT, whenever the RAS is to be permanently disabled, and shall do so according to a timetable coordinated with and approved by ERCOT and the owners of all Facilities controlled by the RAS.

11.3	Automatic Mitigation Plans

(1)	Automatic Mitigation Plans (AMPs) are defined in Protocol Section 2.1, Definitions, and may be relied upon to detect predetermined abnormal system conditions and automatically take pre-coordinated corrective actions to maintain a secure system.

(2)	AMPs must:

(a)	Be proposed by a Transmission Service Provider (TSP) or Resource Entity, and be approved by ERCOT and the TSP(s) and/or Resource Entity(ies) included in the AMP prior to implementation;

(b)	Be designed and implemented in coordination with the owners and operators of Facilities included in the AMP and approved by ERCOT;

(c)	Be automatically armed when appropriate;

(d)	Not operate unnecessarily;

(e)	Comply with all applicable requirements in the Protocols and applicable North American Electric Reliability Corporation (NERC) Reliability Standards; and

(f)	Not include generation re-Dispatch or Load shed.

(3)	AMP Owner(s) or a Designated Agent shall:

(a)	Immediately notify ERCOT, when an AMP is removed from service and when an AMP is returned to service.  ERCOT shall modify its reliability constraints to recognize the availability of the AMP;

(b)	Telemeter the status indication of the following items by Supervisory Control and Data Acquisition (SCADA) to ERCOT for incorporation into ERCOT systems:

(i)	Any automatic or manual arming/activation or operation of the AMP;

(ii)	In-service/out-of-service status of the AMP; and

(iii)	Any additional related telemetry that already exists pertinent to the monitoring of the AMP (e.g. status indication of communications links between associated AMP equipment and the owner’s control center, arming limits of associated AMP equipment).

(c)	Provide the status indication of any automatic or manual arming/activation or operation of the AMP as SCADA alarm inputs to the owner(s) of any Facility controlled by the AMP; and

(d)	Submit documentation when proposing or modifying and/or deactivating/terminating an AMP that detail its design, operation and coordination of the AMP with other Remedial Action Schemes (RASs), AMPs, protection and control systems.

(5)	ERCOT shall conduct a review of each proposed AMP, each proposed modification and proposed indefinite deactivation and/or termination of an existing AMP.  Additionally, ERCOT shall conduct a review of each existing AMP annually or as required by changes in system conditions to ensure its continued effectiveness.

11.4	Remedial Action Plan

(1)	Remedial Action Plans (RAPs) are defined in Protocol Section 2.1, Definitions, and may be relied upon in allowing additional use of the transmission system in Security-Constrained Economic Dispatch (SCED).  Normally, it is desirable that a Transmission Service Provider (TSP) constructs Transmission Facilities adequate to eliminate the need for any RAP; however, in some circumstances, such construction may be unachievable in the available time frame.

(2)	RAPs must:

(a)	Be coordinated by ERCOT with all Transmission Operators (TOs) and Resource Entities included in the RAP, and approved by ERCOT;

(b)	Be limited to the time required to construct replacement Transmission Facilities; however, the RAP will remain in effect if ERCOT has determined the replacement Transmission Facilities to be impractical;

(c)	Comply with all applicable requirements in the Protocols and applicable North American Electric Reliability Corporation (NERC) Reliability Standards;

(d)	Clearly define and document TOs and Resource Entities included in the RAP actions;

(e)	Must be able to resolve the issue for which it was designed over the range of conditions that might reasonably be experienced;

(f)	Be executed by the TOs and/or Resource Entities;

(g)	Have a 15-minute Rating greater than the Normal and Emergency Ratings for the Transmission Facilities it intends to resolve;

(h)	Be defined in the Network Operations Model and considered in the SCED and Reliability Unit Commitment (RUC) processes.  RAPs that cannot be modeled using ERCOT’s existing infrastructure shall be rejected unless the Technical Advisory Committee (TAC) approves a plan to work around the infrastructure problem; and

(i)	Not include generation re-Dispatch or Load shed.

(3)	An approved RAP may be executed immediately after a contingency by the TOs and Resource Entities included in the RAP without instruction by ERCOT or shall be executed upon direction by ERCOT.

(4)	ERCOT shall conduct a review of each existing RAP annually or as required by changes in system conditions to ensure its continued effectiveness.  Each review shall proceed according to a process and timetable documented in ERCOT Procedures.

(5)	ERCOT may approve the expiration of a RAP after consultation with the TOs and Resource Entities included in the RAP.  ERCOT shall modify its reliability constraints to recognize the unavailability of the RAP.

11.4.1	Remedial Action Plan Process

(1)	RAPs may be proposed by any Market Participant or may be developed by ERCOT.  For RAPs submitted by Market Participants not registered as a TSP:

(a)	ERCOT shall post RAPs submitted by a Market Participant not registered as a TSP on the Market Information System (MIS) Secure Area as soon as practicable, but no later than five Business Days of receipt.

(b)	ERCOT shall provide a five Business Day comment period from the date when the proposed RAP under review is posted by ERCOT unless notice of a shorter comment period is provided.

(c)	ERCOT shall consider all comments received within the five Business Day comment period on the proposed RAP, along with its own evaluation and those of the Transmission Facility owners, and either approve, modify or reject that proposed RAP.

(d)	If a proposed RAP is modified or rejected, ERCOT shall post an explanation for the rejection or a description of the modification.

- 11.5	Mitigation Plan

(1)	Mitigation Plans are defined in Protocol Section 2.1, Definitions, and shall not be used to manage constraints in Security-Constrained Economic Dispatch (SCED).  Normally, it is desirable that a Transmission Service Provider (TSP) constructs Transmission Facilities adequate to eliminate the need for a Mitigation Plan; however, in some circumstances, such construction may be unachievable in the available time frame.

(2)	A Mitigation Plan may be proposed by any TSP, and be approved by ERCOT and the included Transmission Operator (TO) prior to implementation.  Mitigation Plans must:

(a)	Be coordinated with the TOs included in the Mitigation Plan;

(b)	Limited in use to the time required to construct replacement Transmission Facilities; however, the Mitigation Plan will remain in effect if ERCOT has determined the replacement Transmission Facilities to be impractical;

(c)	Comply with all requirements of the Protocols and applicable North American Electric Reliability Corporation (NERC) Reliability Standards;

(d)	Clearly define and document TO actions;

(e)	Be executed by TOs;

(f)	Be able to be implemented in a timeframe that will not result in loss of the overloaded Transmission Facility;

(g)	Identify the most limiting protective relay setting beyond the 15-Minute Rating when developing the Mitigation Plan in advance or as soon as practicable when developing the Mitigation Plan in Real-Time;

(h)	Not subject ERCOT to unacceptable risk of widespread cascading Outages; and

(i)	Not include generation re-Dispatch.

(3)	An approved Mitigation Plan may be executed immediately, post-contingency, by the TO without instruction by ERCOT or shall be executed upon direction by ERCOT.

- (4)	Restoration of any Load shed by executing the Mitigation Plan shall be coordinated with ERCOT.

- 11.6	Pre-Contingency Action Plans

(1)	Pre-Contingency Action Plans (PCAPs) are defined in Protocol Section 2.1, Definitions, and are implemented in anticipation of a contingency.  Normally, it is desirable that a Transmission Service Provider (TSP) construct Transmission Facilities adequate to eliminate the need for any PCAP; however, in some circumstances, such construction may be unachievable in the available time frame.

(2)	A PCAP may be proposed by any Market Participant, and be approved by ERCOT and the Transmission Operator (TO) included in the PCAP prior to implementation.  PCAPs must:

(a)	Be coordinated with the TOs included in the PCAP;

(b)	Be limited in use to the time required to construct replacement Transmission Facilities and until such Facilities are placed in-service, or the PCAP is no longer needed; however, the PCAP will remain in effect if ERCOT has determined the replacement Transmission Facilities to be impractical;

(c)	Comply with all requirements of the Protocols and applicable North American Electric Reliability Corporation (NERC) Reliability Standards;

(d)	Clearly define and document TO actions;

(e)	Be executed by TOs; and

(f)	Not include generation re-Dispatch or Load shed.

(3)	An approved PCAP may be executed immediately prior to a contingency by the TO without instruction by ERCOT, or shall be executed upon direction by ERCOT.

(4)	All proposed, approved, amended, and removed PCAPs shall be managed in accordance with paragraph (4) of Section 11.1, Introduction.

(5)	ERCOT may limit the quantity of PCAPs that are used.

- 11.6.1	Pre-Contingency Action Plan Process

(1)	PCAPs may be proposed by any Market Participant or may be developed by ERCOT.  For PCAPs submitted by Market Participants not registered as a TSP:

(a)	ERCOT shall post PCAPs submitted by a Market Participant not registered as a TSP on the Market Information System (MIS) Secure Area as soon as practicable, but no later than five Business Days of receipt.

(b)	ERCOT shall provide a five Business Day comment period from the date when the proposed PCAP under review is posted by ERCOT unless notice of a shorter comment period is provided.

(c)	ERCOT shall consider all comments received within the five Business Day comment period on the proposed PCAP, along with its own evaluation and those of the Transmission Facility owners, and either approve, modify or reject that proposed PCAP.

(d)	If a proposed PCAP is modified or rejected, ERCOT shall post an explanation for the rejection or a description of the modification

- 11.7	Temporary Outage Action Plan

(1)	Temporary Outage Action Plans (TOAPs) are defined in Protocol Section 2.1, Definitions, and shall not be used to manage constraints in Security-Constrained Economic Dispatch (SCED).

(2)	A TOAP may be proposed by any Market Participant and be approved by ERCOT and the Transmission Operator (TO) included in the TOAP prior to implementation.  TOAPs must:

(a)	Be coordinated with the TOs included in the TOAP;

(b)	Limit use to the duration of a specific Transmission Facility or Resource Outage;

(c)	Comply with all requirements of the Protocols and applicable North American Electric Reliability Corporation (NERC) Reliability Standards;

(d)	Clearly define and document TO actions;

(e)	Be executed by TOs;

(f)	Be implemented in a timeframe that will not result in loss of the overloaded Transmission Facility;

(g)	Identify the most limiting protective relay setting beyond the 15-Minute Rating when developing the TOAP in advance or as soon as practicable when developing the TOAP in Real-Time; and

(h)	Not subject ERCOT to unacceptable risk of widespread cascading Outages; and

(i)	Not include generation re-Dispatch.

(3)	An approved TOAP may be executed immediately, post-contingency, by the TO without instruction by ERCOT or shall be executed upon direction by ERCOT.

(4)	ERCOT may limit the quantity of TOAPs that are used.

(5)	Restoration of any Load shed by executing the TOAP shall be coordinated with ERCOT.