## Slide 1: NOGRR215 Discussion Points
Shannon Caraway
Solar Prime LLC

## Slide 2: Managing an Open Access Grid is Challenging
Generation and load can come and go with short notice
Transmission planning, design, and permitting by their nature have longer lead times
Remedial Action Schemes (RASs) have been reliably used for over two decades to manage this timing mismatch
  In most cases, their use is temporary until new transmission upgrades can be designed, permitted, and constructed
  However, in a few cases, such as the East DC tie integration, they have been long-term, because the cost / benefit metrics of new transmission required can not meet the economic hurdles

## Slide 3: High Level RAS Overview
A RAS, is a protection scheme that can automatically take corrective actions, such as adjusting generation, load, or reconfiguring the transmission system
Because these are automatic actions, when deployed post contingency, they can expand the secure operating envelope beyond normal SCED N-1 limits
To illustrate, imagine a new 1,500 MW generator connecting into a 1,000 MWVA transmission line (i.e a Point of Interconnection, with two 1,000 MVA exit lines)
  Without a RAS, the new generator would be SCED limited to <1,000 MW and economically limited even further due to the nodal market design
  With a simple RAS that locally monitors both exit lines and has a run back / trip scheme, the generator can likely operate un-constrained in SCED
Protocols prohibit their use on Interconnection Reliability Operating Limits (IROLs)
A RAS owner can be either a TSP or a Resource Entity

## Slide 4: Long History of RAS Use in ERCOT
Utility use of RASs pre-dated ERCOT deregulation, such as with the East DC tie
Many of the early post-dereg CCGT new gen build, such as Midlothian, Hays, Ennis, Lamar, Kiamichi, Gateway, as well as, more recent CCGT build, such as Mitchell Bend temporarily relied on them, until trans upgrades were made
Similarly, many new renewable gens in West Texas, such as Trent, South Trent, Forest Creek, Rattlesnake, etc. have used them, until trans upgrades were made
Numerous existing generators (Monticello, Martin Lake, Sandow, Stryker, Valley, Morgan, Permian, Ferguson, Wirtz, etc.) have participated in them, while trans upgrades were made to address rapidly changing system conditions.
RASs have also been used to manage rapid load additions, (e.g. Culberson Loop)
In short, RASs have been an indispensable market and reliability tool for 20+ years and now eliminating their use for generation use, would be a major policy change that would create new barriers for gen integration and retention

## Slide 5: Technical and Compliance Overhead
As ERCOT has laid out in their NOGRR215 comments, RASs
  Can in some cases be more complex in their design and implementation, increasing their overhead during their approval process and ongoing mgmt.
  Create the need for additional situational awareness & system mgmt. tools
  Create the need for additional operating procedures and training responsibility for all involved parties (ERCOT, TSP, and Resource Entity)
  Additional NERC compliance overhead for all these same parties
This additional overhead, can translate into additional FTEs, but the key policies, procedures, and system situational awareness infrastructure is relatively mature

## Slide 6: Proposed Motion for WMS Consideration
WMS ask ROS to table action on NOGRR215, while a broader markets and reliability discussion can be had together.
Specifically, hold one or more joint CMWG / OWG meetings dedicated to this topic, where ERCOT is asked to:
  Compare and contrast how the current challenges facing ERCOT are different than previous challenges
    Show the list of RAS installations since 2000
    Are new installations different than the historical installations? If yes, please explain
  Collaborate with market participants to find ways to address reliability concerns and minimizes the impacts to the market
In short, the goal of the joint CMWG / OWG working group is to find a way to address ERCOT’s new pain points, while reliably preserving historic levels of open grid access for all market participants