## Slide 1
Special RTCTF Meeting on Ancillary Service Deployment Expectations and Durations
ERCOT
July 15, 2020

## Slide 2: Acronyms
ERCOT Contingency Reserve Service (ECRS)
Fast Frequency Response (FFR)
Most Severe Single Contingency (MSSC)
Non-Spinning Reserve Service (Non-Spin)
North American Electric Reliability Corporation (NERC)
Physical Responsive Capability (PRC)
Primary Frequency Response (PFR)
Quick-Start Generation Resource (QSGR)
Real-Time Co-optimization (RTC)
Real-Time Market (RTM)
Regulation Down Service (Reg-Down)
Regulation Up Service (Reg-Up)
Responsive Reserve Service (RRS)
Reliability Unit Commitment (RUC)
Security-Constrained Economic Dispatch (SCED)
State-Of-Charge (SOC)

## Slide 3: Ancillary Services Introduction
Each Ancillary Service product is designed and procured to mitigate a unique kind of risk in Real-Time.
Reg-Up and Reg-Down Services are designed to balance system every four seconds to keep the system frequency close to 60 Hz
RRS is designed to ensure ERCOT can avoid shedding firm load for loss of two largest units. Smaller unit trip events are fairly common.
  Per NERC Standard BAL-002, ERCOT Balancing Authority has to recover from Balancing Contingency events within 15 minutes
  Unit trip events greater than 800 MW are considered Balancing Contingency events

## Slide 4: Ancillary Services Introduction cont.
ECRS is designed to recover system frequency back to 60 Hz following Balancing Contingency events and restore RRS.
Non-Spin reserve is primarily procured to mitigate forecast uncertainties and also serves as a replacement reserves to replenish RRS and ECRS.
  Non-Spin requirement are highest during the expected periods of highest risks of net load ramps
  Non-Spin requirements are reduced for any ECRS MW quantities procured
In essence, ECRS and Non-Spin are Ancillary Services that responds slower but has to be sustained longer because net load ramps and forecast uncertainties can last longer

## Slide 5: Ancillary Services Introduction cont.
ERCOT also has an obligation per BAL-002 Standard to restore its NERC defined Contingency Reserve (i.e., PRC) above MSSC within 90 minutes
RUC studies assumes AS capability can be sustained for full one hour. RUC forecasts are hourly averages so on average half of the SCED intervals will be above the net load seen by RUC. Non-spin is procured ensure sufficient capacity to cover net load ramps in these intervals and during hours when forecast error persists longer.
Ancillary Services like ECRS and Non-Spin, that ERCOT is counting on replenishing and sustaining its PRC, has to be capable of sustaining for at least an hour if not longer.

## Slide 6: Ancillary Service Duration Requirements at Other ISOs
NYISO: 10 min and 30 min Reserves must be sustained for at least 1 Hour
MISO: 10 min Reserves must be sustained for at least 1 Hour
PJM: 10 min Reserves must be sustained for at least 30 minutes

## Slide 7: Key Principles on the Definitions of Ancillary Services
The current duration requirement for Ancillary Services is 1 hour, with the exception of FFR
  Resources providing FFR must only be able to sustain the full response for 15 minutes
During discussion on RTC Key Principles in 2019, the task force reviewed topics related to the suite of Ancillary Services
Given the reliability need and deployment of the services and recognizing the ability of the RTM to clear Ancillary Services every 5 minutes, the following principles were adopted:
  MW qualified to provide Regulation Service will be limited to how much Resources can sustain for 15 minutes.
  For RRS, for a Generation Resource or Controllable Load Resource, include a provision to sustain the qualified MW for 15 minutes.

## Slide 8: Key Principles on the Definitions of Ancillary Services cont.
There was also a change regarding qualification for on-line ECRS and Non-Spin where all Resources that are on-line and able to be dispatched by SCED are automatically qualified.
  Changes to the duration of these services were not proposed or discussed
For the remaining Ancillary Service and subtypes, the qualification methodologies and expectations remained as is.
  For RRS from a Resource operating in synchronous condenser fast-response mode
  For RRS from a Load Resources controlled by high set under-frequency relay
  For RRS being provided via FFR
  Off-line Non-Spin
  Off-line ECRS being provided by QSGRs

## Slide 9: Summary of the Ancillary Service Discussions
The table below is intended to provide a summarized view covering topics from both today’s special RTCTF and last month’s special RTCTF
  For all instances, less Ancillary Services may be awarded based on the interaction between power balance and the ASDCs as system conditions get more scarce.
Ancillary Service Subcategory | Qualification Duration | Triggered/Deployed | Recalled
RRS (PFR from SCED-dispatchable Resources) | 15 min. | Automatically based on frequency to deploy more | Automatically based on frequency to deploy less
RRS (under-frequency relay) | 1 hour | Automatically based on a frequency trigger (59.7 Hz); or Manually instructed by ERCOT (EEA or NERC Standards) | Deployed until recalled by ERCOT based on frequency and PRC recovery (XML message shows “0” deployment)
RRS (FFR) | 15 min. | Automatically based on a frequency trigger (59.85 Hz); or Manually instructed by ERCOT (NERC Standards) | Deployed until recalled by ERCOT based on frequency (LFC signal shows “0” deployment)
RRS (Resources in synchronous condenser fast-response mode) | 1 hour | Automatically based on a frequency trigger (59.8 Hz); or Manually instructed by ERCOT (EEA or NERC Standards) | Deployed until recalled by ERCOT based on frequency and PRC recovery (LFC signal shows “0” deployment)

## Slide 10: Summary of the Ancillary Service Discussions cont.
Ancillary Service Subcategory | Qualification Duration | Triggered/Deployed | Recalled
Reg-Up/Down | 15 min. | Automatically through LFC signals to deploy more | Automatically through LFC signals to deploy less
ECRS (SCED-dispatchable Resources including QSGRs) | 1 hour | Less awarded based on the interaction between power balance and the ASDCs | More awarded based on the interaction between power balance and the ASDCs
ECRS (Resources in synchronous condenser fast-response mode | 1 hour | Automatically based on a frequency trigger (59.8 Hz); or Manually instructed by ERCOT (EEA or NERC Standards) | Deployed until recalled by ERCOT based on frequency and PRC recovery (LFC signal shows “0” deployment)
ECRS (“blocky” Load Resources) | 1 hour | Manually instructed by ERCOT (EEA or NERC Standards) | Deployed until recalled by ERCOT based on frequency and PRC recovery (LFC signal shows “0” deployment)
“On-line” Non-Spin | 1 hour | Less awarded based on the interaction between power balance and the ASDCs | More awarded based on the interaction between power balance and the ASDCs
“Off-line” Non-Spin (including non-active power augmentation) | 1 hour | Manually instructed by ERCOT based on PRC, 30-minute system-wide ramp capability, or special congestion circumstances | Deployed until recalled by ERCOT based on PRC, 30-minute system-wide ramp capability, or special congestion circumstances

## Slide 11: Ancillary Service Capability Telemetry in RTC
QSE RRS capability telemetry for SCED-dispatchable Resources to RTC SCED must reflect the energy response the Resource can sustain for a minimum of 15 minutes.
QSE Reg-Up/Down capability telemetry to RTC SCED must reflect the energy response the Resource can sustain for a minimum of 15 minutes.
QSE ECRS/Non-Spin capability telemetry to RTC SCED must reflect the energy response the Resource can sustain for a minimum of 1 hour.

## Slide 12: Example: FFR
 | HSL/LSL (MW) | Max/Min SOC (MWh) | FFR Qual. MW | Energy Bid $/MWh | Energy Offer $/MWh | FFR Offer $/MW/h
Battery A | +-10MW | Max: 20MWh Min: 0.1MWh | 20MW | -10 to 0 MW @$45/MWh | 0 to 10 MW @$100/MWh | 20MW @$0/MW/h
Battery B | +-10MW | Max: 20MWh Min: 0.1MWh | 20MW | -10 to 0 MW @$-300/MWh | 0 to 10 MW @$100/MWh | 20MW @$1/MW/h
Note:
SOC is not used in the ERCOT market software.
Ramp Rate for both Batteries are 999 MW/minute
To be awarded 20 MW of FFR, the Base Point must be -10MW and there must be sufficient stored energy (i.e., SOC) to deliver a sustained 10 MW injection to grid for 15 minutes. 20 MW of FFR is by stopping charging consumption of 10 MW and then injecting 10 MW as measured at the POI
The minimum SOC required for both Batteries to provide 20 MW of FFR is 2.5MWh (10MW*0.25hour)

## Slide 13: Example: FFR
Note: Similar logic would apply for Reg-Up/Down (also 15 minute duration ) and ECRS/Non-Spin (1 hour duration)
20 MW
18 MW
A-UDSP
A-SOC
-10 MW
10 MW
3 MWh
3.33 MWh
2.833 MWh
2 MWh
A-FFR Award
SCED 1
SCED 2
SCED 3
FFR Frequency event @t+2 minutes that lasts for ~7.5 minutes
SCED
Off Cycle
Value |  | SCED 1 @t=0 | SCED Off Cycle @t=3 | SCED 2 @t=5 | SCED 3 @t=10
Battery A telemetry | MW | -10 MW | 10 MW | 10 MW | 10 MW
 | FFR cap | 20 MW | 20 MW | 20 MW | 18 MW
 | SOC | 3 MWh | 3.16 MWh | 2.833 MWh | 2.0 MWh
Battery B telemetry | MW | 0 MW | 0 MW | 0 MW | 0 MW
 | FFR cap | 20 MW | 20 MW | 20 MW | 20 MW
 | SOC | 20 MWh | 20 MWh | 20 MWh | 20 MWh
SCED prices | LMP | $40 / MWh | $43 / MWh | $40 / MWh | $40 / MWh
 | RRS MCPC | $0.5 / MWh | $0.8 / MWh | $0.5 / MWh | $1.0 / MWh
Battery A awards | BP | -10 MW | -10 MW | -10 MW | -10 MW
 | FFR | 20 MW | 20 MW | 20 MW | 18 MW
Battery B awards | BP | 0 MW | 0 MW | 0 MW | 0 MW
 | FFR | 0 MW | 0 MW | 0 MW | 2 MW
3.16 MWh

## Slide 14: Others Ancillary Service Topics Raised at the June 29th RTCTF
There were additional topics that were raised during the June 29th meeting, that aren’t related directly to the primary focus of today’s discussion, but we did want to make note of them.
  Expectation of deployment until recall for “blocky” Ancillary Service deployments, particularly those that occur during scarcity conditions and “off-line” Non-Spin
  Validation of Ancillary Service capability telemetry, such as reasonability checks within ERCOT systems and post-event analysis

## Slide 15
Discussion and wrap-up