## Slide 1
ERCOT Frequency Control Report
June 2020
ERCOT
Operations Planning
PDCWG | July 15th, 2020

## Slide 2: Summary of June 2020
CPS1: 170.75%
Current CPS1 12-Month Rolling Average: 173.74%
0 BAAL Exceedance
5 hourly CPS1 score below 100%
BAAL-003 Events have updated through 2019
2018 BAAL-003 FRM Performance: -843.17
2020 RMS1 Statistics
  Mean: 16.00 mHz
  Min: 12.25 mHz
  Max: 20.34 mHz
Energy Statistics
  Total Energy: 35,374,846 MWh
  Wind Energy: 8,304,076 MWh
  Percent Energy from Wind: 23.47%
  Solar Energy: 980,459 MWh
  Percent Energy from Solar: 2.77%
Minimum System Inertia
  Mean: 232,728
  Max: 272,282 on Jun 10th
  Min: 206,068 on Jun 14th

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
Jun-20 CPS1 (%): 170.75
Notes: Outliers:
1. 63.2% @ 17:00 6/20/2020:
Expected gen deviation:
Large expected gen deviation a the beginning of the hour.(-1812 MW @17:19)
Solar resources contribute significantly to total expected gen deviation from 17:05 to17:20.
Wind/Solar Ramp:
Solar ramps down from 2940 MW to 2380 MW within a 15 min interval from 17:05 to 17:20.
All reg-ups are deployed.
2. 64.8% @ 18:00 6/20/2020:
Expected gen deviation:
Large expected gen deviation for two periods of time for the hour.(18:10 to 18:15,18:26 to 18:46)
(-1228 MW @18:14; -774 MW @18:37 )
Large expected gen deviations are mostly from solar with the exception of thermal generation in shutdown mode.
A thermal unit was in shutdown mode
Wind /solar Ramp: Solar down ramps from 2072 MW to 1885 MW within a 5 min interval from 18:10 to 18:15
Solar down ramps from 2195 MW to 1550 MW within a 20 min interval from 18:26 to 18:46
3. 96.4% @ 12:00 6/22/2020:
Expected gen deviation:
Large expected gen deviation from 12:30 to 12:45. (-2137 MW @12:42 )
Negative throughout the hour.
Large expected gen deviations are from both renewables and thermal resources.
Wind/solar Ramp:
Consistent Wind down ramp throughout the entire hour 11077 MW to 7488 MW ( 300MW /5min)
A steep 100 MW solar down ramp wihtin 5 min from 12:35 to 12:43.
Other:
Generation loss of approximately 72 MW.
4. 69.0% @ 22:00 6/24/2020:
Expected gen deviation:
Large expected gen deviation from 22:10 to 22:20. (-1900 MW @22:20)
A combine cycle resource coming off at the beginning of the hour causing low frequency.
Wind Ramp:
A 170MW /10min wind down occurred at 22:10.
5. 98.7% @ 16:00 6/30/2020:
Expected gen deviation:
Large expected gen deviation at the beginning and the end of the hour. (-1190 MW @16:03; -1498MW @16:48 )
DC tie export ramps from 179 MW to 226 MW during the first 5 minute of the hour.
Wind/Solar Ramp:
Solar ramps down from 2879MW to 2696 MW within 4 minutes at the beginning of the hour.
Wind down ramp 164MW/5min at 16:40
Solar down ramp 191 MW/5min at 16:40.

## Slide 5: BAAL Exceedances & Violations
There was 0 BAAL exceedance in June

## Slide 6: 15-Minute Average CPS1%
June-20 CPS1 (%): 170.75

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 173.74%

## Slide 8: Daily RMS1 of ERCOT Frequency by Year

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2018 BAL-003 Selected Events – Update
Notes: BAL-003

## Slide 19: Op. Year 2018 BAL-003 FRM Performance - Update
Notes: OP2018: FRO = -381.0, FRM_median = -843.17, FRM_average = -959.7
OP2019: FRO = -381.0
OP2020: FRO = -425.0, FRM_median = -811.14, FRM_average = -892.5

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 35,374,846 MWh

## Slide 22: Total Energy from Wind Generation
Notes: 8,304,076 MWh

## Slide 23: % Energy from Wind Generation
Notes: 23.74%

## Slide 24: Total Energy From Solar Generation
Notes: 980,459 MWh

## Slide 25: % Energy from Solar Generation
Notes: 2.77%

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia = 206,068 MW*s on 6/14/2020
Previous Minimum was 128,759 MW*s on 11/18/2018.
Data:
Mean: 232,728
Max: 272,282 on Jun 10th
Min: 206,068 on Jun14th

## Slide 28: Questions?
Thank you!