## Slide 1
Effects of Activating Low Shift Factor Constraints in SCED
Analysis of Stakeholder-Requested Constraints on 6/18/2018 and 8/15/2018
Alex Giarratano
Market Analysis & Validation
CMWG
July 13th, 2020

## Slide 2: Agenda
Overview of New Material
Methodology
Analysis of Constraint SWINWIN8: WINKS_FMR1
  Impact on System Lambda, Resource BPs, and Resource Node LMPs
  Impact on Congestion Rent
Analysis of Constraint SMSHNH28: 3740__A
  Impact on System Lambda, Resource BPs, and Resource Node LMPs
  Impact on Congestion Rent
Conclusions

## Slide 3: Overview of New Material
The following material is a follow-up to material presented at the February 3rd, 2020 (link) and May 11th, 2020 (link) CMWG meetings
Specifically, it is a detailed analysis to understand the potential impact of activating the constraints requested by a stakeholder, as described in the table below.
Date | Equipment | Contingency
June 18th, 2018 | WINKS_FMR1 | XWIN389
 |  | SCHYWIN8
 |  | XWIN289
 |  | SWINWIN8
August 15th, 2018 | 3740_A | SMSHNH28
 |  | SBNDKR28

## Slide 4: Overview of New Material (cont’d.)
RTCA solutions for these Operating Days were examined to see which contingencies and constraints showed up in TCM and would have been activated if the 2% shift factor threshold for activating constraints had not been in effect.
Certain contingencies were redundant so the constraint that occurred the first, was the most limiting, and lasted the longest was the one that was selected to be activated for this analysis.
The following constraints, each of which did not have Resource Shift Factors ≥ 2% (absolute value), were chosen and activated for this analysis:
  June 18th, 2018
    SWINWIN8: WINKS_FMR1
      Would have been activated for SCED intervals between 9:45 and 16:35
  August 15th, 2018
    SMSHNH28: 3740__A
      Would have been activated for SCED intervals between 16:15 and 19:45
  Both of these constraints were radial

## Slide 5: Methodology
Analysis performed using an ERCOT internal SCED simulation tool, intended to rerun production SCED cases sequentially
  Assumes that Resources follow their Base Points exactly
For each analysis, a baseline was created by simply rerunning the sequential SCED cases
The new constraints, their limits, and their respective Resource Shift Factor matrices were added to the original SCED constraints
SCED results from the baseline case and the modified (w/ additional constraint) case were compared including System Lambda, LMPs, and Base Points

## Slide 6: Constraint SWINWIN8: WINKS_FMR1 on 6/18/2018

## Slide 7: SWINWIN8: WINKS_FMR1 Constraint
SWINWIN8 contingency, the loss of 138kV circuit between Wink Sub and Wink Tap, overloads the two transformers in Wink Sub.
Wink Sub in the Far West region.

## Slide 8: Activation of SWINWIN8: WINKS_FMR1 Constraint

## Slide 9: SWINWIN8: WINKS_FMR1 Impact on System Lambda

## Slide 10: SWINWIN8: WINKS_FMR1 Impact on Resource Base Points
SWINWIN8: WINKS_FMR1, a radial constraint (as evidenced by the uniform SF matrices), had no impact on the dispatch of Resources.

## Slide 11: SWINWIN8: WINKS_FMR1 Impact on Resource Node Locational Marginal Prices
SWINWIN8: WINKS_FMR1, a radial constraint (as evidenced by the uniform SF matrices), had no impact on LMPs around the system

## Slide 12: SWINWIN8: WINKS_FMR1 Impact on West Zone Price

## Slide 13: Impact on Congestion Rent on June 18th, 2018
On June 18th, 2018, there were a total of 13 constraints activated, 10 of which actually became binding
The addition of SWINWIN8: WINKS_FMR1 would increase the daily accrued congestion rent by $1M, or ~33%
Existing Congestion Rent: $2,957,573
Estimated Congestion Rent from SWINWIN8: WINKS_FMR1: $979,440

## Slide 14: Constraint SMSHNH28: 3740__A on 8/15/2018

## Slide 15: SMSHNH28: 3740__A Constraint
SMSHNH28 contingency and overload in the North Dallas region.
SMSHNH28 contingency, the loss of 138kV circuit between Northaven Switch and Morrison Lane Switch, overloads the 138kV circuit between Marsh Lane and Morrison Lane

## Slide 16: Activation of SMSHNH28: 3740__A Constraint

## Slide 17: SMSHNH28: 3740__A Impact on System Lambda

## Slide 18: SMSHNH28: 3740__A Impact on Resource Base Points
SMSHNH28: 3740__A, a radial constraint (as evidenced by the uniform SF matrices), had no impact on the dispatch of Resources.

## Slide 19: SMSHNH28: 3740__A Impact on Resource Node Locational Marginal Prices
SMSHNH28: 3740__A, a radial constraint (as evidenced by the uniform SF matrices), had no impact on LMPs around the system

## Slide 20: SMSHNH28: 3740__A Impact on North Load Zone Price

## Slide 21: Impact on Congestion Rent on August 15th, 2018
On August 15th, 2018, there were a total of 14 constraints activated, 11 of which actually became binding
The addition of SMSHNH28: 3740__A would increase the daily accrued congestion rent by $1.9M, or ~282%
Existing Congestion Rent: $676,506
Estimated Congestion Rent from SMSHNH28: 3740__A: $1,905,730

## Slide 22: Conclusions
No changes in Base Points or Resource LMPs were observed in these cases because the constraints were radial. No oscillations in Base Points were observed.
The impact of constraints being activated is dependent on the topology of the system (e.g., radial vs. non-radial, outages) near the constraint. The examples shown here may not be representative of all cases.

## Slide 23: Questions?
Thank you!