| NOGRR Number | 195 | NOGRR Title | Generator Voltage Control Tolerance Band |
| --- | --- | --- | --- |
| Date of Decision |  | July 29, 2020 |  |
| Action |  | Recommended Approval |  |
| Timeline |  | Normal |  |
| Proposed Effective Date |  | Upon system implementation |  |
| Priority and Rank Assigned |  | Priority – 2020; Rank – 300 |  |
| Nodal Operating Guide Sections Requiring Revision |  | 2.2.10, Generation Resource Response Time Requirements 2.7.3.1, Operational Guidelines 2.7.3.3, TO/TSP Responsibilities 2.7.3.4, QSE Responsibilities 2.7.3.5, Resource Entity Responsibilities and Generation Resource Requirements |  |
| Related Documents Requiring Revision/Related Revision Requests |  | None |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) addresses ERCOT audit recommendations from Texas Reliability Entity, Inc. (Texas RE) and proposes to modify generator voltage control tolerance bands. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | ERCOT submits this NOGRR in order to address four items in Section 2, System Operations and Control Requirements. First, in response to a Texas RE audit recommendation, ERCOT proposes to clarify the conditions of notification for deviations from a Voltage Set Point so that they are clear and measurable. Current language simply includes “as soon as practicable.” ERCOT proposes to modify paragraphs (2) and (3) of Section 2.2.10 and paragraphs (3) and (4) of Section 2.7.3.5 to include a maximum time frame of 10 minutes from receipt of the applicable instruction or deviation from the tolerance band identified in paragraph (4) of Section 2.7.3.5. The proposed revisions would provide clear and measurable requirements in connection with North American Electric Reliability Corporation (NERC) Reliability Standard VAR-002-4.1, Generator Operation for Maintaining Network Voltage Schedules, Requirement R2, that action should be taken as soon as practicable, but not longer than ten minutes from the triggering event. Second, ERCOT proposes edits to paragraph (1)(a) of Section 2.7.3.1 in order to add general operational voltage limits for existing and future voltage levels. Third, ERCOT proposes to clarify and standardize the generator voltage control tolerance which, in its current form of 2%, varies depending on what the actual Voltage Set Point is at any given time. Currently, this tolerance is a +/-2% threshold for all kV levels, which can equate up to more than a 14kV spread for 345kV connected generators. That spread is excessive at 138kV and 345kV levels, and does not support reliable voltage control. The tolerance threshold moves depending on what the Voltage Set Point is at the Point of Interconnection (POI), and it can be confusing to track if a Voltage Set Point instruction is given. This NOGRR introduces a fixed threshold in terms of kV and is grouped by base voltage level, which is more easily tracked and measured by System Operators. The tolerances will improve voltage control, especially with higher nominal kV POIs. With the addition of Nodal Protocol Revision Request (NPRR) 776, Voltage Set Point Communication, telemetered Voltage Set Points and POI voltages allow for a common reference point that mitigates historical target and voltage reference discrepancies. Currently, the tolerance bands allow for generators to drift far from their desired Voltage Set Point, which makes it difficult to maintain the reliability on the system. Fourth, ERCOT proposes to require Automatic Voltage Regulator (AVR) settings be set so that full reactive capability is deployed prior to going beyond the tolerance bands. This revision will help ensure that settings such as deadband and droop settings are coordinated, along with plant controllers, to automatically regulate voltage within the tolerance band. Some generators have been found to incorrectly set the deadband to 2%, or the droop settings well close to the 2%, which leads to wide voltage fluctuations before the AVR begins to modify voltage to help control closer to the Voltage Set Point. ERCOT expects the deadband to be much smaller than the tolerance band and droop setting set within the tolerance band. ERCOT recognizes that some AVR settings must be coordinated with other generators’ AVR settings behind the same POI or that are electrically close so that AVR controllers will not be fighting against each other, but instead working together to provide reliable voltage control. |  |
| ROS Decision |  | On 9/5/19, ROS unanimously voted to table NOGRR195 for one month. All Market Segments were present for the vote. On 10/3/19, ROS unanimously voted to table NOGRR195 and refer the issue to the Voltage Profile Working Group (VPWG) and Operations Working Group (OWG). All Market Segments were present for the vote. On 6/4/20, ROS voted via roll call to recommend approval of NOGRR195 as amended by the 6/2/20 LCRA comments. There was one opposing vote from the Independent Generator (Southern Power) Market Segment and six abstentions from the Consumer (2) (OPUC, Sierra Club), Independent Generator (1) (Luminant), and Independent Power Marketer (IPM) (3) (EDF Trading North America, Shell Energy, Morgan Stanley) Market Segments. All Market Segments were present for the vote. On 7/9/20, ROS unanimously voted via roll call to endorse and forward to TAC the 6/4/20 ROS Report as amended by the 7/8/20 ERCOT comments and the Impact Analysis for NOGRR195 with a priority of 2020 and rank of 300. All Market Segments were present for the vote. |  |
| Summary of ROS Discussion |  | On 9/5/19, participants discussed specifics of the timeline for notification of and compliance with Voltage Set Point instructions in various scenarios. Some Market Participants requested additional information regarding potential reliability issues or other concerns that prompted the changes proposed in NOGRR195. On 10/3/19, ERCOT staff summarized additional analysis requested by Market Participants. Market Participants expressed concern for proposed response timelines and switching the basis of the generator voltage control tolerance band to an explicit kV level instead of the current percentage. On 6/4/20, participants debated keeping NOGRR195 tabled for OWG review of the 6/2/20 LCRA comments. On 7/9/20, participants reviewed the 7/8/20 ERCOT comments. |  |
| TAC Decision |  | On 7/29/20, TAC unanimously voted via roll call to recommend approval of NOGRR195 as recommended by ROS in the 7/9/20 ROS Report. All Market Segments were present for the vote. |  |
| Summary of TAC Discussion |  | On 7/29/20, there was no discussion. |  |
| ERCOT Opinion |  | ERCOT supports approval of NOGRR195. |  |

| Sponsor |  |
| --- | --- |
| Name | Stephen Solis / Freddy Garcia |
| E-mail Address | Stephen.Solis@ercot.com / Freddy.Garcia@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-6772 / 512-585-6389 |
| Cell Number |  |
| Market Segment | Not Applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Jordan Troublefield |
| E-Mail Address | Jordan.Troublefield@ercot.com |
| Phone Number | 512-248-6521 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| ERCOT 030320 | Proposed lengthening multiple maximum notification times; the modification of voltage control tolerances; removed AVR settings language from Section 2.7.3.5; adding language to Section 2.7.3.3 regarding the importance of static reactive devices being used by Transmission Operators (TOs) prior to requesting a Voltage Set Point change |
| LCRA 060220 | Removed adjustments made by the 3/3/20 ERCOT comments to the time a Generation Resource has to respond to a Voltage Support Service (VSS) Dispatch Instruction |
| ERCOT 070820 | Applied and accommodated baseline changes |
| PRS 072120 | Endorsed the ROS recommended priority of 2020 and rank of 300 for NOGRR195 |

Market Rules Notes

Please note the baseline Nodal Operating Guide language in the following sections has been updated to reflect the incorporation of the following NOGRR(s) into the Nodal Operating Guide:

- NOGRR204, Related to NPRR989, BESTF-1 Energy Storage Resource Technical Requirements (incorporated 7/1/20)

  - Section 2.2.10

  - Section 2.7.3.3

  - Section 2.7.3.4

  - Section 2.7.3.5

Please note that the following NOGRR(s) also propose revisions to the following section(s):

- NOGRR210, Related to NPRR1005, Clarify Definition of Point of Interconnection (POI) and Add Definition Point of Interconnection Bus (POIB)

  - Section 2.2.10

  - Section 2.7.3.3

  - Section 2.7.3.4

- NOGRR212, Related to NPRR1016, Clarify Requirements for Distribution Generation Resources (DGRs) and Distribution Energy Storage Resources (DESRs)

  - Section 2.2.10

  - Section 2.7.3.3

Revised Proposed Guide Language Revision

2.2.10		Generation Resource Response Time Requirements

(1) 	All Generation Resources providing Voltage Support Service (VSS) as described in Protocol Section 3.15, Voltage Support, shall maintain the necessary procedures and processes plus communications, telemetry, remote control, automation, and staffing in order to normally comply with the response times listed below when a VSS Dispatch Instruction or a TO Voltage Set Point instruction, as described in Protocol Section 6.5.7.7, Voltage Support Service, is given. Compliance is based upon normal operating conditions where VSS Dispatch Instructions respect all equipment operating limits and other restrictions that are periodically placed on equipment. The response time to a VSS Dispatch Instruction or a TO Voltage Set Point instruction shall commence with the successful receipt by the QSE or Generation Resource either through a verbal or telemetered instruction.

(2) 	A Resource Entity, TO, or QSE is not required to comply with a VSS Dispatch Instruction or Voltage Set Point instruction if compliance with such an instruction is impossible due to either a Force Majeure Event or one or more of the conditions described in paragraphs (1) and (2) of Protocol Section 6.5.7.9, Compliance with Dispatch Instruction. In the event compliance with an instruction is precluded under this paragraph:

(a) 	An affected Resource Entity shall, as soon as practicable, notify its QSE, and the Resource Entity or its QSE shall, as soon as practicable, but not longer than 15 minutes from receipt of the instruction by the Resource Entity, notify the Entity issuing the instruction; and

(b)	An affected TO shall, as soon as practicable, but not longer than 15 minutes from notification from the Resource Entity or its QSE, notify ERCOT.

(3) 	The required VSS response times for Generation Resources are:

(a) 	For automatically switchable static Volt-Ampere reactive (VAr) capable devices, when voltage or reactive measurements at the POI are outside of the Voltage Set Point tolerance band identified in paragraph (4) of Section 2.7.3.5, Resource Entity Responsibilities and Generation Resource Requirements; then the response must be fully deployed in no more than five minutes. If a TO and a Resource Entity have determined that a longer response time is appropriate and have entered into a written agreement reflecting that response time, then the Generation Resource shall be required to comply with that agreed response time so long as it does not exceed ten minutes.

(b) 	Response to a TO Voltage Set Point instruction shall be completed in no more than five minutes from receipt of the instruction.

(c) 	Response to a VSS Dispatch Instruction that requires a change to the real power output of the Generation Resource shall be completed as soon as practicable.

(4) 	Shutting down and disconnecting Generation Resources from the ERCOT Transmission Grid:

(a) 	On-Line Generation Resources must be able to commence their shutdown sequence within five minutes of receipt of a Dispatch Instruction from ERCOT. Nuclear-fueled Generation Resources shall comply with the procedural requirements of the Nuclear Regulatory Commission (NRC) when receiving Dispatch Instructions from ERCOT to disconnect the Generation Resource from the ERCOT Transmission Grid.

(b) 	If the ERCOT Transmission Grid condition requires breaker or switch operations to disconnect a non-MW producing generator from the system, such operations shall be completed as soon as practicable, but no longer than 15 minutes of the receipt of a Dispatch Instruction from ERCOT. Once disconnected from the ERCOT Transmission Grid, a Generation Resource shall complete as soon as practicable, but no longer than 15 minutes, the required switching to return the system to a normal configuration except for nuclear-fueled Generation Resources, which shall comply with the procedural requirements of the NRC when receiving Dispatch Instructions from ERCOT to disconnect the Generation Resource from the ERCOT Transmission Grid.

[NOGRR204: Replace Section 2.2.10 above with the following upon system implementation of NPRR989:] - 2.2.10 Generation Resource and Energy Storage Resource Response Time Requirements (1) All Generation Resources and ESRs providing Voltage Support Service (VSS) as described in Protocol Section 3.15, Voltage Support, shall maintain the necessary procedures and processes plus communications, telemetry, remote control, automation, and staffing in order to normally comply with the response times listed below when a VSS Dispatch Instruction or a TO Voltage Set Point instruction, as described in Protocol Section 6.5.7.7, Voltage Support Service, is given. Compliance is based upon normal operating conditions where VSS Dispatch Instructions respect all equipment operating limits and other restrictions that are periodically placed on equipment. The response time to a VSS Dispatch Instruction or a TO Voltage Set Point instruction shall commence with the successful receipt by the QSE, Generation Resource, or ESR either through a verbal or telemetered instruction. (2) A Resource Entity, TO, or QSE is not required to comply with a VSS Dispatch Instruction or Voltage Set Point instruction if compliance with such an instruction is impossible due to either a Force Majeure Event or one or more of the conditions described in paragraphs (1) and (2) of Protocol Section 6.5.7.9, Compliance with Dispatch Instruction. In the event compliance with an instruction is precluded under this paragraph: (a) An affected Resource Entity shall, as soon as practicable, but not longer than 15 minutes from receipt of the instruction by the Resource Entity, notify its QSE, and the Resource Entity or its QSE shall, as soon as practicable, notify the Entity issuing the instruction; and (b) An affected TO shall, as soon as practicable, but not longer than 15 minutes from notification from the Resource Entity or its QSE, notify ERCOT. (3) The required VSS response times for Generation Resources and ESRs are: (a) For automatically switchable static Volt-Ampere reactive (VAr) capable devices, when voltage or reactive measurements at the POI are outside of the Voltage Set Point tolerance band identified in paragraph (4) of Section 2.7.3.5, Resource Entity Responsibilities and Generation Resource or ESR Requirements; then the response must be fully deployed in no more than five minutes. If a TO and a Resource Entity have determined that a longer response time is appropriate and have entered into a written agreement reflecting that response time, then the Generation Resource or ESR shall be required to comply with that agreed response time so long as it does not exceed ten minutes. (b) Response to a TO Voltage Set Point instruction shall be completed in no more than five minutes from receipt of the instruction. (c) Response to a VSS Dispatch Instruction that requires a change to the real power output of the Generation Resource or ESR shall be completed as soon as practicable. (4) Shutting down and disconnecting Generation Resources or ESRs from the ERCOT Transmission Grid: (a) On-Line Generation Resources or ESRs must be able to commence their shutdown sequence within five minutes of receipt of a Dispatch Instruction from ERCOT. Nuclear-fueled Generation Resources shall comply with the procedural requirements of the Nuclear Regulatory Commission (NRC) when receiving Dispatch Instructions from ERCOT to disconnect the Generation Resource from the ERCOT Transmission Grid. (b) If the ERCOT Transmission Grid condition requires breaker or switch operations to disconnect a non-MW producing Generation Resource or ESR from the system, such operations shall be completed as soon as practicable, but no longer than 15 minutes of the receipt of a Dispatch Instruction from ERCOT. Once disconnected from the ERCOT Transmission Grid, a Generation Resource or ESR shall complete as soon as practicable, but no longer than 15 minutes, the required switching to return the system to a normal configuration except for nuclear-fueled Generation Resources, which shall comply with the procedural requirements of the NRC when receiving Dispatch Instructions from ERCOT to disconnect the Generation Resource from the ERCOT Transmission Grid.

2.7.3.1		Operational Guidelines

(1)	The following guidelines describe ideal system operational characteristics and do not establish requirements for any particular Entity:

(a)	General operational voltage limits are:

| Nominal Voltage | Normal Operating Limits | Emergency Operating Limits |
| --- | --- | --- |
| 345 | 327.75 – 362.25 | 310.5 – 379.5 |
| 230 | 218.5 – 241.5 | 207 – 253 |
| 138 | 131.1 – 144.9 | 124.2 – 151.8 |
| 115 | 109.25 – 120.75 | 103.5 – 126.5 |
| 69 | 65.55 – 72.45 | 62.1 – 75.9 |

(b)	Except for Transmission Facilities that are designed to operate outside of normal operating limits, transmission voltage should not exceed 105% nor fall below 95% of the nominal voltage during normal operation of the system.

(c)	Transmission voltage during emergencies (including contingency events) should not exceed equipment over-excitation ratings.

(d)	Transmission voltage during emergencies (including contingency events) should not result in customer voltage exceeding or falling below prescribed limits at distribution substations on the transmission system.

(e)	Transmission voltage post contingency should not exceed 110% nor fall below 90% of the per-unit voltage, unless more restrictive limits have been specified by the TSP for their system, then those limits shall not be exceeded.

(f)	Transmission voltage post contingency should not fall below any Under-Voltage Load Shedding (UVLS) set point during normal operations.

(g)	The accuracy of any transmission voltage that appears to exceed normal or emergency limits should be verified prior to taking further actions.

(h)	Major transmission lines should be kept in service during light Load as much as possible.  Lines should only be removed after all applicable reactive controls are implemented and the practicality of additional generation Dispatch has been considered.  Time permitting, studies should be conducted to verify that reliability will not be degraded by removing any major transmission line from service.

(i)	Generally speaking, static reactive devices should be brought On-Line before predicted daily maximum Load or before dynamic reactive Resources reach operating limits.  Static reactive devices will be taken Off-Line during daily Load decline and before dynamic reactive Resources reach operating limits.

2.7.3.3	TO/TSP Responsibilities

(1)	Each TO shall be responsible for directing Voltage Set Points for each Generation Resource interconnected to its TSP’s Facilities.  Each TO will adjust the Voltage Set Point by communicating directly with the Resource Entity or QSE responsible for the operation of the Generation Resource.  Normal communication is to request voltage or Reactive Power be raised or lowered at a specified bus by a stated number of kV or MVAr (e.g., + 1 kV, +20 MVAr, or -1 kV, -20 MVAr).

(2)	Each TO shall monitor system voltages and shall operate voltage control equipment, including, but not limited to, static Reactive Power resources such as capacitors, reactors and transformer tap changers to maintain system voltages within limits.

(3)	Each TO shall operate static Reactive Power resources within its operating area as required by its criteria while maintaining dynamic reactive reserves, both leading and lagging, provided by Generation Resources.  Except as reasonably necessary to ensure reliability or operational efficiency, TOs should utilize available static reactive devices prior to requesting a Voltage Set Point change from a Generation Resource.

(4)	Each TO shall telemeter to ERCOT via ICCP the Real-Time desired Voltage Set Point and actual voltage at the POI for each Generation Resource interconnected to its system.  Each TO shall modify the telemetered Voltage Set Point as soon as practicable in order to match any verbal Voltage Set Point instruction issued.

(5)	Each TO shall know the status of static transmission Reactive Power resources in its operating area and shall provide such information to ERCOT.

(6)	When voltage levels deviate from established limits, the affected TO shall take immediate steps to relieve the condition using available reactive resources under its control.

(7)	Each TSP shall, as soon as practicable, notify ERCOT of any temporary transmission voltage limit changes and shall coordinate with ERCOT to update the Network Operations Model with any permanent or long-term changes to voltage limits that deviate from those identified in Section 2.7.3.1, Operational Guidelines.

[NOGRR177 and NOGRR204: Replace applicable portions Section 2.7.3.3 above with the following upon system implementation of NPRR857 or NPRR989, respectively:] - 2.7.3.3 TO/TSP/DCTO Responsibilities (1) Each TO shall be responsible for directing Voltage Set Points for each Generation Resource and ESR interconnected to its TSP’s Facilities. Each TO will adjust the Voltage Set Point by communicating directly with the Resource Entity or QSE responsible for the operation of the Generation Resource or ESR. Normal communication is to request voltage or Reactive Power be raised or lowered at a specified bus by a stated number of kV or MVAr (e.g., + 1 kV, +20 MVAr, or -1 kV, -20 MVAr). (2) Each TO shall monitor system voltages and shall operate voltage control equipment, including, but not limited to, static Reactive Power resources such as capacitors, reactors and transformer tap changers to maintain system voltages within limits. (3) Each TO shall operate static Reactive Power resources within its operating area as required by its criteria while maintaining dynamic reactive reserves, both leading and lagging provided by Generation Resources and ESRs. Except as reasonably necessary to ensure reliability or operational efficiency, TOs should utilize available static reactive devices prior to requesting a Voltage Set Point change from a Generation Resource or ESR. (4) Each TO shall telemeter to ERCOT via ICCP the Real-Time desired Voltage Set Point and actual voltage at the POI for each Generation Resource and ESR interconnected to its system. Each TO shall modify the telemetered Voltage Set Point as soon as practicable in order to match any verbal Voltage Set Point instruction issued. (5) Each TO shall know the status of static transmission Reactive Power resources in its operating area and shall provide such information to ERCOT. (6) When voltage levels deviate from established limits, the affected TO shall take immediate steps to relieve the condition using available reactive resources under its control. (7) Each TSP and DCTO shall, as soon as practicable, notify ERCOT of any temporary transmission voltage limit changes and shall coordinate with ERCOT to update the Network Operations Model with any permanent or long-term changes to voltage limits that deviate from those identified in Section 2.7.3.1, Operational Guidelines.

2.7.3.4	QSE Responsibilities

(1)	Each QSE shall ensure that any Generation Resource that it represents and that is required to provide VSS responds to any VSS Dispatch Instruction including VSS Dispatch Instruction to exceed its CURL or URL or TO Voltage Set Point instruction within the time requirements specified in paragraph (3)(b) of Section 2.2.10, Generation Resource Response Time Requirements, even if the new Voltage Set Point is within the tolerance band identified in paragraph (4) of Section 2.7.3.5, Resource Entity Responsibilities and Generation Resource Requirements.  If the Resource Entity notifies the QSE that a Generation Resource cannot comply with the VSS Dispatch Instruction or TO Voltage Set Point instruction, either the Resource Entity or its QSE shall, as soon as practicable, notify the Entity that issued the instruction.  The Resource Entity or its QSE shall provide the reason for not being able to comply and an estimated time for resolution, when known.

(2)	Each QSE representing a Generation Resource shall provide in Real-Time the desired Voltage Set Point and the associated POI kV measurement to the Generation Resource.

(3)	Each QSE will continuously monitor the status of its Generating Resources’ AVRs and PSSs.

(4)	Each QSE must, as soon as practicable, notify ERCOT when a Generation Resource experiences a change that affects its reactive capability, including any change to the operation mode of the Generation Resource’s AVR.

[NOGRR204: Replace Section 2.7.3.4 above with the following upon system implementation of NPRR989:] - 2.7.3.4 QSE Responsibilities (1) Each QSE shall ensure that any Generation Resource or ESR that it represents and that is required to provide VSS responds to any VSS Dispatch Instruction including VSS Dispatch Instruction to exceed its CURL or URL or TO Voltage Set Point instruction within the time requirements specified in paragraph (3)(b) of Section 2.2.10, Generation Resource and Energy Storage Resource Response Time Requirements even if the new Voltage Set Point is within the tolerance band identified in paragraph (4) of Section 2.7.3.5, Resource Entity Responsibilities and Generation Resource and Energy Storage Resource Requirements. If the Resource Entity notifies the QSE that a Generation Resource or an ESR cannot comply with the VSS Dispatch Instruction or TO Voltage Set Point instruction, either the Resource Entity or its QSE shall, as soon as practicable, notify the Entity that issued the instruction. The Resource Entity or its QSE shall provide the reason for not being able to comply and an estimated time for resolution, when known. (2) Each QSE representing a Generation Resource or ESR shall provide in Real-Time the desired Voltage Set Point and the associated POI kV measurement to the Generation Resource or ESR. (3) Each QSE will continuously monitor the status of its Resources’ AVRs and PSSs. (4) Each QSE must, as soon as practicable, notify ERCOT when a Generation Resource or ESR experiences a change that affects its reactive capability, including any change to the operation mode of the Generation Resource’s or ESR’s AVR.

2.7.3.5	Resource Entity Responsibilities and Generation Resource Requirements

(1)	Each Resource Entity shall ensure that its Generation Resource(s) responds to all VSS Dispatch Instruction or a TO Voltage Set Point instruction from its QSE or interconnecting TO within the time requirements specified in paragraph (3)(b) of Section 2.2.10, Generation Resource Response Time Requirements, even if the new Voltage Set Point is within the tolerance band identified in paragraph (4) below.

(2)	Generation Resources with high reactive loading resulting from abnormal conditions shall not reduce their reactive loading without the consent of ERCOT unless equipment damage is imminent based on the sole and reasonable judgment of the Resource Entity. In that case the Resource Entity will notify its QSE and its TO as soon as practicable of its action.

(3)	Each Resource Entity shall monitor Real-Time provided Voltage Set Point instructions it receives.  The Resource Entity shall inform its QSE and either the Resource Entity or its QSE shall notify the Resource Entity’s TO, as soon as practicable, but not longer than 15 minutes from receipt of the instruction by the Resource Entity, if it cannot comply with TO Voltage Set Point instructions, or not longer than 31 minutes from being outside of the tolerance band if it cannot maintain the POI voltage within the tolerance band identified in paragraph (4) below.  If a Resource Entity cannot comply with a VSS Dispatch Instruction, the Resource Entity shall inform its QSE and its QSE shall notify ERCOT as soon as practicable but not longer than 10 minutes from the receipt of the instruction by the Resource Entity.

(4)	A Resource Entity required to provide VSS shall maintain the generator voltage or Reactive Power schedule to maintain voltage at the POI to be within a tolerance band of the Voltage Set Point while operating at less than or equal to the maximum reactive capability of the Generation Resource.  A Generation Resource’s POI voltage may be out of the tolerance band if it has exhausted all of its reactive capability.  The tolerance bands are as follows:

| Nominal Voltage | Tolerance Band KV |
| --- | --- |
| 345 | +/- 4kV |
| 230 | +/- 3kV |
| 138 | +/- 2kV |
| 115 | +/- 2kV |
| 69 | +/- 1kV |

(5)	Required reactive capability must be maintained at all times that the Generation Resource is On-Line.  When a Generation Resource experiences a change that affects its reactive capability, the associated Resource Entity shall notify its QSE and TO as soon as practicable but not longer than 30 minutes from becoming aware of the change in reactive capability.

(6)	Each Resource Entity shall communicate any generator-owned transmission voltage limits that deviate from those identified in Section 2.7.3.1, Operational Guidelines, to ERCOT and to its QSE.

- Resource Entity Responsibilities and Generation Resource and Energy Storage Resource Requirements Each Resource Entity shall ensure that its Generation Resource(s) and ESR(s) responds to all VSS Dispatch Instruction or a TO Voltage Set Point instruction from its QSE or interconnecting TO within the time requirements specified in paragraph (3)(b) of Section 2.2.10, Generation Resource and Energy Storage Resource Response Time Requirements, even if the new Voltage Set Point is within the tolerance band identified in paragraph (4) below. Generation Resources or ESRs with high reactive loading resulting from abnormal conditions shall not reduce their reactive loading without the consent of ERCOT unless equipment damage is imminent based on the sole and reasonable judgment of the Resource Entity. In that case the Resource Entity will notify its QSE and its TO as soon as practicable of its action. Each Resource Entity shall monitor Real-Time provided Voltage Set Point instructions it receives. The Resource Entity shall inform its QSE and either the Resource Entity or its QSE shall notify the Resource Entity’s TO, as soon as practicable, but not longer than 15 minutes from receipt of the instruction by the Resource Entity, if it cannot comply with TO Voltage Set Point instructions, or not longer than 30 minutes from being outside of the tolerance band if it cannot maintain the POI voltage within the tolerance band identified in paragraph (4) below. If a Resource Entity cannot comply with a VSS Dispatch Instruction, the Resource Entity shall inform its QSE and its QSE shall notify ERCOT as soon as practicable but not longer than 15 minutes from the receipt of the instruction by the Resource Entity. A Resource Entity required to provide VSS shall maintain the Resource’s voltage or Reactive Power schedule to maintain voltage at the POI to be within a tolerance band of the Voltage Set Point while operating at less than or equal to the maximum reactive capability of the Generation Resource or ESR. A Generation Resource’s or ESR’s POI voltage may be out of the tolerance band if it has exhausted all of its reactive capability. The tolerance bands are as follows: Required reactive capability must be maintained at all times that the Generation Resource or ESR is On-Line. When a Generation Resource or ESR experiences a change that affects its reactive capability, the associated Resource Entity shall notify its QSE and TO, as soon as practicable. Each Resource Entity shall communicate any Resource Entity-owned transmission voltage limits that deviate from those identified in Section 2.7.3.1, Operational Guidelines, to ERCOT and to its QSE.

[NOGRR204: Replace Section 2.7.3.5 above with the following upon system implementation of NPRR989:] - 2.7.3.5 Resource Entity Responsibilities and Generation Resource and Energy Storage Resource Requirements (1) Each Resource Entity shall ensure that its Generation Resource(s) and ESR(s) responds to all VSS Dispatch Instruction or a TO Voltage Set Point instruction from its QSE or interconnecting TO within the time requirements specified in paragraph (3)(b) of Section 2.2.10, Generation Resource and Energy Storage Resource Response Time Requirements, even if the new Voltage Set Point is within the tolerance band identified in paragraph (4) below. (2) Generation Resources or ESRs with high reactive loading resulting from abnormal conditions shall not reduce their reactive loading without the consent of ERCOT unless equipment damage is imminent based on the sole and reasonable judgment of the Resource Entity. In that case the Resource Entity will notify its QSE and its TO as soon as practicable of its action. (3) Each Resource Entity shall monitor Real-Time provided Voltage Set Point instructions it receives. The Resource Entity shall inform its QSE and either the Resource Entity or its QSE shall notify the Resource Entity’s TO, as soon as practicable, but not longer than 15 minutes from receipt of the instruction by the Resource Entity, if it cannot comply with TO Voltage Set Point instructions, or not longer than 30 minutes from being outside of the tolerance band if it cannot maintain the POI voltage within the tolerance band identified in paragraph (4) below. If a Resource Entity cannot comply with a VSS Dispatch Instruction, the Resource Entity shall inform its QSE and its QSE shall notify ERCOT as soon as practicable but not longer than 15 minutes from the receipt of the instruction by the Resource Entity. (4) A Resource Entity required to provide VSS shall maintain the Resource’s voltage or Reactive Power schedule to maintain voltage at the POI to be within a tolerance band of the Voltage Set Point while operating at less than or equal to the maximum reactive capability of the Generation Resource or ESR. A Generation Resource’s or ESR’s POI voltage may be out of the tolerance band if it has exhausted all of its reactive capability. The tolerance bands are as follows: Nominal Voltage; Tolerance Band KV. 345; +/- 4kV. 230; +/- 3kV. 138; +/- 2kV. 115; +/- 2kV. 69; +/- 1kV. (5) Required reactive capability must be maintained at all times that the Generation Resource or ESR is On-Line. When a Generation Resource or ESR experiences a change that affects its reactive capability, the associated Resource Entity shall notify its QSE and TO, as soon as practicable but not longer than 30 minutes from becoming aware of the change in reactive capability. (6) Each Resource Entity shall communicate any Resource Entity-owned transmission voltage limits that deviate from those identified in Section 2.7.3.1, Operational Guidelines, to ERCOT and to its QSE.