## Slide 1
PDCWG Report to ROS
Chair: Chad Mulholland, NRG
Vice Chair: Jimmy Jackson, CPS
ROS
August 6th, 2020

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
  BAL-001-TRE-2 FMEs & IMFR
    2 FMEs in the month of June
  Frequency Control Report

## Slide 3: Meeting Minutes
PDCWG Meeting 7/15/2020
  SAR 12 for BAL-001-TRE
  Draft SCR to add Solar Feedback Component to GTBD Calculation
  High Frequency Event Follow-up Discussion (Event from 3/16/20)
  ERCOT Reports and FME Discussion

## Slide 4: Frequency Measurable Events Performance

## Slide 5: Frequency Measurable Events
There were 2 FMEs in June
  6/13/2020 12:00:48
    Loss of 679 MW
    Interconnection Frequency Response: 1293 MW/0.1 Hz
    8 of 54 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    9 of 54 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.
  6/15/2020
    Loss of 511 MW
    Interconnection Frequency Response: 1087 MW/0.1 Hz
    15 of 54 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    11 of 54 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 6: Interconnection Minimum Frequency Response (IMFR) Performance
IMFR Performance currently 872.75 MW/0.1Hz
Frequency Response Obligation (FRO): 425 MW/0.1 Hz

## Slide 7: Frequency Control Report
May 2020

## Slide 8: CPS1 Performance

## Slide 9: RMS1 Performance of ERCOT Frequency

## Slide 10: Frequency Profile Analysis

## Slide 11: Time Error Corrections

## Slide 12: ERCOT Total Energy

## Slide 13: ERCOT Total Energy from Wind Generation

## Slide 14: ERCOT % Energy from Wind Generation

## Slide 15: ERCOT Total Energy from Solar Generation

## Slide 16: ERCOT % Energy from Solar Generation

## Slide 17
Questions?