## Slide 1
ERCOT Frequency Control Report
July 2020
ERCOT
Operations Planning
PDCWG | August 19th, 2020

## Slide 2: Summary of July 2020
CPS1: 168.35%
Current CPS1 12-Month Rolling Average: 173.03%
4 BAAL Exceedance
13 hourly CPS1 score below 100%
BAAL-003 Events have updated through 2019
2019 BAAL-003 FRM Performance: -811.14
2020 RMS1 Statistics
  Mean: 16.12 mHz
  Min: 12.25 mHz
  Max: 20.4 mHz
Energy Statistics
  Total Energy: 40,193,479 MWh
  Wind Energy: 6,904,465 MWh
  Percent Energy from Wind: 17.18%
  Solar Energy: 1,092,033 MWh
  Percent Energy from Solar: 2,72%
Minimum System Inertia
  Mean: 278, 431 MW*s
  Max: 299,461 MW*s on July 31st
  Min: 241,311 MW*s on July 1st
Notes: 2018 BAAL-003 FRM Performance: -843.17

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
Jul-20 CPS1 (%): 168.35
Notes: Outliers:
1. 20.27% @ 7/1/2020 18:00
  Frequency Event: at the start of the hour with about 801 MWs lost and nadir of 59.847Hz
  Expected Gen Dev:
  Large exp. Gen. dev of -1035 @ 18:33 mostly due to wind, Large expected gen dev of -2466 @ 18:53 mostly due
  To wind and solar
  Wind/Solar Ramp: Solar ramp from 2225 to 1358 MW between 18:32 and 19:00
  Regulation: Regulation up exhausted throughout the hour
2. 20.72% @ 7/22/2020 18:00
  Expected Gen Dev:
  Large exp. Gen. dev of -1642 @ 18:19 mostly due to wind and solar, Large expected gen dev of -2204 @ 18:45 mostly due to wind and solar
  Wind/Solar Ramp: Solar ramp from 2262 to 1356 MW between 18:28 and 18:45
  Regulation: Regulation up exhausted from 18:00-18:22 and 18:33-18:46
3. 37.13% @ 7/6/2020 15:00
  Frequency Event: @ 15:09, loss of about 762 MWs lost, and nadir of 59.808Hz
Expected Gen Dev:
  Large exp. Gen. dev of -1076 @ 15:15 mostly due to thermal resources being slow to reach BP after responding to low frequency event
  Wind/Solar Ramp: Solar ramp from 3327 to 2968 MW between 15:36 and 15:48
  Regulation: Regulation up exhausted from 15:10 – 15:16, Reg down exhausted from 15:22 to 16:00
4. 42.82% @ 7/21/2020 18:00
  Expected Gen Dev:
  Large exp. Gen. dev of -1059 @ 18:28 mostly due to wind and solar, Large Exp. Gen. Dev of -1836 @ 18:54 mostly due to wind and solar with some thermal contributions
  Wind/Solar Ramp: Solar ramp from 1869 to 1460 MW between 18:12 and 18:27, Wind ramp from 9043 to 7766 MW between 18:33 and 18:56 (PWRR capped out to -30MW/min)
  Regulation: Regulation up exhausted throughout the hour
5. 63.69% @ 7/20/2020 11:00
  Frequency Event: @ 11:47, loss of about 806 MWs lost, and nadir of 59.815Hz
Expected Gen Dev:
  Large exp. Gen. dev of -1381 @ 11:53 mostly due to thermal resources being slow to reach BP after responding to low frequency event
  Wind/Solar Ramp: Wind on down ramp from 3997 to 3082 MW between 11:14 and 11:53
  Regulation: Regulation up and down exhausted for short intervals throughout
6. 71.89% @ 7/4/2020 19:00
  Expected Gen Dev:
  Large exp. Gen. dev of -1601 @ 19:09 mostly due to thermal resources shutting down
  Wind/Solar Ramp: Solar on down ramp throughout hour from 2449 to 778 MW between 19:00 and 20:00
  Regulation: Regulation up exhausted throughout the hour
7. 77.24% @ 7/3/2020 18:00
  Expected Gen Dev:
  Large exp. Gen. dev of -1315 @ 18:54 mostly due to thermal resources shutting down (~800 MW in shutdown)
  Wind/Solar Ramp: Solar on down from 2878 to 2197 MW between 18:24 and 19:00
  Regulation: Regulation up exhausted throughout the hour
84.40% @ 7/9/2020 20:00
  Expected Gen Dev:
  Large exp. Gen. dev of -1003 @ 20:19 mostly due to thermal resources being slow to reach BP after responding to low frequency event
  Wind/Solar Ramp: Wind on down ramp from 17168 to 16684 MW between 20:09 and 20:22, solar down ramp from 730 to 220 MW between 20:00 and 20:23
  Regulation: Regulation up exhausted throughout the hour
89.37% @ 7/28/2020 17:00
  Expected Gen Dev:
  Large exp. Gen. dev of -1517@ 17:16 mostly due to wind and solar resources with some CCPs transitioning configurations
  Wind/Solar Ramp: Solar ramp down from 2745 to 2265 MW between 17:08 and 17:27, wind ramp up from 4673 to 5526 MW between 17:38 and 18:00
  Regulation: Regulation up exhausted throughout the first half of the hour, Reg down exhausted during second half of hour
10. 91.91% @ 7/6/2020 2:00
  Expected Gen Dev:
  Large exp. Gen. dev of -1823 @ 02:20 top contributions from thermal resources shutting down and from wind resources
  Wind/Solar Ramp: wind down ramp from 7659 to 5207 MW between 02:00 and 03:00
  Regulation: Regulation up exhausted throughout the hour
94.16% @ 7/1/2020 17:00
  Expected Gen Dev:
  Large exp. Gen. dev of -1863 @ 17:09 due to wind and solar resources
  Wind/Solar Ramp: solar ramp down of about 120MW between 17:00 and 17:05
  Regulation: Regulation up exhausted in the first half of hour, reg down in second half of hour
97.18% @ 7/12/2020 14:00
  Expected Gen Dev:
  Large exp. Gen. dev of -1381 @ 14:54 from thermal resources
  Wind/Solar Ramp: solar ramp down of about 100MW between 14:15 and 14:20, solar ramp down of about 130 MW between 14:46 and 14:51
  Regulation: Regulation up exhausted for short periods in the first half of hour, exhausted for entire second half of hour
13. 98.88% @ 7/5/2020 17:00
  Expected Gen Dev:
  Large exp. Gen. dev of -851 @ 17:39 from solar resources
  Wind/Solar Ramp: solar ramp down of about 200 MW between 17:33 and 17:35
  Regulation: Regulation up exhausted at the start and end of the hour, reg down exhausted in the middle of the hour

## Slide 5: BAAL Exceedances & Violations
There was 4 BAAL exceedances in July
Notes: 1 on 7/1 (loss of 801 MW), 2 on 7/6 (Loss of 762 MW), and 1 on 7/9 (Loss of 843 MW)

## Slide 6: 15-Minute Average CPS1%
Jul-20 CPS1 (%): 168.35

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 173.03%

## Slide 8: Daily RMS1 of ERCOT Frequency by Year

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2019 BAL-003 Selected Events – Update
Notes: BAL-003

## Slide 19: Op. Year 2018 BAL-003 FRM Performance - Update
Notes: OP2018: FRO = -381.0, FRM_median = -843.17, FRM_average = -959.7
OP2019: FRO = -381.0, FRM_median = -811.14, FRM_average = -892.5
OP2020: FRO = -425.0,

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 40,193,479 MWh

## Slide 22: Total Energy from Wind Generation
Notes: 6,904,465 MWh

## Slide 23: % Energy from Wind Generation
Notes: 17.18%

## Slide 24: Total Energy From Solar Generation
Notes: 1,092,033 MWh

## Slide 25: % Energy from Solar Generation
Notes: 2.72%

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia = 241,311 MW*s on 7/1/2020
Previous Minimum was 128,759 MW*s on 11/18/2018.
Data:
Mean: 278,431
Max: 299,461 on July 31st
Min: 241,311 on July 1st

## Slide 28: Questions?
Thank you!