## Slide 1
NOGRR 215
Transmission Issues Related to Generation Constraints Workshop
August 21, 2020

## Slide 2: Business Case
Significant increase in interest regarding RASs for new generators being developed in areas where interconnection studies for those new generators have demonstrated that the local transmission system cannot handle delivery of the capacity from the new and existing generation.
ERCOT is expecting many more requests of this type.

## Slide 3: RAS Timeline
Chart: RAS Proposals Post Nodal
| 39701 | 40151 | 40037 | 40513 | 40679 | 41464 | 41654 | 42522 | 42634 | 43074 | 43768 | 44014 | 43770 | 43875 | 43929 | 43935 | 43992 | 44029 | 42430 | 41086 | 40630
Milestones | 10 | 15 | 20 | 40 | 25 | 15 | 30 | 35 | 40 | 25 | 10 | 35 | 5 | 15 | 20 | 25 | 30 | 40 | 15 | 10 | 10
RAS 2
RAS 3
RAS 4
RAS 5

## Slide 4: RAS History
Nodal Go Live
Dec. 2010
Southwest Blackout Sept. 2011
Remedial Action Schemes | Approval Date | Recently Proposed Date | Retired
Monticello B | 6/1/2004 |  | 6/18/2018
Mount Enterprise | 6/6/2005 |  | 11/2/2012
Ennis West 138 kV | 7/25/2005 |  | 12/10/2013
Collin 345/138 kV Auto # 1 Series Reactor* | 2/27/2006 |  | 3/3/2015
Parkway-Schertz | 2/27/2006 |  | 8/5/2015
Liggett Switch Series Reactor* | 1/19/2007 |  | 9/15/2015
Whirlwind-Matador | 3/19/2008 |  | 6/1/2012
Elkton | 9/10/2008 |  | 3/15/2016
Stryker Creek | 9/10/2008 |  | 
Allen Switch 345/138 kV Auto # 1Series Reactor* | 10/28/2008 |  | 8/31/2016
China Grove Series Reactor* | 10/28/2008 |  | 7/6/2016
Golden Switch | 10/28/2008 |  | 11/16/2013
Monticello Mining | 10/28/2008 |  | 3/16/2016
Temple Switch 345/138 kV Auto # 1 Series Reactor* | 10/28/2008 |  | 9/21/2015
Benbrook 345/138 kV Autotransformer A Series Reactor* | 2/26/2009 |  | 8/6/2014
Benbrook 345/138 kV Autotransformers B Series Reactor* | 2/26/2009 |  | 8/6/2014
Eskota | 8/12/2009 |  | 
Horse Hollow Gen Tie | 12/2/2009 |  | 
Stanton East | 4/14/2010 |  | 11/9/2014
Mount Enterprise | 5/5/2010 |  | 11/2/2012
Allen Switch -- Ben Davis 345 kV Line Series Reactor* | 3/28/2011 |  | 1/9/2013
Barney Davis | 5/16/2011 |  | 
Permian Basin | 7/9/2013 |  | 6/6/2018
Morgan Creek | 1/15/2014 |  | 
Wirtz | 6/1/2016 |  | 
Mitchell Bend | 9/21/2016 |  | 
Culberson Loop | 10/30/2019 |  | 
Rocksprings |  | 11/1/2019 | 
RAS 1 |  | 2/14/2020 | 
RAS 2 |  | 4/8/2020 | 
RAS 3 |  | 4/14/2020 | 
RAS 4 |  | 6/10/2020 | 
Bearkat | 7/2/2020 |  | 
RAS 5 |  | 7/17/2020 | 
All SPS/RAS’s have been and are TSP owned
Transmission system is different than it was 10-20 years ago
Nodal Market provides for more efficient dispatch
LMP designed to provide price signal for Resource location
PRC-012-2 effective Jan 1, 2021
  *Would not currently qualify as a RAS

## Slide 5: Business Case
An increase in number of RASs may negatively impact system reliability and increase risk to ERCOT System.
  Increased risk on ability to recognize an Outage’s impact on RAS.
  Increasing difficulty with recognizing impact of combinations of Outages on multiple RAS.
  Increased risk associated with RAS-RAS interactions in RAS-concentrated areas.
  Needed generation not committed in MMS due to treatment of RASs and related contingencies.

## Slide 6: Business Case
  Increased compliance burden on RAS Entities and ERCOT.
  Other risks are described in the NOGRR Business Case section.
  Post-contingency, pre-RAS system conditions are meeting the criteria for potential cascading Outages (need RAS + GTC to ensure reliability, which is 2x risk compared to no RAS)
    Under normal conditions and during Outages
    RAS misoperation could lead to cascading Outages

## Slide 7: RAS Example
Gen B
Station 1
300 MW
200 MW
Station 2
Station 3
Station 4
Station 5
500 MW
166%
164%
Gen A
Line A
Line B
New Resource
Station 6
Line B rating = 300 MVA
RAS trips Gen B
RAS allows 166% N-1 line loading
Cascade Criteria = 125% of Emergency Rating
RAS misoperation could lead to instability

## Slide 8: RAS + GTC
Gen B
Station 1
300 MW
237 MW
200 MW
137 MW
Station 2
Station 3
Station 4
Station 5
500 MW
375 MW
125%
123%
Gen A
Line A
Line B
New Resource
Station 6
GTC needed to maintain <125% exceedance with RAS
GTC prevents possible collapse scenario
Without RAS, N-1 thermal constraint is most limiting with no threat of instability and easily managed by SCED.

## Slide 9: Language Overview
Reliability RAS
  Limit RASs to those needed to avoid actual or anticipated transmission security criteria in Operating Guide 2.2.2.
  RAS may not be used for constraints that can be resolved through market tools.

## Slide 10: Language Overview
Exit Strategy
  Exit Strategy no longer required as part of RAS proposal.
  Provide strategy if one has been identified, for example through planned transmission project.
ERCOT RAS review
  Align with current practice of reviewing new, modified, retirement RAS proposals.
  Issue Market Notice for proposals and approvals.
Retirement
  Retirement may be proposed by RAS Entity and evaluated through normal processes.
  ERCOT can determine a RAS is no longer needed through an ERCOT initiated review (ex: 5 yr. review) or through transmission planning process.

## Slide 11: Discussion
Questions?