## Slide 1
ERCOT 2020 UFLS Survey Results
ERCOT Compliance

## Slide 2: Background on the ERCOT UFLS Survey and Requirements
ERCOT coordinated and conducted the survey with ERCOT Transmission Operators (TOs.) The survey serves to ensure that the required automatic under-frequency load shed circuits are configured to provide the appropriate load relief in an under-frequency event. The table below, taken from the ERCOT Nodal Operating Guides, Section 2.6.1 (1) Requirements for Under-Frequency Load Shedding, lists the required load shed amounts:
Frequency Threshold | Load Relief
59.3 Hz | At least 5% of the TO Load
58.9 Hz | A total of at least 15% of the TO Load
58.5 Hz | A total of at least 25% of the TO Load
ERCOT Nodal Operating Guides, Section 2.6.1 (2)
  ERCOT will, prior to the peak each year, survey each TO’s compliance with the automatic Load shedding requirements described in paragraph (1) above, and report its findings to the Technical Advisory Committee (TAC). For purposes of determining a TO’s compliance with this annual survey requirement, TO Load will be the total amount of Load being served by the DSPs that the TO represents, as well as the TO’s transmission-level Customer Load, at the specified time of the survey.

## Slide 3: Timeline of the 2020 ERCOT UFLS Survey
Below is a timeline reflecting the survey dates and activities:
Date | Activity
March 19th | ERCOT announcement of survey timeline to the OWG.
April 1st | Market Notice sent by ERCOT Client Services to ERCOT TO Authorized Representatives.
May 14th @ 11:00 AM | Date and time of survey.
July 13th | Survey results due to ERCOT.
August – September | Results reported to OWG, ROS, and TAC

## Slide 4: Results of the 2020 ERCOT UFLS Survey
The overall results of the 2020 UFLS survey are reflected below:
TOs successfully met the UFLS requirements for all three thresholds.
The ERCOT load at the time of the survey was 44,052 MW. In comparison, the 2019 survey overall total result was 30.55% at 44,607 MW of load.
Frequency Threshold | Minimum Requirement | Survey Measurement
59.3 Hz | At least 5% of the TO Load | 7.39%
58.9 Hz | A total of at least 15% of the TO Load | 20.26%
58.5 Hz | A total of at least 25% of the TO Load | 32.80%