## Summary
Release Date: September 2, 2020
FINAL
Seasonal Assessment of Resource Adequacy for the ERCOT Region (SARA)
Fall 2020
SUMMARY
The Electric Reliability Council of Texas (ERCOT) anticipates there will be sufficient installed generating capacity available to serve system-wide forecasted peak demand this fall (October-November 2020).
“We study a range of normal to extreme scenarios prior to each season to determine whether there are any operational risks associated with meeting the forecasted peak demand,” said Manager of Resource Adequacy Pete Warnken. “At this time, our assessments show there will be adequate generation for fall.”
The peak demand forecast was developed using revised Moody’s economic data obtained in April 2020. The final fall SARA includes a 60,966 MW peak demand forecast, which is unchanged from the preliminary fall forecast and is based on normal weather conditions during fall peak demand periods, from 2004 through 2018.
ERCOT anticipates there will be more than 86,000 MW of resource capacity available at the start of the fall season, including 1,475 MW of planned wind and solar capacity that is expected to be available during fall peak demand periods.
This fall SARA includes a unit outage forecast of 14,267 MW, which is based on the historical average of outages for weekday peak hours for each of the last three fall seasons (2017-2019).

## Scenarios
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Fall 2020 - Final
Release Date: September 2, 2020
Forecasted Capacity and Demand
|  | Operational Resources (thermal and hydro), MW | 65850.2895 | Based on current Seasonal Maximum Sustainable Limits reported through the unit registration process
|  | Switchable Capacity Total, MW | 3639 | Installed capacity of units that can interconnect with other Regions and are available to ERCOT
|  | Less Switchable Capacity Unavailable to ERCOT, MW | -558 | Based on survey responses of Switchable Resource owners
|  | Available Mothballed Capacity, MW | 0 | Based on seasonal Mothball units plus Probability of Return responses of Mothball Resource owners
|  | Capacity from Private Use Networks, MW | 2772.3273 | Average grid injection during the top 20 fall peak load hours over the last three years, plus the forecasted net change in generation capacity available to the ERCOT grid pursuant to Nodal Protocol Section 10.3.2.4.
|  | Coastal Wind, Peak Average Capacity Contribution, MW | 1204.56 | Based on 35% of installed capacity for coastal wind resources (fall season) per ERCOT Nodal Protocols Section 3.2.6.2.2
|  | Panhandle Wind, Peak Average Capacity Contribution, MW | 1895.741 | Based on 43% of installed capacity for panhandle wind resources (fall season) per ERCOT Nodal Protocols Section 3.2.6.2.2
|  | Other Wind, Peak Average Capacity Contribution, MW | 6502.598 | Based on 38% of installed capacity for other wind resources (fall season) per ERCOT Nodal Protocols Section 3.2.6.2.2
|  | Solar Utility-Scale, Peak Average Capacity Contribution, MW | 2392.104 | Based on 66% of rated capacity for solar resources (fall season) per Nodal Protocols Section 3.2.6.2.2
|  | Storage, Peak Average Capacity Contribution, MW | 0 | Based on 0% of rated capacity (fall season); resources assumed to provide regulation reserves rather than sustained capacity available to meet peak loads
|  | RMR Capacity to be under Contract | 0
|  | Capacity Pending Retirement, MW | 0 | Announced retired capacity that is undergoing ERCOT grid reliability reviews pursuant to Nodal Protocol Section 3.14.1.2
|  | Non-Synchronous Ties, Capacity Contribution, MW | 837.53 | Based on net imports during winter 2013/2014 Energy Emergency Alert (EEA) intervals (Used as a proxy for the fall season due to lack of EEA intervals)
|  | Planned Thermal Resources with Signed IA, Air Permits and Water Rights, MW | 0 | Based on in-service dates provided by developers
|  | Planned Coastal Wind with Signed IA, Peak Average Capacity Contribution, MW | 129.815 | Based on in-service dates provided by developers and 35% fall capacity contribution for coastal wind resources
|  | Planned Panhandle Wind with Signed IA, Peak Average Capacity Contribution, MW | 0 | Based on in-service dates provided by developers and 43% fall capacity contribution for panhandle wind resources
|  | Planned Other Wind with Signed IA, Peak Average Capacity Contribution, MW | 959.918 | Based on in-service dates provided by developers and 38% fall capacity contribution for other wind resources
|  | Planned Solar Utility-Scale, Peak Average Capacity Contribution, MW | 385.704 | Based on in-service dates provided by developers and 66% fall capacity contribution for solar resources
|  | Planned Storage, Peak Average Capacity Contribution, MW | 0 | Based on in-service dates provided by developers and 0% fall capacity contribution for storage resources
| [a] Total Resources, MW |  | 86011.5868
| [b] Peak Demand, MW |  | 60966 | Based on average weather conditions at the time of the fall peak demand from 2004 – 2018, and updated based on a revised economic growth forecast prepared in April 2020
| [c] Reserve Capacity [a - b], MW |  | 25045.5868
Range of Potential Risks
|  |  | Forecasted Season Peak Load / Typical Generation Outages | Forecasted Season Peak Load / Extreme Generation Outages | Forecasted Season Peak Load / Extreme Low Wind Output | Extreme Season Peak Load / Typical Generation Outages
|  | Seasonal Load Adjustment | 0 | 0 | 0 | 4694 | Based on 2014 fall weather conditions and an April 2020 revised economic growth forecast; the extreme fall forecast is 65,660 MW
|  | Typical Maintenance Outages, Thermal | 9925.9474 | 9925.9474 | 9925.9474 | 9925.9474 | Based on the historical average of planned outages for October through November weekdays, hours ending 2 pm - 8 pm, for the last three fall seasons (2017 - 2019)
|  | Typical Forced Outages, Thermal | 4341.4223 | 4341.4223 | 4341.4223 | 4341.4223 | Based on historical average of forced outages for October through November weekdays, hours ending 2 pm - 8 pm, for the last three fall seasons (2017 - 2019)
|  | 95th Percentile Forced Outages, Thermal | 0 | 3157.4777 | 0 | 0 | Based on the 95th percentile of historical forced outages for October through November weekdays, hours ending 2 pm - 8 pm, for the last three fall seasons (2017 - 2019); the adjustment is the 95th percentile value, 8,006 MW, less the typical forced outage amount of 3,616 MW
|  | Low Wind Output Adjustment | 0 | 0 | 8907.632 | 0 | Based on the 5th percentile of hourly wind capacity factors (output as a percentage of installed capacity) associated with the 100 highest Net Load hours (Load minus wind output) for the 2015-2019 fall Peak Load seasons; this low wind output level is 1,785 MW
| [d] Total Uses of Reserve Capacity |  | 14267.3697 | 17424.8474 | 23175.0017 | 18961.3697
| [e] Capacity Available for Operating Reserves, Normal Operating Conditions (c-d), MW |  | 10778.2171 | 7620.7394 | 1870.5851 | 6084.2171 | See the Background tab for additional details
Less than 2,300 MW indicates risk of EEA1

## FallCapacities
Unit Capacities - Fall
| UNIT NAME | GENERATION INTERCONNECTION PROJECT CODE | UNIT CODE | COUNTY | FUEL | CDR ZONE | START YEAR | CAPACITY (MW)
Operational Resources (Thermal)
4 | COMANCHE PEAK U1 |  | CPSES_UNIT1 | SOMERVELL | NUCLEAR | NORTH | 1990 | 1222
5 | COMANCHE PEAK U2 |  | CPSES_UNIT2 | SOMERVELL | NUCLEAR | NORTH | 1993 | 1209
6 | SOUTH TEXAS U1 | 20INR0287 | STP_STP_G1 | MATAGORDA | NUCLEAR | COASTAL | 1988 | 1323.2
7 | SOUTH TEXAS U2 |  | STP_STP_G2 | MATAGORDA | NUCLEAR | COASTAL | 1989 | 1310
8 | COLETO CREEK |  | COLETO_COLETOG1 | GOLIAD | COAL | SOUTH | 1980 | 655
9 | FAYETTE POWER U1 |  | FPPYD1_FPP_G1 | FAYETTE | COAL | SOUTH | 1979 | 603
10 | FAYETTE POWER U2 |  | FPPYD1_FPP_G2 | FAYETTE | COAL | SOUTH | 1980 | 603
11 | FAYETTE POWER U3 |  | FPPYD2_FPP_G3 | FAYETTE | COAL | SOUTH | 1988 | 444
12 | J K SPRUCE U1 |  | CALAVERS_JKS1 | BEXAR | COAL | SOUTH | 1992 | 560
13 | J K SPRUCE U2 |  | CALAVERS_JKS2 | BEXAR | COAL | SOUTH | 2010 | 785
14 | LIMESTONE U1 |  | LEG_LEG_G1 | LIMESTONE | COAL | NORTH | 1985 | 824
15 | LIMESTONE U2 |  | LEG_LEG_G2 | LIMESTONE | COAL | NORTH | 1986 | 836
16 | MARTIN LAKE U1 |  | MLSES_UNIT1 | RUSK | COAL | NORTH | 1977 | 815
17 | MARTIN LAKE U2 |  | MLSES_UNIT2 | RUSK | COAL | NORTH | 1978 | 820
18 | MARTIN LAKE U3 |  | MLSES_UNIT3 | RUSK | COAL | NORTH | 1979 | 820
19 | OAK GROVE SES U1 |  | OGSES_UNIT1A | ROBERTSON | COAL | NORTH | 2010 | 855
20 | OAK GROVE SES U2 |  | OGSES_UNIT2 | ROBERTSON | COAL | NORTH | 2011 | 855
21 | SAN MIGUEL U1 |  | SANMIGL_G1 | ATASCOSA | COAL | SOUTH | 1982 | 391
22 | SANDY CREEK U1 |  | SCES_UNIT1 | MCLENNAN | COAL | NORTH | 2013 | 945
23 | TWIN OAKS U1 |  | TNP_ONE_TNP_O_1 | ROBERTSON | COAL | NORTH | 1990 | 155
24 | TWIN OAKS U2 |  | TNP_ONE_TNP_O_2 | ROBERTSON | COAL | NORTH | 1991 | 155
25 | W A PARISH U5 |  | WAP_WAP_G5 | FORT BEND | COAL | HOUSTON | 1977 | 664
26 | W A PARISH U6 |  | WAP_WAP_G6 | FORT BEND | COAL | HOUSTON | 1978 | 663
27 | W A PARISH U7 |  | WAP_WAP_G7 | FORT BEND | COAL | HOUSTON | 1980 | 577
28 | W A PARISH U8 |  | WAP_WAP_G8 | FORT BEND | COAL | HOUSTON | 1982 | 610
29 | ARTHUR VON ROSENBERG 1 CTG 1 |  | BRAUNIG_AVR1_CT1 | BEXAR | GAS-CC | SOUTH | 2000 | 164
30 | ARTHUR VON ROSENBERG 1 CTG 2 |  | BRAUNIG_AVR1_CT2 | BEXAR | GAS-CC | SOUTH | 2000 | 164
31 | ARTHUR VON ROSENBERG 1 STG |  | BRAUNIG_AVR1_ST | BEXAR | GAS-CC | SOUTH | 2000 | 190
32 | ATKINS CTG 7 |  | ATKINS_ATKINSG7 | BRAZOS | GAS-GT | NORTH | 1973 | 19
33 | BARNEY M DAVIS CTG 3 | 20INR0312 | B_DAVIS_B_DAVIG3 | NUECES | GAS-CC | COASTAL | 2010 | 161
34 | BARNEY M DAVIS CTG 4 | 20INR0312 | B_DAVIS_B_DAVIG4 | NUECES | GAS-CC | COASTAL | 2010 | 161
35 | BARNEY M DAVIS STG 1 | 20INR0312 | B_DAVIS_B_DAVIG1 | NUECES | GAS-ST | COASTAL | 1974 | 330
36 | BARNEY M DAVIS STG 2 | 20INR0312 | B_DAVIS_B_DAVIG2 | NUECES | GAS-CC | COASTAL | 1976 | 322
37 | BASTROP ENERGY CENTER CTG 1 |  | BASTEN_GTG1100 | BASTROP | GAS-CC | SOUTH | 2002 | 157
38 | BASTROP ENERGY CENTER CTG 2 |  | BASTEN_GTG2100 | BASTROP | GAS-CC | SOUTH | 2002 | 157
39 | BASTROP ENERGY CENTER STG |  | BASTEN_ST0100 | BASTROP | GAS-CC | SOUTH | 2002 | 236
40 | BOSQUE ENERGY CENTER CTG 1 |  | BOSQUESW_BSQSU_1 | BOSQUE | GAS-CC | NORTH | 2000 | 160.5
41 | BOSQUE ENERGY CENTER CTG 2 |  | BOSQUESW_BSQSU_2 | BOSQUE | GAS-CC | NORTH | 2000 | 160.5
42 | BOSQUE ENERGY CENTER CTG 3 |  | BOSQUESW_BSQSU_3 | BOSQUE | GAS-CC | NORTH | 2001 | 159.5
43 | BOSQUE ENERGY CENTER STG 4 |  | BOSQUESW_BSQSU_4 | BOSQUE | GAS-CC | NORTH | 2001 | 83.3
44 | BOSQUE ENERGY CENTER STG 5 |  | BOSQUESW_BSQSU_5 | BOSQUE | GAS-CC | NORTH | 2009 | 221.5
45 | BRAZOS VALLEY CTG 1 |  | BVE_UNIT1 | FORT BEND | GAS-CC | HOUSTON | 2003 | 168
46 | BRAZOS VALLEY CTG 2 |  | BVE_UNIT2 | FORT BEND | GAS-CC | HOUSTON | 2003 | 168
47 | BRAZOS VALLEY STG 3 |  | BVE_UNIT3 | FORT BEND | GAS-CC | HOUSTON | 2003 | 270
48 | CALENERGY-FALCON SEABOARD CTG 1 |  | FLCNS_UNIT1 | HOWARD | GAS-CC | WEST | 1987 | 77
49 | CALENERGY-FALCON SEABOARD CTG 2 |  | FLCNS_UNIT2 | HOWARD | GAS-CC | WEST | 1987 | 77
50 | CALENERGY-FALCON SEABOARD STG 3 |  | FLCNS_UNIT3 | HOWARD | GAS-CC | WEST | 1988 | 71
51 | CALHOUN (PORT COMFORT) CTG 1 |  | CALHOUN_UNIT1 | CALHOUN | GAS-GT | COASTAL | 2017 | 46.5
52 | CALHOUN (PORT COMFORT) CTG 2 |  | CALHOUN_UNIT2 | CALHOUN | GAS-GT | COASTAL | 2017 | 46.5
53 | CASTLEMAN CHAMON CTG 1 |  | CHAMON_CTG_0101 | HARRIS | GAS-GT | HOUSTON | 2017 | 46.5
54 | CASTLEMAN CHAMON CTG 2 |  | CHAMON_CTG_0301 | HARRIS | GAS-GT | HOUSTON | 2017 | 46.5
55 | CEDAR BAYOU 4 CTG 1 |  | CBY4_CT41 | CHAMBERS | GAS-CC | HOUSTON | 2009 | 168
56 | CEDAR BAYOU 4 CTG 2 |  | CBY4_CT42 | CHAMBERS | GAS-CC | HOUSTON | 2009 | 168
57 | CEDAR BAYOU 4 STG |  | CBY4_ST04 | CHAMBERS | GAS-CC | HOUSTON | 2009 | 182
58 | CEDAR BAYOU STG 1 |  | CBY_CBY_G1 | CHAMBERS | GAS-ST | HOUSTON | 1970 | 745
59 | CEDAR BAYOU STG 2 |  | CBY_CBY_G2 | CHAMBERS | GAS-ST | HOUSTON | 1972 | 749
60 | COLORADO BEND ENERGY CENTER CTG 1 |  | CBEC_GT1 | WHARTON | GAS-CC | SOUTH | 2007 | 83.9
61 | COLORADO BEND ENERGY CENTER CTG 2 |  | CBEC_GT2 | WHARTON | GAS-CC | SOUTH | 2007 | 76.9
62 | COLORADO BEND ENERGY CENTER CTG 3 |  | CBEC_GT3 | WHARTON | GAS-CC | SOUTH | 2008 | 82.9
63 | COLORADO BEND ENERGY CENTER CTG 4 |  | CBEC_GT4 | WHARTON | GAS-CC | SOUTH | 2008 | 77.2
64 | COLORADO BEND ENERGY CENTER STG 1 |  | CBEC_STG1 | WHARTON | GAS-CC | SOUTH | 2007 | 107
65 | COLORADO BEND ENERGY CENTER STG 2 |  | CBEC_STG2 | WHARTON | GAS-CC | SOUTH | 2008 | 110
66 | COLORADO BEND II CTG 7 | 18INR0077 | CBECII_CT7 | WHARTON | GAS-CC | SOUTH | 2017 | 332.5
67 | COLORADO BEND II CTG 8 | 18INR0077 | CBECII_CT8 | WHARTON | GAS-CC | SOUTH | 2017 | 338.2
68 | COLORADO BEND II STG 9 | 18INR0077 | CBECII_STG9 | WHARTON | GAS-CC | SOUTH | 2017 | 482.8
69 | CVC CHANNELVIEW CTG 1 |  | CVC_CVC_G1 | HARRIS | GAS-CC | HOUSTON | 2008 | 168
70 | CVC CHANNELVIEW CTG 2 |  | CVC_CVC_G2 | HARRIS | GAS-CC | HOUSTON | 2008 | 163
71 | CVC CHANNELVIEW CTG 3 |  | CVC_CVC_G3 | HARRIS | GAS-CC | HOUSTON | 2008 | 163
72 | CVC CHANNELVIEW STG 5 |  | CVC_CVC_G5 | HARRIS | GAS-CC | HOUSTON | 2008 | 128
73 | DANSBY CTG 2 |  | DANSBY_DANSBYG2 | BRAZOS | GAS-GT | NORTH | 2004 | 46.5
74 | DANSBY CTG 3 |  | DANSBY_DANSBYG3 | BRAZOS | GAS-GT | NORTH | 2010 | 48.5
75 | DANSBY STG 1 |  | DANSBY_DANSBYG1 | BRAZOS | GAS-ST | NORTH | 1978 | 108.5
76 | DECKER CREEK CTG 1 |  | DECKER_DPGT_1 | TRAVIS | GAS-GT | SOUTH | 1989 | 49
77 | DECKER CREEK CTG 2 |  | DECKER_DPGT_2 | TRAVIS | GAS-GT | SOUTH | 1989 | 49
78 | DECKER CREEK CTG 3 |  | DECKER_DPGT_3 | TRAVIS | GAS-GT | SOUTH | 1989 | 49
79 | DECKER CREEK CTG 4 |  | DECKER_DPGT_4 | TRAVIS | GAS-GT | SOUTH | 1989 | 49
80 | DECKER CREEK STG 1 (RETIRING ON 10/31/2020) |  | DECKER_DPG1 | TRAVIS | GAS-ST | SOUTH | 1971 | 320
81 | DECKER CREEK STG 2 |  | DECKER_DPG2 | TRAVIS | GAS-ST | SOUTH | 1978 | 420
82 | DECORDOVA CTG 1 |  | DCSES_CT10 | HOOD | GAS-GT | NORTH | 1990 | 72
83 | DECORDOVA CTG 2 |  | DCSES_CT20 | HOOD | GAS-GT | NORTH | 1990 | 71
84 | DECORDOVA CTG 3 |  | DCSES_CT30 | HOOD | GAS-GT | NORTH | 1990 | 70
85 | DECORDOVA CTG 4 |  | DCSES_CT40 | HOOD | GAS-GT | NORTH | 1990 | 71
86 | DEER PARK ENERGY CENTER CTG 1 |  | DDPEC_GT1 | HARRIS | GAS-CC | HOUSTON | 2002 | 194
87 | DEER PARK ENERGY CENTER CTG 2 |  | DDPEC_GT2 | HARRIS | GAS-CC | HOUSTON | 2002 | 206
88 | DEER PARK ENERGY CENTER CTG 3 |  | DDPEC_GT3 | HARRIS | GAS-CC | HOUSTON | 2002 | 194
89 | DEER PARK ENERGY CENTER CTG 4 |  | DDPEC_GT4 | HARRIS | GAS-CC | HOUSTON | 2002 | 206
90 | DEER PARK ENERGY CENTER CTG 6 |  | DDPEC_GT6 | HARRIS | GAS-CC | HOUSTON | 2014 | 179
91 | DEER PARK ENERGY CENTER STG 1 |  | DDPEC_ST1 | HARRIS | GAS-CC | HOUSTON | 2002 | 290
92 | DENTON ENERGY CENTER IC A |  | DEC_AGR_A | DENTON | GAS-IC | NORTH | 2018 | 56.5
93 | DENTON ENERGY CENTER IC B |  | DEC_AGR_B | DENTON | GAS-IC | NORTH | 2018 | 56.5
94 | DENTON ENERGY CENTER IC C |  | DEC_AGR_C | DENTON | GAS-IC | NORTH | 2018 | 56.5
95 | DENTON ENERGY CENTER IC D |  | DEC_AGR_D | DENTON | GAS-IC | NORTH | 2018 | 56.5
96 | ECTOR COUNTY ENERGY CTG 1 |  | ECEC_G1 | ECTOR | GAS-GT | WEST | 2015 | 153.6
97 | ECTOR COUNTY ENERGY CTG 2 |  | ECEC_G2 | ECTOR | GAS-GT | WEST | 2015 | 153.6
98 | ELK STATION IC 3 |  | AEEC_ELK_3 | HALE | GAS-IC | PANHANDLE | 2016 | 195
99 | ENNIS POWER STATION CTG 2 | 21INR0448 | ETCCS_CT1 | ELLIS | GAS-CC | NORTH | 2002 | 212
100 | ENNIS POWER STATION STG 1 | 21INR0448 | ETCCS_UNIT1 | ELLIS | GAS-CC | NORTH | 2002 | 117
101 | EXTEX LAPORTE GEN STN CTG 1 |  | AZ_AZ_G1 | HARRIS | GAS-GT | HOUSTON | 2009 | 38
102 | EXTEX LAPORTE GEN STN CTG 2 |  | AZ_AZ_G2 | HARRIS | GAS-GT | HOUSTON | 2009 | 38
103 | EXTEX LAPORTE GEN STN CTG 3 |  | AZ_AZ_G3 | HARRIS | GAS-GT | HOUSTON | 2009 | 38
104 | EXTEX LAPORTE GEN STN CTG 4 |  | AZ_AZ_G4 | HARRIS | GAS-GT | HOUSTON | 2009 | 38
105 | FERGUSON REPLACEMENT CTG 1 |  | FERGCC_FERGGT1 | LLANO | GAS-CC | SOUTH | 2014 | 173
106 | FERGUSON REPLACEMENT CTG 2 |  | FERGCC_FERGGT2 | LLANO | GAS-CC | SOUTH | 2014 | 173
107 | FERGUSON REPLACEMENT STG 1 |  | FERGCC_FERGST1 | LLANO | GAS-CC | SOUTH | 2014 | 186
108 | FORNEY ENERGY CENTER CTG 11 |  | FRNYPP_GT11 | KAUFMAN | GAS-CC | NORTH | 2003 | 169
109 | FORNEY ENERGY CENTER CTG 12 |  | FRNYPP_GT12 | KAUFMAN | GAS-CC | NORTH | 2003 | 161
110 | FORNEY ENERGY CENTER CTG 13 |  | FRNYPP_GT13 | KAUFMAN | GAS-CC | NORTH | 2003 | 161
111 | FORNEY ENERGY CENTER CTG 21 |  | FRNYPP_GT21 | KAUFMAN | GAS-CC | NORTH | 2003 | 169
112 | FORNEY ENERGY CENTER CTG 22 |  | FRNYPP_GT22 | KAUFMAN | GAS-CC | NORTH | 2003 | 161
113 | FORNEY ENERGY CENTER CTG 23 |  | FRNYPP_GT23 | KAUFMAN | GAS-CC | NORTH | 2003 | 161
114 | FORNEY ENERGY CENTER STG 10 |  | FRNYPP_ST10 | KAUFMAN | GAS-CC | NORTH | 2003 | 409
115 | FORNEY ENERGY CENTER STG 20 |  | FRNYPP_ST20 | KAUFMAN | GAS-CC | NORTH | 2003 | 409
116 | FREESTONE ENERGY CENTER CTG 1 |  | FREC_GT1 | FREESTONE | GAS-CC | NORTH | 2002 | 155.2
117 | FREESTONE ENERGY CENTER CTG 2 |  | FREC_GT2 | FREESTONE | GAS-CC | NORTH | 2002 | 155.2
118 | FREESTONE ENERGY CENTER CTG 4 |  | FREC_GT4 | FREESTONE | GAS-CC | NORTH | 2002 | 155.4
119 | FREESTONE ENERGY CENTER CTG 5 |  | FREC_GT5 | FREESTONE | GAS-CC | NORTH | 2002 | 155.4
120 | FREESTONE ENERGY CENTER STG 3 |  | FREC_ST3 | FREESTONE | GAS-CC | NORTH | 2002 | 177.6
121 | FREESTONE ENERGY CENTER STG 6 |  | FREC_ST6 | FREESTONE | GAS-CC | NORTH | 2002 | 176.5
122 | FRIENDSWOOD G (FEGC) CTG 1 |  | FEGC_UNIT1 | HARRIS | GAS-GT | HOUSTON | 2018 | 119
123 | GRAHAM STG 1 |  | GRSES_UNIT1 | YOUNG | GAS-ST | WEST | 1960 | 234
124 | GRAHAM STG 2 |  | GRSES_UNIT2 | YOUNG | GAS-ST | WEST | 1969 | 390
125 | GREENS BAYOU CTG 73 |  | GBY_GBYGT73 | HARRIS | GAS-GT | HOUSTON | 1976 | 57
126 | GREENS BAYOU CTG 74 |  | GBY_GBYGT74 | HARRIS | GAS-GT | HOUSTON | 1976 | 57
127 | GREENS BAYOU CTG 81 |  | GBY_GBYGT81 | HARRIS | GAS-GT | HOUSTON | 1976 | 57
128 | GREENS BAYOU CTG 82 |  | GBY_GBYGT82 | HARRIS | GAS-GT | HOUSTON | 1976 | 50
129 | GREENS BAYOU CTG 83 |  | GBY_GBYGT83 | HARRIS | GAS-GT | HOUSTON | 1976 | 57
130 | GREENS BAYOU CTG 84 |  | GBY_GBYGT84 | HARRIS | GAS-GT | HOUSTON | 1976 | 57
131 | GREENVILLE IC ENGINE PLANT IC 1 |  | STEAM_ENGINE_1 | HUNT | GAS-IC | NORTH | 2010 | 8.2
132 | GREENVILLE IC ENGINE PLANT IC 2 |  | STEAM_ENGINE_2 | HUNT | GAS-IC | NORTH | 2010 | 8.2
133 | GREENVILLE IC ENGINE PLANT IC 3 |  | STEAM_ENGINE_3 | HUNT | GAS-IC | NORTH | 2010 | 8.2
134 | GUADALUPE ENERGY CENTER CTG 1 |  | GUADG_GAS1 | GUADALUPE | GAS-CC | SOUTH | 2000 | 158
135 | GUADALUPE ENERGY CENTER CTG 2 |  | GUADG_GAS2 | GUADALUPE | GAS-CC | SOUTH | 2000 | 158
136 | GUADALUPE ENERGY CENTER CTG 3 |  | GUADG_GAS3 | GUADALUPE | GAS-CC | SOUTH | 2000 | 158
137 | GUADALUPE ENERGY CENTER CTG 4 |  | GUADG_GAS4 | GUADALUPE | GAS-CC | SOUTH | 2000 | 158
138 | GUADALUPE ENERGY CENTER STG 5 |  | GUADG_STM5 | GUADALUPE | GAS-CC | SOUTH | 2000 | 200
139 | GUADALUPE ENERGY CENTER STG 6 |  | GUADG_STM6 | GUADALUPE | GAS-CC | SOUTH | 2000 | 200
140 | HANDLEY STG 3 |  | HLSES_UNIT3 | TARRANT | GAS-ST | NORTH | 1963 | 395
141 | HANDLEY STG 4 |  | HLSES_UNIT4 | TARRANT | GAS-ST | NORTH | 1976 | 435
142 | HANDLEY STG 5 |  | HLSES_UNIT5 | TARRANT | GAS-ST | NORTH | 1977 | 435
143 | HAYS ENERGY FACILITY CSG 1 |  | HAYSEN_HAYSENG1 | HAYS | GAS-CC | SOUTH | 2002 | 214
144 | HAYS ENERGY FACILITY CSG 2 |  | HAYSEN_HAYSENG2 | HAYS | GAS-CC | SOUTH | 2002 | 216
145 | HAYS ENERGY FACILITY CSG 3 |  | HAYSEN_HAYSENG3 | HAYS | GAS-CC | SOUTH | 2002 | 215
146 | HAYS ENERGY FACILITY CSG 4 |  | HAYSEN_HAYSENG4 | HAYS | GAS-CC | SOUTH | 2002 | 218
147 | HIDALGO ENERGY CENTER CTG 1 |  | DUKE_DUKE_GT1 | HIDALGO | GAS-CC | SOUTH | 2000 | 145
148 | HIDALGO ENERGY CENTER CTG 2 |  | DUKE_DUKE_GT2 | HIDALGO | GAS-CC | SOUTH | 2000 | 145
149 | HIDALGO ENERGY CENTER STG 1 |  | DUKE_DUKE_ST1 | HIDALGO | GAS-CC | SOUTH | 2000 | 173
150 | JACK COUNTY GEN FACILITY CTG 1 |  | JACKCNTY_CT1 | JACK | GAS-CC | NORTH | 2006 | 150
151 | JACK COUNTY GEN FACILITY CTG 2 |  | JACKCNTY_CT2 | JACK | GAS-CC | NORTH | 2006 | 150
152 | JACK COUNTY GEN FACILITY CTG 3 |  | JCKCNTY2_CT3 | JACK | GAS-CC | NORTH | 2011 | 150
153 | JACK COUNTY GEN FACILITY CTG 4 |  | JCKCNTY2_CT4 | JACK | GAS-CC | NORTH | 2011 | 150
154 | JACK COUNTY GEN FACILITY STG 1 |  | JACKCNTY_STG | JACK | GAS-CC | NORTH | 2006 | 285
155 | JACK COUNTY GEN FACILITY STG 2 |  | JCKCNTY2_ST2 | JACK | GAS-CC | NORTH | 2011 | 285
156 | JOHNSON COUNTY GEN FACILITY CTG 1 |  | TEN_CT1 | JOHNSON | GAS-CC | NORTH | 1997 | 163
157 | JOHNSON COUNTY GEN FACILITY STG 1 |  | TEN_STG | JOHNSON | GAS-CC | NORTH | 1997 | 106
158 | LAKE HUBBARD STG 1 |  | LHSES_UNIT1 | DALLAS | GAS-ST | NORTH | 1970 | 392
159 | LAKE HUBBARD STG 2 |  | LHSES_UNIT2A | DALLAS | GAS-ST | NORTH | 1973 | 523
160 | LAMAR ENERGY CENTER CTG 11 |  | LPCCS_CT11 | LAMAR | GAS-CC | NORTH | 2000 | 161
161 | LAMAR ENERGY CENTER CTG 12 |  | LPCCS_CT12 | LAMAR | GAS-CC | NORTH | 2000 | 153
162 | LAMAR ENERGY CENTER CTG 21 |  | LPCCS_CT21 | LAMAR | GAS-CC | NORTH | 2000 | 153
163 | LAMAR ENERGY CENTER CTG 22 |  | LPCCS_CT22 | LAMAR | GAS-CC | NORTH | 2000 | 161
164 | LAMAR ENERGY CENTER STG 1 |  | LPCCS_UNIT1 | LAMAR | GAS-CC | NORTH | 2000 | 204
165 | LAMAR ENERGY CENTER STG 2 |  | LPCCS_UNIT2 | LAMAR | GAS-CC | NORTH | 2000 | 204
166 | LAREDO CTG 4 |  | LARDVFTN_G4 | WEBB | GAS-GT | SOUTH | 2008 | 93
167 | LAREDO CTG 5 |  | LARDVFTN_G5 | WEBB | GAS-GT | SOUTH | 2008 | 90.2
168 | LEON CREEK PEAKER CTG 1 |  | LEON_CRK_LCPCT1 | BEXAR | GAS-GT | SOUTH | 2004 | 46
169 | LEON CREEK PEAKER CTG 2 |  | LEON_CRK_LCPCT2 | BEXAR | GAS-GT | SOUTH | 2004 | 46
170 | LEON CREEK PEAKER CTG 3 |  | LEON_CRK_LCPCT3 | BEXAR | GAS-GT | SOUTH | 2004 | 46
171 | LEON CREEK PEAKER CTG 4 |  | LEON_CRK_LCPCT4 | BEXAR | GAS-GT | SOUTH | 2004 | 46
172 | LOST PINES POWER CTG 1 |  | LOSTPI_LOSTPGT1 | BASTROP | GAS-CC | SOUTH | 2001 | 178
173 | LOST PINES POWER CTG 2 |  | LOSTPI_LOSTPGT2 | BASTROP | GAS-CC | SOUTH | 2001 | 172
174 | LOST PINES POWER STG 1 |  | LOSTPI_LOSTPST1 | BASTROP | GAS-CC | SOUTH | 2001 | 188
175 | MAGIC VALLEY STATION CTG 1 |  | NEDIN_NEDIN_G1 | HIDALGO | GAS-CC | SOUTH | 2001 | 212.5
176 | MAGIC VALLEY STATION CTG 2 |  | NEDIN_NEDIN_G2 | HIDALGO | GAS-CC | SOUTH | 2001 | 212.5
177 | MAGIC VALLEY STATION STG 3 |  | NEDIN_NEDIN_G3 | HIDALGO | GAS-CC | SOUTH | 2001 | 254.9
178 | MIDLOTHIAN ENERGY FACILITY CTG 1 |  | MDANP_CT1 | ELLIS | GAS-CC | NORTH | 2001 | 233
179 | MIDLOTHIAN ENERGY FACILITY CTG 2 |  | MDANP_CT2 | ELLIS | GAS-CC | NORTH | 2001 | 231
180 | MIDLOTHIAN ENERGY FACILITY CTG 3 |  | MDANP_CT3 | ELLIS | GAS-CC | NORTH | 2001 | 230
181 | MIDLOTHIAN ENERGY FACILITY CTG 4 |  | MDANP_CT4 | ELLIS | GAS-CC | NORTH | 2001 | 233
182 | MIDLOTHIAN ENERGY FACILITY CTG 5 |  | MDANP_CT5 | ELLIS | GAS-CC | NORTH | 2002 | 245
183 | MIDLOTHIAN ENERGY FACILITY CTG 6 |  | MDANP_CT6 | ELLIS | GAS-CC | NORTH | 2002 | 247
184 | MORGAN CREEK CTG 1 |  | MGSES_CT1 | MITCHELL | GAS-GT | WEST | 1988 | 68
185 | MORGAN CREEK CTG 2 |  | MGSES_CT2 | MITCHELL | GAS-GT | WEST | 1988 | 67
186 | MORGAN CREEK CTG 3 |  | MGSES_CT3 | MITCHELL | GAS-GT | WEST | 1988 | 67
187 | MORGAN CREEK CTG 4 |  | MGSES_CT4 | MITCHELL | GAS-GT | WEST | 1988 | 68
188 | MORGAN CREEK CTG 5 |  | MGSES_CT5 | MITCHELL | GAS-GT | WEST | 1988 | 69
189 | MORGAN CREEK CTG 6 |  | MGSES_CT6 | MITCHELL | GAS-GT | WEST | 1988 | 69
190 | MOUNTAIN CREEK STG 6 |  | MCSES_UNIT6 | DALLAS | GAS-ST | NORTH | 1956 | 122
191 | MOUNTAIN CREEK STG 7 |  | MCSES_UNIT7 | DALLAS | GAS-ST | NORTH | 1958 | 118
192 | MOUNTAIN CREEK STG 8 |  | MCSES_UNIT8 | DALLAS | GAS-ST | NORTH | 1967 | 568
193 | NUECES BAY REPOWER CTG 8 |  | NUECES_B_NUECESG8 | NUECES | GAS-CC | COASTAL | 2010 | 161
194 | NUECES BAY REPOWER CTG 9 |  | NUECES_B_NUECESG9 | NUECES | GAS-CC | COASTAL | 2010 | 161
195 | NUECES BAY REPOWER STG 7 |  | NUECES_B_NUECESG7 | NUECES | GAS-CC | COASTAL | 1972 | 322
196 | O W SOMMERS STG 1 |  | CALAVERS_OWS1 | BEXAR | GAS-ST | SOUTH | 1972 | 420
197 | O W SOMMERS STG 2 |  | CALAVERS_OWS2 | BEXAR | GAS-ST | SOUTH | 1974 | 410
198 | ODESSA-ECTOR POWER CTG 11 |  | OECCS_CT11 | ECTOR | GAS-CC | WEST | 2001 | 167.5
199 | ODESSA-ECTOR POWER CTG 12 |  | OECCS_CT12 | ECTOR | GAS-CC | WEST | 2001 | 159
200 | ODESSA-ECTOR POWER CTG 21 | 20INR0282 | OECCS_CT21 | ECTOR | GAS-CC | WEST | 2001 | 167.5
201 | ODESSA-ECTOR POWER CTG 22 | 20INR0282 | OECCS_CT22 | ECTOR | GAS-CC | WEST | 2001 | 159
202 | ODESSA-ECTOR POWER STG 1 |  | OECCS_UNIT1 | ECTOR | GAS-CC | WEST | 2001 | 207.2
203 | ODESSA-ECTOR POWER STG 2 | 20INR0282 | OECCS_UNIT2 | ECTOR | GAS-CC | WEST | 2001 | 207.2
204 | PANDA SHERMAN POWER CTG 1 |  | PANDA_S_SHER1CT1 | GRAYSON | GAS-CC | NORTH | 2014 | 218.5
205 | PANDA SHERMAN POWER CTG 2 |  | PANDA_S_SHER1CT2 | GRAYSON | GAS-CC | NORTH | 2014 | 218.5
206 | PANDA SHERMAN POWER STG 1 |  | PANDA_S_SHER1ST1 | GRAYSON | GAS-CC | NORTH | 2014 | 353.1
207 | PANDA TEMPLE I POWER CTG 1 |  | PANDA_T1_TMPL1CT1 | BELL | GAS-CC | NORTH | 2014 | 218.5
208 | PANDA TEMPLE I POWER CTG 2 |  | PANDA_T1_TMPL1CT2 | BELL | GAS-CC | NORTH | 2014 | 218.5
209 | PANDA TEMPLE I POWER STG 1 |  | PANDA_T1_TMPL1ST1 | BELL | GAS-CC | NORTH | 2014 | 353.1
210 | PANDA TEMPLE II POWER CTG 1 |  | PANDA_T2_TMPL2CT1 | BELL | GAS-CC | NORTH | 2015 | 218.5
211 | PANDA TEMPLE II POWER CTG 2 |  | PANDA_T2_TMPL2CT2 | BELL | GAS-CC | NORTH | 2015 | 218.5
212 | PANDA TEMPLE II POWER STG 1 |  | PANDA_T2_TMPL2ST1 | BELL | GAS-CC | NORTH | 2015 | 353.1
213 | PARIS ENERGY CENTER CTG 1 |  | TNSKA_GT1 | LAMAR | GAS-CC | NORTH | 1989 | 86
214 | PARIS ENERGY CENTER CTG 2 |  | TNSKA_GT2 | LAMAR | GAS-CC | NORTH | 1989 | 86
215 | PARIS ENERGY CENTER STG 1 |  | TNSKA_STG | LAMAR | GAS-CC | NORTH | 1990 | 87
216 | PASADENA COGEN FACILITY CTG 2 |  | PSG_PSG_GT2 | HARRIS | GAS-CC | HOUSTON | 2000 | 168
217 | PASADENA COGEN FACILITY CTG 3 |  | PSG_PSG_GT3 | HARRIS | GAS-CC | HOUSTON | 2000 | 168
218 | PASADENA COGEN FACILITY STG 2 |  | PSG_PSG_ST2 | HARRIS | GAS-CC | HOUSTON | 2000 | 168
219 | PEARSALL ENGINE PLANT IC A |  | PEARSAL2_AGR_A | FRIO | GAS-IC | SOUTH | 2012 | 50.6
220 | PEARSALL ENGINE PLANT IC B |  | PEARSAL2_AGR_B | FRIO | GAS-IC | SOUTH | 2012 | 50.6
221 | PEARSALL ENGINE PLANT IC C |  | PEARSAL2_AGR_C | FRIO | GAS-IC | SOUTH | 2012 | 50.6
222 | PEARSALL ENGINE PLANT IC D |  | PEARSAL2_AGR_D | FRIO | GAS-IC | SOUTH | 2012 | 50.6
223 | PERMIAN BASIN CTG 1 |  | PB2SES_CT1 | WARD | GAS-GT | WEST | 1988 | 64
224 | PERMIAN BASIN CTG 2 |  | PB2SES_CT2 | WARD | GAS-GT | WEST | 1988 | 66
225 | PERMIAN BASIN CTG 3 |  | PB2SES_CT3 | WARD | GAS-GT | WEST | 1988 | 65
226 | PERMIAN BASIN CTG 4 |  | PB2SES_CT4 | WARD | GAS-GT | WEST | 1990 | 65
227 | PERMIAN BASIN CTG 5 |  | PB2SES_CT5 | WARD | GAS-GT | WEST | 1990 | 66
228 | PHR PEAKERS (BAC) CTG 1 |  | BAC_CTG1 | GALVESTON | GAS-GT | HOUSTON | 2018 | 61
229 | PHR PEAKERS (BAC) CTG 2 |  | BAC_CTG2 | GALVESTON | GAS-GT | HOUSTON | 2018 | 62
230 | PHR PEAKERS (BAC) CTG 3 |  | BAC_CTG3 | GALVESTON | GAS-GT | HOUSTON | 2018 | 52
231 | PHR PEAKERS (BAC) CTG 4 |  | BAC_CTG4 | GALVESTON | GAS-GT | HOUSTON | 2018 | 56
232 | PHR PEAKERS (BAC) CTG 5 |  | BAC_CTG5 | GALVESTON | GAS-GT | HOUSTON | 2018 | 56
233 | PHR PEAKERS (BAC) CTG 6 |  | BAC_CTG6 | GALVESTON | GAS-GT | HOUSTON | 2018 | 55
234 | POWERLANE PLANT STG 1 |  | STEAM1A_STEAM_1 | HUNT | GAS-ST | NORTH | 1966 | 17.5
235 | POWERLANE PLANT STG 2 |  | STEAM_STEAM_2 | HUNT | GAS-ST | NORTH | 1967 | 23.5
236 | POWERLANE PLANT STG 3 |  | STEAM_STEAM_3 | HUNT | GAS-ST | NORTH | 1978 | 39.5
237 | QUAIL RUN ENERGY CTG 1 |  | QALSW_GT1 | ECTOR | GAS-CC | WEST | 2007 | 81
238 | QUAIL RUN ENERGY CTG 2 |  | QALSW_GT2 | ECTOR | GAS-CC | WEST | 2007 | 81
239 | QUAIL RUN ENERGY CTG 3 |  | QALSW_GT3 | ECTOR | GAS-CC | WEST | 2008 | 80
240 | QUAIL RUN ENERGY CTG 4 |  | QALSW_GT4 | ECTOR | GAS-CC | WEST | 2008 | 80
241 | QUAIL RUN ENERGY STG 1 |  | QALSW_STG1 | ECTOR | GAS-CC | WEST | 2007 | 98
242 | QUAIL RUN ENERGY STG 2 |  | QALSW_STG2 | ECTOR | GAS-CC | WEST | 2008 | 98
243 | R W MILLER CTG 4 |  | MIL_MILLERG4 | PALO PINTO | GAS-GT | NORTH | 1994 | 104
244 | R W MILLER CTG 5 |  | MIL_MILLERG5 | PALO PINTO | GAS-GT | NORTH | 1994 | 104
245 | R W MILLER STG 1 |  | MIL_MILLERG1 | PALO PINTO | GAS-ST | NORTH | 1968 | 75
246 | R W MILLER STG 2 |  | MIL_MILLERG2 | PALO PINTO | GAS-ST | NORTH | 1972 | 120
247 | R W MILLER STG 3 |  | MIL_MILLERG3 | PALO PINTO | GAS-ST | NORTH | 1975 | 208
248 | RAY OLINGER CTG 4 |  | OLINGR_OLING_4 | COLLIN | GAS-GT | NORTH | 2001 | 75
249 | RAY OLINGER STG 1 |  | OLINGR_OLING_1 | COLLIN | GAS-ST | NORTH | 1967 | 78
250 | RAY OLINGER STG 2 |  | OLINGR_OLING_2 | COLLIN | GAS-ST | NORTH | 1971 | 107
251 | RAY OLINGER STG 3 |  | OLINGR_OLING_3 | COLLIN | GAS-ST | NORTH | 1975 | 146
252 | REDGATE IC A |  | REDGATE_AGR_A | HIDALGO | GAS-IC | SOUTH | 2016 | 56.3
253 | REDGATE IC B |  | REDGATE_AGR_B | HIDALGO | GAS-IC | SOUTH | 2016 | 56.3
254 | REDGATE IC C |  | REDGATE_AGR_C | HIDALGO | GAS-IC | SOUTH | 2016 | 56.3
255 | REDGATE IC D |  | REDGATE_AGR_D | HIDALGO | GAS-IC | SOUTH | 2016 | 56.3
256 | RIO NOGALES POWER CTG 1 |  | RIONOG_CT1 | GUADALUPE | GAS-CC | SOUTH | 2002 | 173
257 | RIO NOGALES POWER CTG 2 | 21INR0328 | RIONOG_CT2 | GUADALUPE | GAS-CC | SOUTH | 2002 | 160
258 | RIO NOGALES POWER CTG 3 |  | RIONOG_CT3 | GUADALUPE | GAS-CC | SOUTH | 2002 | 173
259 | RIO NOGALES POWER STG 4 |  | RIONOG_ST1 | GUADALUPE | GAS-CC | SOUTH | 2002 | 310
260 | SAM RAYBURN POWER CTG 1 |  | RAYBURN_RAYBURG1 | VICTORIA | GAS-GT | SOUTH | 1963 | 13.5
261 | SAM RAYBURN POWER CTG 2 |  | RAYBURN_RAYBURG2 | VICTORIA | GAS-GT | SOUTH | 1963 | 13.5
262 | SAM RAYBURN POWER CTG 7 |  | RAYBURN_RAYBURG7 | VICTORIA | GAS-CC | SOUTH | 2003 | 50
263 | SAM RAYBURN POWER CTG 8 |  | RAYBURN_RAYBURG8 | VICTORIA | GAS-CC | SOUTH | 2003 | 51
264 | SAM RAYBURN POWER CTG 9 |  | RAYBURN_RAYBURG9 | VICTORIA | GAS-CC | SOUTH | 2003 | 50
265 | SAM RAYBURN POWER STG 10 |  | RAYBURN_RAYBURG10 | VICTORIA | GAS-CC | SOUTH | 2003 | 40
266 | SAN JACINTO SES CTG 1 |  | SJS_SJS_G1 | HARRIS | GAS-GT | HOUSTON | 1995 | 83
267 | SAN JACINTO SES CTG 2 |  | SJS_SJS_G2 | HARRIS | GAS-GT | HOUSTON | 1995 | 83
268 | SANDHILL ENERGY CENTER CTG 1 |  | SANDHSYD_SH1 | TRAVIS | GAS-GT | SOUTH | 2001 | 47
269 | SANDHILL ENERGY CENTER CTG 2 |  | SANDHSYD_SH2 | TRAVIS | GAS-GT | SOUTH | 2001 | 47
270 | SANDHILL ENERGY CENTER CTG 3 |  | SANDHSYD_SH3 | TRAVIS | GAS-GT | SOUTH | 2001 | 47
271 | SANDHILL ENERGY CENTER CTG 4 |  | SANDHSYD_SH4 | TRAVIS | GAS-GT | SOUTH | 2001 | 47
272 | SANDHILL ENERGY CENTER CTG 5A |  | SANDHSYD_SH_5A | TRAVIS | GAS-CC | SOUTH | 2004 | 151
273 | SANDHILL ENERGY CENTER CTG 6 |  | SANDHSYD_SH6 | TRAVIS | GAS-GT | SOUTH | 2010 | 47
274 | SANDHILL ENERGY CENTER CTG 7 |  | SANDHSYD_SH7 | TRAVIS | GAS-GT | SOUTH | 2010 | 47
275 | SANDHILL ENERGY CENTER STG 5C |  | SANDHSYD_SH_5C | TRAVIS | GAS-CC | SOUTH | 2004 | 148
276 | SILAS RAY CTG 10 |  | SILASRAY_SILAS_10 | CAMERON | GAS-GT | COASTAL | 2004 | 46
277 | SILAS RAY POWER CTG 9 |  | SILASRAY_SILAS_9 | CAMERON | GAS-CC | COASTAL | 1996 | 38
278 | SILAS RAY POWER STG 6 |  | SILASRAY_SILAS_6 | CAMERON | GAS-CC | COASTAL | 1962 | 20
279 | SIM GIDEON STG 1 |  | GIDEON_GIDEONG1 | BASTROP | GAS-ST | SOUTH | 1965 | 130
280 | SIM GIDEON STG 2 |  | GIDEON_GIDEONG2 | BASTROP | GAS-ST | SOUTH | 1968 | 135
281 | SIM GIDEON STG 3 |  | GIDEON_GIDEONG3 | BASTROP | GAS-ST | SOUTH | 1972 | 336
282 | SKY GLOBAL POWER ONE IC A |  | SKY1_SKY1A | COLORADO | GAS-IC | SOUTH | 2016 | 26.7
283 | SKY GLOBAL POWER ONE IC B |  | SKY1_SKY1B | COLORADO | GAS-IC | SOUTH | 2016 | 26.7
284 | STRYKER CREEK STG 1 |  | SCSES_UNIT1A | CHEROKEE | GAS-ST | NORTH | 1958 | 167
285 | STRYKER CREEK STG 2 |  | SCSES_UNIT2 | CHEROKEE | GAS-ST | NORTH | 1965 | 502
286 | T H WHARTON CTG 1 |  | THW_THWGT_1 | HARRIS | GAS-GT | HOUSTON | 1967 | 14
287 | T H WHARTON POWER CTG 31 |  | THW_THWGT31 | HARRIS | GAS-CC | HOUSTON | 1972 | 56
288 | T H WHARTON POWER CTG 32 |  | THW_THWGT32 | HARRIS | GAS-CC | HOUSTON | 1972 | 56
289 | T H WHARTON POWER CTG 33 |  | THW_THWGT33 | HARRIS | GAS-CC | HOUSTON | 1972 | 56
290 | T H WHARTON POWER CTG 34 |  | THW_THWGT34 | HARRIS | GAS-CC | HOUSTON | 1972 | 56
291 | T H WHARTON POWER CTG 41 |  | THW_THWGT41 | HARRIS | GAS-CC | HOUSTON | 1972 | 56
292 | T H WHARTON POWER CTG 42 |  | THW_THWGT42 | HARRIS | GAS-CC | HOUSTON | 1972 | 56
293 | T H WHARTON POWER CTG 43 |  | THW_THWGT43 | HARRIS | GAS-CC | HOUSTON | 1974 | 56
294 | T H WHARTON POWER CTG 44 |  | THW_THWGT44 | HARRIS | GAS-CC | HOUSTON | 1974 | 56
295 | T H WHARTON POWER CTG 51 |  | THW_THWGT51 | HARRIS | GAS-GT | HOUSTON | 1975 | 57
296 | T H WHARTON POWER CTG 52 |  | THW_THWGT52 | HARRIS | GAS-GT | HOUSTON | 1975 | 57
297 | T H WHARTON POWER CTG 53 |  | THW_THWGT53 | HARRIS | GAS-GT | HOUSTON | 1975 | 57
298 | T H WHARTON POWER CTG 54 |  | THW_THWGT54 | HARRIS | GAS-GT | HOUSTON | 1975 | 57
299 | T H WHARTON POWER CTG 55 |  | THW_THWGT55 | HARRIS | GAS-GT | HOUSTON | 1975 | 57
300 | T H WHARTON POWER CTG 56 |  | THW_THWGT56 | HARRIS | GAS-GT | HOUSTON | 1975 | 57
301 | T H WHARTON POWER STG 3 |  | THW_THWST_3 | HARRIS | GAS-CC | HOUSTON | 1974 | 110
302 | T H WHARTON POWER STG 4 |  | THW_THWST_4 | HARRIS | GAS-CC | HOUSTON | 1974 | 110
303 | TEXAS CITY POWER CTG A |  | TXCTY_CTA | GALVESTON | GAS-CC | HOUSTON | 2000 | 99.1
304 | TEXAS CITY POWER CTG B |  | TXCTY_CTB | GALVESTON | GAS-CC | HOUSTON | 2000 | 99.1
305 | TEXAS CITY POWER CTG C |  | TXCTY_CTC | GALVESTON | GAS-CC | HOUSTON | 2000 | 99.1
306 | TEXAS CITY POWER STG |  | TXCTY_ST | GALVESTON | GAS-CC | HOUSTON | 2000 | 131.5
307 | TEXAS GULF SULPHUR CTG 1 |  | TGF_TGFGT_1 | WHARTON | GAS-GT | SOUTH | 1985 | 71
308 | TRINIDAD STG 6 |  | TRSES_UNIT6 | HENDERSON | GAS-ST | NORTH | 1965 | 235
309 | V H BRAUNIG CTG 5 |  | BRAUNIG_VHB6CT5 | BEXAR | GAS-GT | SOUTH | 2009 | 48
310 | V H BRAUNIG CTG 6 |  | BRAUNIG_VHB6CT6 | BEXAR | GAS-GT | SOUTH | 2009 | 48
311 | V H BRAUNIG CTG 7 |  | BRAUNIG_VHB6CT7 | BEXAR | GAS-GT | SOUTH | 2009 | 48
312 | V H BRAUNIG CTG 8 |  | BRAUNIG_VHB6CT8 | BEXAR | GAS-GT | SOUTH | 2009 | 47
313 | V H BRAUNIG STG 1 |  | BRAUNIG_VHB1 | BEXAR | GAS-ST | SOUTH | 1966 | 217
314 | V H BRAUNIG STG 2 |  | BRAUNIG_VHB2 | BEXAR | GAS-ST | SOUTH | 1968 | 230
315 | V H BRAUNIG STG 3 |  | BRAUNIG_VHB3 | BEXAR | GAS-ST | SOUTH | 1970 | 412
316 | VICTORIA CITY (CITYVICT) CTG 1 |  | CITYVICT_CTG01 | VICTORIA | GAS-GT | SOUTH | 2020 | 46.5
317 | VICTORIA CITY (CITYVICT) CTG 2 |  | CITYVICT_CTG02 | VICTORIA | GAS-GT | SOUTH | 2020 | 46.5
318 | VICTORIA PORT (VICTPORT) CTG 1 |  | VICTPORT_CTG01 | VICTORIA | GAS-GT | SOUTH | 2019 | 46.5
319 | VICTORIA PORT (VICTPORT) CTG 2 |  | VICTPORT_CTG02 | VICTORIA | GAS-GT | SOUTH | 2019 | 46.5
320 | VICTORIA POWER CTG 6 |  | VICTORIA_VICTORG6 | VICTORIA | GAS-CC | SOUTH | 2009 | 171
321 | VICTORIA POWER STG 5 |  | VICTORIA_VICTORG5 | VICTORIA | GAS-CC | SOUTH | 1963 | 132
322 | W A PARISH CTG 1 |  | WAP_WAPGT_1 | FORT BEND | GAS-GT | HOUSTON | 1967 | 13
323 | W A PARISH STG 1 |  | WAP_WAP_G1 | FORT BEND | GAS-ST | HOUSTON | 1958 | 169
324 | W A PARISH STG 2 |  | WAP_WAP_G2 | FORT BEND | GAS-ST | HOUSTON | 1958 | 169
325 | W A PARISH STG 3 |  | WAP_WAP_G3 | FORT BEND | GAS-ST | HOUSTON | 1961 | 246
326 | W A PARISH STG 4 |  | WAP_WAP_G4 | FORT BEND | GAS-ST | HOUSTON | 1968 | 536
327 | WICHITA FALLS CTG 1 |  | WFCOGEN_UNIT1 | WICHITA | GAS-CC | WEST | 1987 | 20
328 | WICHITA FALLS CTG 2 |  | WFCOGEN_UNIT2 | WICHITA | GAS-CC | WEST | 1987 | 20
329 | WICHITA FALLS CTG 3 |  | WFCOGEN_UNIT3 | WICHITA | GAS-CC | WEST | 1987 | 20
330 | WICHITA FALLS STG 4 |  | WFCOGEN_UNIT4 | WICHITA | GAS-CC | WEST | 1987 | 17
331 | WINCHESTER POWER PARK CTG 1 |  | WIPOPA_WPP_G1 | FAYETTE | GAS-GT | SOUTH | 2009 | 44
332 | WINCHESTER POWER PARK CTG 2 |  | WIPOPA_WPP_G2 | FAYETTE | GAS-GT | SOUTH | 2009 | 44
333 | WINCHESTER POWER PARK CTG 3 |  | WIPOPA_WPP_G3 | FAYETTE | GAS-GT | SOUTH | 2009 | 44
334 | WINCHESTER POWER PARK CTG 4 |  | WIPOPA_WPP_G4 | FAYETTE | GAS-GT | SOUTH | 2009 | 44
335 | WISE-TRACTEBEL POWER CTG 1 | 20INR0286 | WCPP_CT1 | WISE | GAS-CC | NORTH | 2004 | 245.4
336 | WISE-TRACTEBEL POWER CTG 2 | 20INR0286 | WCPP_CT2 | WISE | GAS-CC | NORTH | 2004 | 245.4
337 | WISE-TRACTEBEL POWER STG 1 | 20INR0286 | WCPP_ST1 | WISE | GAS-CC | NORTH | 2004 | 298
338 | WOLF HOLLOW 2 CTG 4 | 18INR0076 | WHCCS2_CT4 | HOOD | GAS-CC | NORTH | 2017 | 330.8
339 | WOLF HOLLOW 2 CTG 5 | 18INR0076 | WHCCS2_CT5 | HOOD | GAS-CC | NORTH | 2017 | 331.3
340 | WOLF HOLLOW 2 STG 6 | 18INR0076 | WHCCS2_STG6 | HOOD | GAS-CC | NORTH | 2017 | 470.8
341 | WOLF HOLLOW POWER CTG 1 |  | WHCCS_CT1 | HOOD | GAS-CC | NORTH | 2002 | 245.3
342 | WOLF HOLLOW POWER CTG 2 |  | WHCCS_CT2 | HOOD | GAS-CC | NORTH | 2002 | 245.3
343 | WOLF HOLLOW POWER STG |  | WHCCS_STG | HOOD | GAS-CC | NORTH | 2002 | 270
344 | NACOGDOCHES POWER (SEASONAL MOTHBALL ON 10/16/2020, AVAILABLE 5/15 THROUGH 10/15) |  | NACPW_UNIT1 | NACOGDOCHES | BIOMASS | NORTH | 2012 | 105
345 | BIOENERGY AUSTIN WALZEM RD LFG |  | DG_WALZE_4UNITS | BEXAR | BIOMASS | SOUTH | 2002 | 9.8
346 | BIOENERGY TEXAS COVEL GARDENS LFG |  | DG_MEDIN_1UNIT | BEXAR | BIOMASS | SOUTH | 2005 | 9.6
347 | FARMERS BRANCH LANDFILL GAS TO ENERGY |  | DG_HBR_2UNITS | DENTON | BIOMASS | NORTH | 2011 | 3.2
348 | GRAND PRAIRIE LFG |  | DG_TRIRA_1UNIT | DALLAS | BIOMASS | NORTH | 2015 | 4
349 | NELSON GARDENS LFG |  | DG_78252_4UNITS | BEXAR | BIOMASS | SOUTH | 2013 | 4.2
350 | SKYLINE LFG |  | DG_FERIS_4 UNITS | DALLAS | BIOMASS | NORTH | 2007 | 6.4
351 | WM RENEWABLE-AUSTIN LFG |  | DG_SPRIN_4UNITS | TRAVIS | BIOMASS | SOUTH | 2007 | 6.4
352 | WM RENEWABLE-BIOENERGY PARTNERS LFG |  | DG_BIOE_2UNITS | DENTON | BIOMASS | NORTH | 1988 | 6.2
353 | WM RENEWABLE-DFW GAS RECOVERY LFG |  | DG_BIO2_4UNITS | DENTON | BIOMASS | NORTH | 2009 | 6.4
354 | WM RENEWABLE-MESQUITE CREEK LFG |  | DG_FREIH_2UNITS | COMAL | BIOMASS | SOUTH | 2011 | 3.2
355 | WM RENEWABLE-WESTSIDE LFG |  | DG_WSTHL_3UNITS | PARKER | BIOMASS | NORTH | 2010 | 4.8
356 | Operational Capacity Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 65562.1
357
358 | Operational Resources (Hydro)
359 | AMISTAD HYDRO 1 |  | AMISTAD_AMISTAG1 | VAL VERDE | HYDRO | SOUTH | 1983 | 37.9
360 | AMISTAD HYDRO 2 |  | AMISTAD_AMISTAG2 | VAL VERDE | HYDRO | SOUTH | 1983 | 37.9
361 | AUSTIN HYDRO 1 |  | AUSTPL_AUSTING1 | TRAVIS | HYDRO | SOUTH | 1940 | 8
362 | AUSTIN HYDRO 2 |  | AUSTPL_AUSTING2 | TRAVIS | HYDRO | SOUTH | 1940 | 9
363 | BUCHANAN HYDRO 1 |  | BUCHAN_BUCHANG1 | LLANO | HYDRO | SOUTH | 1938 | 16
364 | BUCHANAN HYDRO 2 |  | BUCHAN_BUCHANG2 | LLANO | HYDRO | SOUTH | 1938 | 16
365 | BUCHANAN HYDRO 3 |  | BUCHAN_BUCHANG3 | LLANO | HYDRO | SOUTH | 1950 | 17
366 | DENISON DAM 1 |  | DNDAM_DENISOG1 | GRAYSON | HYDRO | NORTH | 1944 | 40
367 | DENISON DAM 2 |  | DNDAM_DENISOG2 | GRAYSON | HYDRO | NORTH | 1948 | 40
368 | EAGLE PASS HYDRO |  | EAGLE_HY_EAGLE_HY1 | MAVERICK | HYDRO | SOUTH | 2005 | 9.6
369 | FALCON HYDRO 1 |  | FALCON_FALCONG1 | STARR | HYDRO | SOUTH | 1954 | 12
370 | FALCON HYDRO 2 |  | FALCON_FALCONG2 | STARR | HYDRO | SOUTH | 1954 | 12
371 | FALCON HYDRO 3 |  | FALCON_FALCONG3 | STARR | HYDRO | SOUTH | 1954 | 12
372 | GRANITE SHOALS HYDRO 1 |  | WIRTZ_WIRTZ_G1 | BURNET | HYDRO | SOUTH | 1951 | 29
373 | GRANITE SHOALS HYDRO 2 |  | WIRTZ_WIRTZ_G2 | BURNET | HYDRO | SOUTH | 1951 | 29
374 | GUADALUPE BLANCO RIVER AUTH-CANYON |  | CANYHY_CANYHYG1 | COMAL | HYDRO | SOUTH | 1989 | 6
375 | INKS HYDRO 1 |  | INKSDA_INKS_G1 | LLANO | HYDRO | SOUTH | 1938 | 14
376 | MARBLE FALLS HYDRO 1 |  | MARBFA_MARBFAG1 | BURNET | HYDRO | SOUTH | 1951 | 21
377 | MARBLE FALLS HYDRO 2 |  | MARBFA_MARBFAG2 | BURNET | HYDRO | SOUTH | 1951 | 20
378 | MARSHALL FORD HYDRO 1 |  | MARSFO_MARSFOG1 | TRAVIS | HYDRO | SOUTH | 1941 | 36
379 | MARSHALL FORD HYDRO 2 |  | MARSFO_MARSFOG2 | TRAVIS | HYDRO | SOUTH | 1941 | 36
380 | MARSHALL FORD HYDRO 3 |  | MARSFO_MARSFOG3 | TRAVIS | HYDRO | SOUTH | 1941 | 36
381 | WHITNEY DAM HYDRO |  | WND_WHITNEY1 | BOSQUE | HYDRO | NORTH | 1953 | 22
382 | WHITNEY DAM HYDRO 2 |  | WND_WHITNEY2 | BOSQUE | HYDRO | NORTH | 1953 | 22
383 | Operational Capacity Total (Hydro) | [6 empty] | 538.4
384 | Hydro Capacity Contribution (Top 20 Hours) |  | HYDRO_CAP_CONT |  |  |  |  | 408.3
385
386 | Operational Hydro Resources, Settlement Only Distributed Generators (SODGs)
387 | ARLINGTON OUTLET HYDROELECTRIC FACILITY |  | DG_OAKHL_1UNIT | TARRANT | HYDRO | NORTH | 2014 | 1.4
388 | GUADALUPE BLANCO RIVER AUTH-LAKEWOOD TAP |  | DG_LKWDT_2UNITS | GONZALES | HYDRO | SOUTH | 1931 | 4.8
389 | GUADALUPE BLANCO RIVER AUTH-MCQUEENEY |  | DG_MCQUE_5UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 7.7
390 | GUADALUPE BLANCO RIVER AUTH-SCHUMANSVILLE |  | DG_SCHUM_2UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 3.6
391 | LEWISVILLE HYDRO-CITY OF GARLAND |  | DG_LWSVL_1UNIT | DENTON | HYDRO | NORTH | 1991 | 2.2
392 | Operational Hydro Resources Total, Settlement Only Distributed Generators (SODGs) | [6 empty] | 19.7
393 | Hydro SODG Capacity Contribution (Highest 20 Peak Load Hours) | [6 empty] | 14.9397
394
395 | Operational Capacity Unavailable due to Extended Outage or Derate |  | OPERATION_UNAVAIL |  |  |  |  | -135.0501
396 | Operational Capacity Total (Including Hydro) |  | OPERATION_TOTAL |  |  |  |  | 65850.2895
397
398 | Operational Resources (Switchable)
399 | ANTELOPE IC 1 |  | AEEC_ANTLP_1 | HALE | GAS-IC | PANHANDLE | 2016 | 56
400 | ANTELOPE IC 2 |  | AEEC_ANTLP_2 | HALE | GAS-IC | PANHANDLE | 2016 | 56
401 | ANTELOPE IC 3 |  | AEEC_ANTLP_3 | HALE | GAS-IC | PANHANDLE | 2016 | 56
402 | ELK STATION CTG 1 |  | AEEC_ELK_1 | HALE | GAS-GT | PANHANDLE | 2016 | 195
403 | ELK STATION CTG 2 |  | AEEC_ELK_2 | HALE | GAS-GT | PANHANDLE | 2016 | 195
404 | TENASKA FRONTIER STATION CTG 1 |  | FTR_FTR_G1 | GRIMES | GAS-CC | NORTH | 2000 | 180
405 | TENASKA FRONTIER STATION CTG 2 |  | FTR_FTR_G2 | GRIMES | GAS-CC | NORTH | 2000 | 180
406 | TENASKA FRONTIER STATION CTG 3 |  | FTR_FTR_G3 | GRIMES | GAS-CC | NORTH | 2000 | 180
407 | TENASKA FRONTIER STATION STG 4 |  | FTR_FTR_G4 | GRIMES | GAS-CC | NORTH | 2000 | 400
408 | TENASKA GATEWAY STATION CTG 1 |  | TGCCS_CT1 | RUSK | GAS-CC | NORTH | 2001 | 162
409 | TENASKA GATEWAY STATION CTG 2 |  | TGCCS_CT2 | RUSK | GAS-CC | NORTH | 2001 | 179
410 | TENASKA GATEWAY STATION CTG 3 |  | TGCCS_CT3 | RUSK | GAS-CC | NORTH | 2001 | 178
411 | TENASKA GATEWAY STATION STG 4 |  | TGCCS_UNIT4 | RUSK | GAS-CC | NORTH | 2001 | 389
412 | TENASKA KIAMICHI STATION 1CT101 |  | KMCHI_1CT101 | FANNIN | GAS-CC | NORTH | 2003 | 154
413 | TENASKA KIAMICHI STATION 1CT201 |  | KMCHI_1CT201 | FANNIN | GAS-CC | NORTH | 2003 | 151
414 | TENASKA KIAMICHI STATION 1ST |  | KMCHI_1ST | FANNIN | GAS-CC | NORTH | 2003 | 312
415 | TENASKA KIAMICHI STATION 2CT101 |  | KMCHI_2CT101 | FANNIN | GAS-CC | NORTH | 2003 | 149
416 | TENASKA KIAMICHI STATION 2CT201 |  | KMCHI_2CT201 | FANNIN | GAS-CC | NORTH | 2003 | 150
417 | TENASKA KIAMICHI STATION 2ST |  | KMCHI_2ST | FANNIN | GAS-CC | NORTH | 2003 | 317
418 | Switchable Capacity Total | [6 empty] | 3639
419
420 | Switchable Capacity Unavailable to ERCOT
421 | ANTELOPE IC 1 |  | AEEC_ANTLP_1_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | -56
422 | ANTELOPE IC 2 |  | AEEC_ANTLP_2_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | -56
423 | ANTELOPE IC 3 |  | AEEC_ANTLP_3_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | -56
424 | ELK STATION CTG 1 |  | AEEC_ELK_1_UNAVAIL | HALE | GAS-GT | PANHANDLE | 2017 | -195
425 | ELK STATION CTG 2 |  | AEEC_ELK_2_UNAVAIL | HALE | GAS-GT | PANHANDLE | 2017 | -195
426 | Switchable Capacity Unavailable to ERCOT |  | SWITCH_UNAVAIL |  |  |  |  | -558
427
428 | Available Mothball Capacity based on Owner's Return Probability |  | MOTH_AVAIL |  |  |  |  | 0
429
430 | Private-Use Network Capacity Contribution (Top 20 Hours) |  | PUN_CAP_CONT |  | GAS |  |  | 2731.3273
431 | Private-Use Network Forecast Adjustment (per Protocol 10.3.2.4) |  | PUN_CAP_ADJUST |  | GAS |  |  | 41
432
433 | Operational Resources (Wind)
434 | BAFFIN WIND UNIT1 |  | BAFFIN_UNIT1 | KENEDY | WIND-C | COASTAL | 2016 | 100
435 | BAFFIN WIND UNIT2 |  | BAFFIN_UNIT2 | KENEDY | WIND-C | COASTAL | 2016 | 102
436 | BRUENNING'S BREEZE A |  | BBREEZE_UNIT1 | WILLACY | WIND-C | COASTAL | 2017 | 120
437 | BRUENNING'S BREEZE B |  | BBREEZE_UNIT2 | WILLACY | WIND-C | COASTAL | 2017 | 108
438 | CAMERON COUNTY WIND |  | CAMWIND_UNIT1 | CAMERON | WIND-C | COASTAL | 2016 | 165
439 | CHAPMAN RANCH WIND IA (SANTA CRUZ) |  | SANTACRU_UNIT1 | NUECES | WIND-C | COASTAL | 2017 | 150.6
440 | CHAPMAN RANCH WIND IB (SANTA CRUZ) |  | SANTACRU_UNIT2 | NUECES | WIND-C | COASTAL | 2017 | 98.4
441 | GULF WIND I |  | TGW_T1 | KENEDY | WIND-C | COASTAL | 2009 | 141.6
442 | GULF WIND II |  | TGW_T2 | KENEDY | WIND-C | COASTAL | 2009 | 141.6
443 | KARANKAWA WIND 1A |  | KARAKAW1_UNIT1 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 103.3
444 | KARANKAWA WIND 1B |  | KARAKAW1_UNIT2 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 103.3
445 | KARANKAWA WIND 2 |  | KARAKAW2_UNIT3 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 100.4
446 | LOS VIENTOS WIND I |  | LV1_LV1A | WILLACY | WIND-C | COASTAL | 2013 | 200.1
447 | LOS VIENTOS WIND II |  | LV2_LV2 | WILLACY | WIND-C | COASTAL | 2013 | 201.6
448 | MAGIC VALLEY WIND (REDFISH) 1A |  | REDFISH_MV1A | WILLACY | WIND-C | COASTAL | 2012 | 99.8
449 | MAGIC VALLEY WIND (REDFISH) 1B |  | REDFISH_MV1B | WILLACY | WIND-C | COASTAL | 2012 | 103.5
450 | MIDWAY WIND |  | MIDWIND_UNIT1 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 162.8
451 | PAPALOTE CREEK WIND |  | PAP1_PAP1 | SAN PATRICIO | WIND-C | COASTAL | 2009 | 179.9
452 | PAPALOTE CREEK WIND II |  | COTTON_PAP2 | SAN PATRICIO | WIND-C | COASTAL | 2010 | 200.1
453 | PENASCAL WIND 1 |  | PENA_UNIT1 | KENEDY | WIND-C | COASTAL | 2009 | 160.8
454 | PENASCAL WIND 2 |  | PENA_UNIT2 | KENEDY | WIND-C | COASTAL | 2009 | 141.6
455 | PENASCAL WIND 3 |  | PENA3_UNIT3 | KENEDY | WIND-C | COASTAL | 2011 | 100.8
456 | PEYTON CREEK WIND |  | PEY_UNIT1 | MATAGORDA | WIND-C | COASTAL | 2020 | 151.2
457 | SAN ROMAN WIND |  | SANROMAN_WIND_1 | CAMERON | WIND-C | COASTAL | 2017 | 95.2
458 | STELLA WIND |  | STELLA_UNIT1 | KENEDY | WIND-C | COASTAL | 2018 | 201
459 | HARBOR WIND |  | DG_NUECE_6UNITS | NUECES | WIND-C | COASTAL | 2012 | 9
460 | BRISCOE WIND |  | BRISCOE_WIND | BRISCOE | WIND-P | PANHANDLE | 2015 | 149.8
461 | CANADIAN BREAKS WIND |  | CN_BRKS_UNIT_1 | OLDHAM | WIND-P | PANHANDLE | 2019 | 210.1
462 | COTTON PLAINS WIND |  | COTPLNS_COTTONPL | FLOYD | WIND-P | PANHANDLE | 2017 | 50.4
463 | DOUG COLBECK'S CORNER (CONWAY) B |  | GRANDVW1_COLB | CARSON | WIND-P | PANHANDLE | 2016 | 100.2
464 | DOUG COLBECK'S CORNER (CONWAY) A |  | GRANDVW1_COLA | CARSON | WIND-P | PANHANDLE | 2016 | 100.2
465 | FALVEZ ASTRA WIND |  | ASTRA_UNIT1 | RANDALL | WIND-P | PANHANDLE | 2017 | 163.2
466 | GRANDVIEW WIND 1 (CONWAY) GV1A |  | GRANDVW1_GV1A | CARSON | WIND-P | PANHANDLE | 2014 | 107.4
467 | GRANDVIEW WIND 1 (CONWAY) GV1B |  | GRANDVW1_GV1B | CARSON | WIND-P | PANHANDLE | 2014 | 103.8
468 | HEREFORD WIND G |  | HRFDWIND_WIND_G | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 99.9
469 | HEREFORD WIND V |  | HRFDWIND_WIND_V | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 100
470 | JUMBO ROAD WIND 1 |  | HRFDWIND_JRDWIND1 | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 146.2
471 | JUMBO ROAD WIND 2 |  | HRFDWIND_JRDWIND2 | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 153.6
472 | LONGHORN WIND NORTH U1 |  | LHORN_N_UNIT1 | FLOYD | WIND-P | PANHANDLE | 2015 | 100
473 | LONGHORN WIND NORTH U2 |  | LHORN_N_UNIT2 | FLOYD | WIND-P | PANHANDLE | 2015 | 100
474 | MARIAH DEL NORTE 1 |  | MARIAH_NORTE1 | PARMER | WIND-P | PANHANDLE | 2017 | 115.2
475 | MARIAH DEL NORTE 2 |  | MARIAH_NORTE2 | PARMER | WIND-P | PANHANDLE | 2017 | 115.2
476 | MCADOO WIND |  | MWEC_G1 | DICKENS | WIND-P | PANHANDLE | 2008 | 150
477 | MIAMI WIND G1 |  | MIAM1_G1 | GRAY | WIND-P | PANHANDLE | 2014 | 144.3
478 | MIAMI WIND G2 |  | MIAM1_G2 | GRAY | WIND-P | PANHANDLE | 2014 | 144.3
479 | OLD SETTLER WIND |  | COTPLNS_OLDSETLR | FLOYD | WIND-P | PANHANDLE | 2017 | 151.2
480 | PANHANDLE WIND 1 U1 |  | PH1_UNIT1 | CARSON | WIND-P | PANHANDLE | 2014 | 109.2
481 | PANHANDLE WIND 1 U2 |  | PH1_UNIT2 | CARSON | WIND-P | PANHANDLE | 2014 | 109.2
482 | PANHANDLE WIND 2 U1 |  | PH2_UNIT1 | CARSON | WIND-P | PANHANDLE | 2014 | 94.2
483 | PANHANDLE WIND 2 U2 |  | PH2_UNIT2 | CARSON | WIND-P | PANHANDLE | 2014 | 96.6
484 | ROUTE 66 WIND |  | ROUTE_66_WIND1 | CARSON | WIND-P | PANHANDLE | 2015 | 150
485 | SALT FORK 1 WIND U1 |  | SALTFORK_UNIT1 | DONLEY | WIND-P | PANHANDLE | 2017 | 64
486 | SALT FORK 1 WIND U2 |  | SALTFORK_UNIT2 | DONLEY | WIND-P | PANHANDLE | 2017 | 110
487 | SOUTH PLAINS WIND 1 U1 |  | SPLAIN1_WIND1 | FLOYD | WIND-P | PANHANDLE | 2015 | 102
488 | SOUTH PLAINS WIND 1 U2 |  | SPLAIN1_WIND2 | FLOYD | WIND-P | PANHANDLE | 2015 | 98
489 | SOUTH PLAINS WIND 2 U1 |  | SPLAIN2_WIND21 | FLOYD | WIND-P | PANHANDLE | 2016 | 148.5
490 | SOUTH PLAINS WIND 2 U2 |  | SPLAIN2_WIND22 | FLOYD | WIND-P | PANHANDLE | 2016 | 151.8
491 | SPINNING SPUR WIND TWO A |  | SSPURTWO_WIND_1 | OLDHAM | WIND-P | PANHANDLE | 2014 | 161
492 | SPINNING SPUR WIND TWO B |  | SSPURTWO_SS3WIND2 | OLDHAM | WIND-P | PANHANDLE | 2015 | 98
493 | SPINNING SPUR WIND TWO C |  | SSPURTWO_SS3WIND1 | OLDHAM | WIND-P | PANHANDLE | 2015 | 96
494 | WAKE WIND 1 |  | WAKEWE_G1 | DICKENS | WIND-P | PANHANDLE | 2016 | 114.9
495 | WAKE WIND 2 |  | WAKEWE_G2 | DICKENS | WIND-P | PANHANDLE | 2016 | 142.3
496 | WHIRLWIND ENERGY |  | WEC_WECG1 | FLOYD | WIND-P | PANHANDLE | 2007 | 57
497 | WOLF FLATS WIND (WIND MGT) |  | DG_TURL_UNIT1 | HALL | WIND-P | PANHANDLE | 2007 | 1
498 | ANACACHO WIND |  | ANACACHO_ANA | KINNEY | WIND-O | SOUTH | 2012 | 99.8
499 | BARTON CHAPEL WIND |  | BRTSW_BCW1 | JACK | WIND-O | NORTH | 2007 | 120
500 | BLUE SUMMIT WIND 1 A | 18INR0072 | BLSUMMIT_BLSMT1_5 | WILBARGER | WIND-O | WEST | 2013 | 8.8
501 | BLUE SUMMIT WIND 1 B | 18INR0072 | BLSUMMIT_BLSMT1_6 | WILBARGER | WIND-O | WEST | 2013 | 124.3
502 | BLUE SUMMIT WIND 2 A |  | BLSUMMIT_UNIT2_25 | WILBARGER | WIND-O | WEST | 2020 | 89.7
503 | BLUE SUMMIT WIND 2 B |  | BLSUMMIT_UNIT2_17 | WILBARGER | WIND-O | WEST | 2020 | 6.7
504 | BLUE SUMMIT WIND 3 A |  | BLSUMIT3_UNIT_17 | WILBARGER | WIND-O | WEST | 2020 | 13.4
505 | BLUE SUMMIT WIND 3 B |  | BLSUMIT3_UNIT_25 | WILBARGER | WIND-O | WEST | 2020 | 182.4
506 | BOBCAT BLUFF WIND |  | BCATWIND_WIND_1 | ARCHER | WIND-O | WEST | 2020 | 162
507 | BUCKTHORN WIND 1 A |  | BUCKTHRN_UNIT1 | ERATH | WIND-O | NORTH | 2017 | 44.9
508 | BUCKTHORN WIND 1 B |  | BUCKTHRN_UNIT2 | ERATH | WIND-O | NORTH | 2017 | 55.7
509 | BUFFALO GAP WIND 1 |  | BUFF_GAP_UNIT1 | TAYLOR | WIND-O | WEST | 2006 | 120.6
510 | BUFFALO GAP WIND 2_1 |  | BUFF_GAP_UNIT2_1 | TAYLOR | WIND-O | WEST | 2007 | 115.5
511 | BUFFALO GAP WIND 2_2 |  | BUFF_GAP_UNIT2_2 | TAYLOR | WIND-O | WEST | 2007 | 117
512 | BUFFALO GAP WIND 3 |  | BUFF_GAP_UNIT3 | TAYLOR | WIND-O | WEST | 2008 | 170.2
513 | BULL CREEK WIND U1 |  | BULLCRK_WND1 | BORDEN | WIND-O | WEST | 2009 | 88
514 | BULL CREEK WIND U2 |  | BULLCRK_WND2 | BORDEN | WIND-O | WEST | 2009 | 90
515 | CABEZON WIND (RIO BRAVO I WIND) 1 A |  | CABEZON_WIND1 | STARR | WIND-O | SOUTH | 2019 | 115.2
516 | CABEZON WIND (RIO BRAVO I WIND) 1 B |  | CABEZON_WIND2 | STARR | WIND-O | SOUTH | 2019 | 122.4
517 | CALLAHAN WIND |  | CALLAHAN_WND1 | CALLAHAN | WIND-O | WEST | 2004 | 114
518 | CAMP SPRINGS WIND 1 |  | CSEC_CSECG1 | SCURRY | WIND-O | WEST | 2007 | 130.5
519 | CAMP SPRINGS WIND 2 |  | CSEC_CSECG2 | SCURRY | WIND-O | WEST | 2007 | 120
520 | CAPRICORN RIDGE WIND 1 | 17INR0054 | CAPRIDGE_CR1 | STERLING | WIND-O | WEST | 2007 | 231.7
521 | CAPRICORN RIDGE WIND 2 | 17INR0054 | CAPRIDGE_CR2 | STERLING | WIND-O | WEST | 2007 | 149.5
522 | CAPRICORN RIDGE WIND 3 | 17INR0054 | CAPRIDGE_CR3 | STERLING | WIND-O | WEST | 2008 | 200.9
523 | CAPRICORN RIDGE WIND 4 | 17INR0061 | CAPRIDG4_CR4 | COKE | WIND-O | WEST | 2008 | 121.5
524 | CEDRO HILL WIND 1 |  | CEDROHIL_CHW1 | WEBB | WIND-O | SOUTH | 2010 | 75
525 | CEDRO HILL WIND 2 |  | CEDROHIL_CHW2 | WEBB | WIND-O | SOUTH | 2010 | 75
526 | CHAMPION WIND |  | CHAMPION_UNIT1 | NOLAN | WIND-O | WEST | 2008 | 126.5
527 | DERMOTT WIND 1_1 |  | DERMOTT_UNIT1 | SCURRY | WIND-O | WEST | 2017 | 126.5
528 | DERMOTT WIND 1_2 |  | DERMOTT_UNIT2 | SCURRY | WIND-O | WEST | 2017 | 126.5
529 | DESERT SKY WIND 1 | 17INR0070 | INDNENR_INDNENR | PECOS | WIND-O | WEST | 2002 | 85.1
530 | DESERT SKY WIND 2 | 17INR0070 | INDNENR_INDNENR_2 | PECOS | WIND-O | WEST | 2002 | 85.1
531 | ELBOW CREEK WIND |  | ELB_ELBCREEK | HOWARD | WIND-O | WEST | 2008 | 118.7
532 | ELECTRA WIND 1 |  | DIGBY_UNIT1 | WILBARGER | WIND-O | WEST | 2017 | 98.9
533 | ELECTRA WIND 2 |  | DIGBY_UNIT2 | WILBARGER | WIND-O | WEST | 2017 | 131.1
534 | FLAT TOP WIND I |  | FTWIND_UNIT_1 | MILLS | WIND-O | NORTH | 2018 | 200
535 | FLUVANNA RENEWABLE 1 A |  | FLUVANNA_UNIT1 | SCURRY | WIND-O | WEST | 2017 | 79.8
536 | FLUVANNA RENEWABLE 1 B |  | FLUVANNA_UNIT2 | SCURRY | WIND-O | WEST | 2017 | 75.6
537 | FOARD CITY WIND 1 A |  | FOARDCTY_UNIT1 | FOARD | WIND-O | WEST | 2019 | 186.5
538 | FOARD CITY WIND 1 B |  | FOARDCTY_UNIT2 | FOARD | WIND-O | WEST | 2019 | 163.8
539 | FOREST CREEK WIND |  | MCDLD_FCW1 | GLASSCOCK | WIND-O | WEST | 2007 | 124.2
540 | GOAT WIND |  | GOAT_GOATWIND | STERLING | WIND-O | WEST | 2008 | 80
541 | GOAT WIND 2 |  | GOAT_GOATWIN2 | STERLING | WIND-O | WEST | 2010 | 69.6
542 | GOLDTHWAITE WIND 1 |  | GWEC_GWEC_G1 | MILLS | WIND-O | NORTH | 2014 | 148.6
543 | GOPHER CREEK WIND 1 |  | GOPHER_UNIT1 | BORDEN | WIND-O | WEST | 2020 | 82
544 | GOPHER CREEK WIND 2 |  | GOPHER_UNIT2 | BORDEN | WIND-O | WEST | 2020 | 76
545 | GREEN MOUNTAIN WIND (BRAZOS) U1 |  | BRAZ_WND_WND1 | SCURRY | WIND-O | WEST | 2003 | 99
546 | GREEN MOUNTAIN WIND (BRAZOS) U2 |  | BRAZ_WND_WND2 | SCURRY | WIND-O | WEST | 2003 | 61
547 | GREEN PASTURES WIND I |  | GPASTURE_WIND_I | BAYLOR | WIND-O | WEST | 2015 | 150
548 | VERTIGO WIND (FORMERLY GREEN PASTURES WIND 2) |  | VERTIGO_WIND_I | BAYLOR | WIND-O | WEST | 2015 | 150
549 | GUNSIGHT MOUNTAIN WIND |  | GUNMTN_G1 | HOWARD | WIND-O | WEST | 2016 | 119.9
550 | HACKBERRY WIND |  | HWF_HWFG1 | SHACKELFORD | WIND-O | WEST | 2008 | 163.5
551 | HICKMAN (SANTA RITA WIND) 1 |  | HICKMAN_G1 | REGAN AND IRION | WIND-O | WEST | 2018 | 152.5
552 | HICKMAN (SANTA RITA WIND) 2 |  | HICKMAN_G2 | REGAN AND IRION | WIND-O | WEST | 2018 | 147.5
553 | HIDALGO & STARR WIND 11 |  | MIRASOLE_MIR11 | HIDALGO | WIND-O | SOUTH | 2016 | 52
554 | HIDALGO & STARR WIND 12 |  | MIRASOLE_MIR12 | HIDALGO | WIND-O | SOUTH | 2016 | 98
555 | HIDALGO & STARR WIND 21 |  | MIRASOLE_MIR21 | HIDALGO | WIND-O | SOUTH | 2016 | 100
556 | HORSE CREEK WIND 1 |  | HORSECRK_UNIT1 | HASKELL | WIND-O | WEST | 2017 | 131.1
557 | HORSE CREEK WIND 2 |  | HORSECRK_UNIT2 | HASKELL | WIND-O | WEST | 2017 | 98.9
558 | HORSE HOLLOW WIND 1 | 17INR0052 | H_HOLLOW_WND1 | TAYLOR | WIND-O | WEST | 2005 | 230
559 | HORSE HOLLOW WIND 2 | 17INR0052 | HHOLLOW2_WIND1 | TAYLOR | WIND-O | WEST | 2006 | 184
560 | HORSE HOLLOW WIND 3 | 17INR0052 | HHOLLOW3_WND_1 | TAYLOR | WIND-O | WEST | 2006 | 241.4
561 | HORSE HOLLOW WIND 4 | 17INR0052 | HHOLLOW4_WND1 | TAYLOR | WIND-O | WEST | 2006 | 115
562 | INADALE WIND 1 |  | INDL_INADALE1 | NOLAN | WIND-O | WEST | 2008 | 95
563 | INADALE WIND 2 |  | INDL_INADALE2 | NOLAN | WIND-O | WEST | 2008 | 102
564 | INDIAN MESA WIND |  | INDNNWP_INDNNWP2 | PECOS | WIND-O | WEST | 2001 | 91.8
565 | JAVELINA I WIND 18 |  | BORDAS_JAVEL18 | WEBB | WIND-O | SOUTH | 2015 | 19.7
566 | JAVELINA I WIND 20 |  | BORDAS_JAVEL20 | WEBB | WIND-O | SOUTH | 2015 | 230
567 | JAVELINA II WIND 1 |  | BORDAS2_JAVEL2_A | WEBB | WIND-O | SOUTH | 2017 | 96
568 | JAVELINA II WIND 2 |  | BORDAS2_JAVEL2_B | WEBB | WIND-O | SOUTH | 2017 | 74
569 | JAVELINA II WIND 3 |  | BORDAS2_JAVEL2_C | WEBB | WIND-O | SOUTH | 2017 | 30
570 | KEECHI WIND |  | KEECHI_U1 | JACK | WIND-O | NORTH | 2015 | 110
571 | KING MOUNTAIN WIND (NE) |  | KING_NE_KINGNE | UPTON | WIND-O | WEST | 2001 | 79.7
572 | KING MOUNTAIN WIND (NW) |  | KING_NW_KINGNW | UPTON | WIND-O | WEST | 2001 | 79.7
573 | KING MOUNTAIN WIND (SE) |  | KING_SE_KINGSE | UPTON | WIND-O | WEST | 2001 | 40.5
574 | KING MOUNTAIN WIND (SW) |  | KING_SW_KINGSW | UPTON | WIND-O | WEST | 2001 | 79.7
575 | LANGFORD WIND POWER |  | LGD_LANGFORD | TOM GREEN | WIND-O | WEST | 2009 | 160
576 | LOCKETT WIND FARM |  | LOCKETT_UNIT1 | WILBARGER | WIND-O | WEST | 2019 | 183.7
577 | LOGANS GAP WIND I U1 |  | LGW_UNIT1 | COMANCHE | WIND-O | NORTH | 2015 | 106.3
578 | LOGANS GAP WIND I U2 |  | LGW_UNIT2 | COMANCHE | WIND-O | NORTH | 2015 | 103.8
579 | LONE STAR WIND 1 (MESQUITE) |  | LNCRK_G83 | SHACKELFORD | WIND-O | WEST | 2006 | 194
580 | LONE STAR WIND 2 (POST OAK) U1 |  | LNCRK2_G871 | SHACKELFORD | WIND-O | WEST | 2007 | 98
581 | LONE STAR WIND 2 (POST OAK) U2 |  | LNCRK2_G872 | SHACKELFORD | WIND-O | WEST | 2007 | 100
582 | LORAINE WINDPARK I |  | LONEWOLF_G1 | MITCHELL | WIND-O | WEST | 2010 | 49.5
583 | LORAINE WINDPARK II |  | LONEWOLF_G2 | MITCHELL | WIND-O | WEST | 2010 | 51
584 | LORAINE WINDPARK III |  | LONEWOLF_G3 | MITCHELL | WIND-O | WEST | 2011 | 25.5
585 | LORAINE WINDPARK IV |  | LONEWOLF_G4 | MITCHELL | WIND-O | WEST | 2011 | 24
586 | LOS VIENTOS III WIND |  | LV3_UNIT_1 | STARR | WIND-O | SOUTH | 2015 | 200
587 | LOS VIENTOS IV WIND |  | LV4_UNIT_1 | STARR | WIND-O | SOUTH | 2016 | 200
588 | LOS VIENTOS V WIND |  | LV5_UNIT_1 | STARR | WIND-O | SOUTH | 2016 | 110
589 | MESQUITE CREEK WIND 1 |  | MESQCRK_WND1 | DAWSON | WIND-O | WEST | 2015 | 105.6
590 | MESQUITE CREEK WIND 2 |  | MESQCRK_WND2 | DAWSON | WIND-O | WEST | 2015 | 105.6
591 | NIELS BOHR WIND A (BEARKAT WIND A) |  | NBOHR_UNIT1 | GLASSCOCK | WIND-O | WEST | 2018 | 196.6
592 | NOTREES WIND 1 |  | NWF_NWF1 | WINKLER | WIND-O | WEST | 2009 | 92.6
593 | NOTREES WIND 2 |  | NWF_NWF2 | WINKLER | WIND-O | WEST | 2009 | 60
594 | OCOTILLO WIND |  | OWF_OWF | HOWARD | WIND-O | WEST | 2008 | 58.8
595 | PANTHER CREEK WIND 1 |  | PC_NORTH_PANTHER1 | HOWARD | WIND-O | WEST | 2008 | 142.5
596 | PANTHER CREEK WIND 2 |  | PC_SOUTH_PANTHER2 | HOWARD | WIND-O | WEST | 2019 | 115.5
597 | PANTHER CREEK WIND 3 | 21INR0449 | PC_SOUTH_PANTHER3 | HOWARD | WIND-O | WEST | 2009 | 199.5
598 | PECOS WIND 1 (WOODWARD) |  | WOODWRD1_WOODWRD1 | PECOS | WIND-O | WEST | 2001 | 90
599 | PECOS WIND 2 (WOODWARD) |  | WOODWRD2_WOODWRD2 | PECOS | WIND-O | WEST | 2001 | 86
600 | PYRON WIND 1 |  | PYR_PYRON1 | NOLAN | WIND-O | WEST | 2008 | 121.5
601 | PYRON WIND 2 |  | PYR_PYRON2 | NOLAN | WIND-O | WEST | 2008 | 127.5
602 | RANCHERO WIND |  | RANCHERO_UNIT1 | CROCKETT | WIND-O | WEST | 2020 | 150
603 | RANCHERO WIND |  | RANCHERO_UNIT2 | CROCKETT | WIND-O | WEST | 2020 | 150
604 | RATTLESNAKE I WIND ENERGY CENTER G1 |  | RSNAKE_G1 | GLASSCOCK | WIND-O | WEST | 2015 | 104.3
605 | RATTLESNAKE I WIND ENERGY CENTER G2 |  | RSNAKE_G2 | GLASSCOCK | WIND-O | WEST | 2015 | 103
606 | RED CANYON WIND |  | RDCANYON_RDCNY1 | BORDEN | WIND-O | WEST | 2006 | 89.6
607 | ROCK SPRINGS VAL VERDE WIND (FERMI) 1 |  | FERMI_WIND1 | VAL VERDE | WIND-O | WEST | 2017 | 121.9
608 | ROCK SPRINGS VAL VERDE WIND (FERMI) 2 |  | FERMI_WIND2 | VAL VERDE | WIND-O | WEST | 2017 | 27.4
609 | ROSCOE WIND |  | TKWSW1_ROSCOE | NOLAN | WIND-O | WEST | 2008 | 114
610 | ROSCOE WIND 2A |  | TKWSW1_ROSCOE2A | NOLAN | WIND-O | WEST | 2008 | 95
611 | RTS WIND |  | RTS_U1 | MCCULLOCH | WIND-O | SOUTH | 2018 | 160
612 | SAND BLUFF WIND | 20INR0296 | MCDLD_SBW1 | GLASSCOCK | WIND-O | WEST | 2008 | 90
613 | SENDERO WIND ENERGY |  | EXGNSND_WIND_1 | JIM HOGG | WIND-O | SOUTH | 2015 | 76
614 | SEYMOUR HILLS WIND (S_HILLS WIND) |  | S_HILLS_UNIT1 | BAYLOR | WIND-O | WEST | 2019 | 30.2
615 | SENATE WIND |  | SENATEWD_UNIT1 | JACK | WIND-O | NORTH | 2012 | 150
616 | SHANNON WIND |  | SHANNONW_UNIT_1 | CLAY | WIND-O | WEST | 2015 | 204.1
617 | SHERBINO 1 WIND | 19INR0120 | KEO_KEO_SM1 | PECOS | WIND-O | WEST | 2008 | 150
618 | SHERBINO 2 WIND | 19INR0120 | KEO_SHRBINO2 | PECOS | WIND-O | WEST | 2020 | 132
619 | SILVER STAR WIND | 18INR0064 | FLTCK_SSI | ERATH | WIND-O | NORTH | 2008 | 52.8
620 | SNYDER WIND | 20INR0257 | ENAS_ENA1 | SCURRY | WIND-O | WEST | 2007 | 63
621 | SOUTH TRENT WIND |  | STWF_T1 | NOLAN | WIND-O | WEST | 2008 | 98.2
622 | STANTON WIND ENERGY |  | SWEC_G1 | MARTIN | WIND-O | WEST | 2008 | 120
623 | STEPHENS RANCH WIND 1 |  | SRWE1_UNIT1 | BORDEN | WIND-O | WEST | 2014 | 211.2
624 | STEPHENS RANCH WIND 2 |  | SRWE1_SRWE2 | BORDEN | WIND-O | WEST | 2015 | 164.7
625 | SWEETWATER WIND 1 | 18INR0073 | SWEETWND_WND1 | NOLAN | WIND-O | WEST | 2003 | 42.5
626 | SWEETWATER WIND 2A | 17INR0068 | SWEETWN2_WND24 | NOLAN | WIND-O | WEST | 2006 | 16.8
627 | SWEETWATER WIND 2B | 17INR0068 | SWEETWN2_WND2 | NOLAN | WIND-O | WEST | 2004 | 110.8
628 | SWEETWATER WIND 3A |  | SWEETWN3_WND3A | NOLAN | WIND-O | WEST | 2011 | 33.6
629 | SWEETWATER WIND 3B |  | SWEETWN3_WND3B | NOLAN | WIND-O | WEST | 2011 | 118.6
630 | SWEETWATER WIND 4-5 |  | SWEETWN5_WND5 | NOLAN | WIND-O | WEST | 2007 | 85
631 | SWEETWATER WIND 4-4B |  | SWEETWN4_WND4B | NOLAN | WIND-O | WEST | 2007 | 112
632 | SWEETWATER WIND 4-4A |  | SWEETWN4_WND4A | NOLAN | WIND-O | WEST | 2007 | 125
633 | TAHOKA WIND 1 |  | TAHOKA_UNIT_1 | LYNN | WIND-O | WEST | 2019 | 150
634 | TAHOKA WIND 2 |  | TAHOKA_UNIT_2 | LYNN | WIND-O | WEST | 2019 | 150
635 | TEXAS BIG SPRING WIND A |  | SGMTN_SIGNALMT | HOWARD | WIND-O | WEST | 1999 | 27.7
636 | TEXAS BIG SPRING WIND B |  | SGMTN_SIGNALM2 | HOWARD | WIND-O | WEST | 1999 | 6.6
637 | TORRECILLAS WIND 1 |  | TORR_UNIT1_25 | WEBB | WIND-O | SOUTH | 2019 | 150
638 | TORRECILLAS WIND 2 |  | TORR_UNIT2_23 | WEBB | WIND-O | SOUTH | 2019 | 23
639 | TORRECILLAS WIND 3 |  | TORR_UNIT2_25 | WEBB | WIND-O | SOUTH | 2019 | 127.5
640 | TRENT WIND | 17INR0069 | TRENT_TRENT | NOLAN | WIND-O | WEST | 2001 | 150
641 | TRINITY HILLS WIND 1 | 20INR0019 | TRINITY_TH1_BUS1 | ARCHER | WIND-O | WEST | 2012 | 103.4
642 | TRINITY HILLS WIND 2 | 20INR0019 | TRINITY_TH1_BUS2 | ARCHER | WIND-O | WEST | 2012 | 94.6
643 | TURKEY TRACK WIND |  | TTWEC_G1 | NOLAN | WIND-O | WEST | 2008 | 169.5
644 | TYLER BLUFF WIND |  | TYLRWIND_UNIT1 | COOKE | WIND-O | NORTH | 2017 | 125.6
645 | WHITETAIL WIND |  | EXGNWTL_WIND_1 | WEBB | WIND-O | SOUTH | 2012 | 92.3
646 | WINDTHORST 2 WIND |  | WNDTHST2_UNIT1 | ARCHER | WIND-O | WEST | 2014 | 67.6
647 | WKN MOZART WIND |  | MOZART_WIND_1 | KENT | WIND-O | WEST | 2012 | 30
648 | WILLOW SPRINGS WIND A |  | SALVTION_UNIT1 | HASKELL | WIND-O | WEST | 2017 | 125
649 | WILLOW SPRINGS WIND B |  | SALVTION_UNIT2 | HASKELL | WIND-O | WEST | 2017 | 125
650 | WILSON RANCH (INFINITY LIVE OAK WIND) |  | WL_RANCH_UNIT1 | SCHLEICHER | WIND-O | WEST | 2020 | 199.5
651 | WOLF RIDGE WIND | 21INR0511 | WHTTAIL_WR1 | COOKE | WIND-O | NORTH | 2008 | 112.5
652 | TSTC WEST TEXAS WIND |  | DG_ROSC2_1UNIT | NOLAN | WIND-O | WEST | 2008 | 2
653 | Operational Capacity Total (Wind) | [6 empty] | 24962.4
654
655 | Operational Wind Capacity Sub-total (Coastal Counties) |  | WIND_OPERATIONAL_C |  |  |  |  | 3441.6
656 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PEAK_PCT_C | % |  |  |  | 35
657
658 | Operational Wind Capacity Sub-total (Panhandle Counties) |  | WIND_OPERATIONAL_P |  |  |  |  | 4408.7
659 | Wind Peak Average Capacity Percentage (Panhandle) |  | WIND_PEAK_PCT_P | % |  |  |  | 43
660
661 | Operational Wind Capacity Sub-total (Other Counties) |  | WIND_OPERATIONAL_O |  |  |  |  | 17112.1
662 | Wind Peak Average Capacity Percentage (Other) |  | WIND_PEAK_PCT_O | % |  |  |  | 38
663
664 | Operational Resources (Solar)
665 | ACACIA SOLAR |  | ACACIA_UNIT_1 | PRESIDIO | SOLAR | WEST | 2012 | 10
666 | BHE SOLAR PEARL PROJECT (SIRIUS 2) |  | SIRIUS_UNIT2 | PECOS | SOLAR | WEST | 2017 | 49.1
667 | BLUEBELL SOLAR (CAPRICORN RIDGE SOLAR) |  | CAPRIDG4_BB_PV | STERLING | SOLAR | WEST | 2019 | 30
668 | BNB LAMESA SOLAR (PHASE I) |  | LMESASLR_UNIT1 | DAWSON | SOLAR | WEST | 2018 | 101.6
669 | BNB LAMESA SOLAR (PHASE II) |  | LMESASLR_IVORY | DAWSON | SOLAR | WEST | 2018 | 50
670 | CASTLE GAP SOLAR |  | CASL_GAP_UNIT1 | UPTON | SOLAR | WEST | 2018 | 180
671 | FOWLER RANCH |  | FWLR_SLR_UNIT1 | CRANE | SOLAR | WEST | 2020 | 152.5
672 | FS BARILLA SOLAR-PECOS |  | HOVEY_UNIT1 | PECOS | SOLAR | WEST | 2015 | 22
673 | FS EAST PECOS SOLAR |  | BOOTLEG_UNIT1 | PECOS | SOLAR | WEST | 2017 | 121.1
674 | HOLSTEIN SOLAR 1 |  | HOLSTEIN_SOLAR1 | NOLAN | SOLAR | WEST | 2020 | 102.2
675 | HOLSTEIN SOLAR 2 |  | HOLSTEIN_SOLAR2 | NOLAN | SOLAR | WEST | 2020 | 102.3
676 | LAPETUS SOLAR |  | LAPETUS_UNIT_1 | ANDREWS | SOLAR | WEST | 2020 | 100.7
677 | OBERON SOLAR |  | OBERON_UNIT_1 | ECTOR | SOLAR | WEST | 2020 | 180
678 | OCI ALAMO 1 SOLAR |  | OCI_ALM1_UNIT1 | BEXAR | SOLAR | SOUTH | 2013 | 39.2
679 | OCI ALAMO 4 SOLAR-BRACKETVILLE |  | ECLIPSE_UNIT1 | KINNEY | SOLAR | SOUTH | 2014 | 37.6
680 | OCI ALAMO 5 (DOWNIE RANCH) |  | HELIOS_UNIT1 | UVALDE | SOLAR | SOUTH | 2015 | 100
681 | OCI ALAMO 6 (SIRIUS/WEST TEXAS) |  | SIRIUS_UNIT1 | PECOS | SOLAR | WEST | 2017 | 110.2
682 | OCI ALAMO 7 (PAINT CREEK) |  | SOLARA_UNIT1 | HASKELL | SOLAR | WEST | 2016 | 112
683 | PHOEBE SOLAR 1 |  | PHOEBE_UNIT1 | WINKLER | SOLAR | WEST | 2019 | 125.1
684 | PHOEBE SOLAR 2 |  | PHOEBE_UNIT2 | WINKLER | SOLAR | WEST | 2019 | 128.1
685 | PROSPERO SOLAR 1 |  | PROSPERO_UNIT1 | ANDREWS | SOLAR | WEST | 2020 | 153.6
686 | PROSPERO SOLAR 2 |  | PROSPERO_UNIT2 | ANDREWS | SOLAR | WEST | 2020 | 150
687 | QUEEN SOLAR PHASE I |  | QUEEN_SL_SOLAR1 | UPTON | SOLAR | WEST | 2020 | 102.5
688 | QUEEN SOLAR PHASE I |  | QUEEN_SL_SOLAR2 | UPTON | SOLAR | WEST | 2020 | 102.5
689 | QUEEN SOLAR PHASE II |  | QUEEEN_SL_SOLAR3 | UPTON | SOLAR | WEST | 2020 | 102.5
690 | QUEEN SOLAR PHASE II |  | QUEEEN_SL_SOLAR4 | UPTON | SOLAR | WEST | 2020 | 97.5
691 | RE ROSEROCK SOLAR 1 |  | REROCK_UNIT1 | PECOS | SOLAR | WEST | 2016 | 78.8
692 | RE ROSEROCK SOLAR 2 |  | REROCK_UNIT2 | PECOS | SOLAR | WEST | 2016 | 78.8
693 | RIGGINS (SE BUCKTHORN WESTEX SOLAR) |  | RIGGINS_UNIT1 | PECOS | SOLAR | WEST | 2018 | 150
694 | SOLAIREHOLMAN 1 |  | LASSO_UNIT1 | BREWSTER | SOLAR | WEST | 2018 | 50
695 | SP-TX-12-PHASE B |  | SPTX12B_UNIT1 | UPTON | SOLAR | WEST | 2017 | 157.5
696 | WAYMARK SOLAR |  | WAYMARK_UNIT1 | UPTON | SOLAR | WEST | 2018 | 182
697 | WEBBERVILLE SOLAR |  | WEBBER_S_WSP1 | TRAVIS | SOLAR | SOUTH | 2011 | 26.7
698 | WEST OF PECOS SOLAR |  | W_PECOS_UNIT1 | REEVES | SOLAR | WEST | 2019 | 101
699 | ALEXIS SOLAR |  | DG_ALEXIS_ALEXIS | BROOKS | SOLAR | SOUTH | 2019 | 10
700 | BECK 1 |  | DG_CECSOLAR_DG_BECK1 | BEXAR | SOLAR | SOUTH | 2016 | 1
701 | BLUE WING 1 SOLAR |  | DG_BROOK_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.6
702 | BLUE WING 2 SOLAR |  | DG_ELMEN_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.3
703 | BOVINE SOLAR LLC |  | DG_BOVINE_BOVINE | AUSTIN | SOLAR | SOUTH | 2018 | 5
704 | BOVINE SOLAR LLC |  | DG_BOVINE2_BOVINE2 | AUSTIN | SOLAR | SOUTH | 2018 | 5
705 | BRONSON SOLAR I |  | DG_BRNSN_BRNSN | FORT BEND | SOLAR | HOUSTON | 2018 | 5
706 | BRONSON SOLAR II |  | DG_BRNSN2_BRNSN2 | FORT BEND | SOLAR | HOUSTON | 2018 | 5
707 | CASCADE SOLAR I |  | DG_CASCADE_CASCADE | WHARTON | SOLAR | SOUTH | 2018 | 5
708 | CASCADE SOLAR II |  | DG_CASCADE2_CASCADE2 | WHARTON | SOLAR | SOUTH | 2018 | 5
709 | CHISUM SOLAR |  | DG_CHISUM_CHISUM | LAMAR | SOLAR | NORTH | 2018 | 10
710 | COMMERCE_SOLAR |  | DG_ X443PV1_SWRI_PV1 | BEXAR | SOLAR | SOUTH | 2019 | 5
711 | EDDY SOLAR II |  | DG_EDDYII_EDDYII | MCLENNAN | SOLAR | NORTH | 2018 | 10
712 | FIFTH GENERATION SOLAR 1 |  | DG_FIFTHGS1_FGSOLAR1 | TRAVIS | SOLAR | SOUTH | 2016 | 1.6
713 | GRIFFIN SOLAR |  | DG_GRIFFIN_GRIFFIN | MCLEENNAN | SOLAR | NORTH | 2019 | 5
714 | HIGHWAY 56 |  | DG_HWY56_HWY56 | GRAYSON | SOLAR | NORTH | 2017 | 5.3
715 | HM SEALY SOLAR 1 |  | DG_SEALY_1UNIT | AUSTIN | SOLAR | SOUTH | 2015 | 1.6
716 | LAMPWICK SOLAR |  | DG_LAMPWICK_LAMPWICK | MENARD | SOLAR | SOUTH | 2019 | 7.5
717 | LEON |  | DG_LEON_LEON | HUNT | SOLAR | NORTH | 2017 | 10
718 | MARLIN |  | DG_MARLIN_MARLIN | FALLS | SOLAR | NORTH | 2017 | 5.3
719 | MARS SOLAR (DG) |  | DG_MARS_MARS | WEBB | SOLAR | SOUTH | 2019 | 10
720 | NORTH GAINESVILLE |  | DG_NGNSVL_NGAINESV | COOKE | SOLAR | NORTH | 2017 | 5.2
721 | OCI ALAMO 2 SOLAR-ST. HEDWIG |  | DG_STHWG_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 4.4
722 | OCI ALAMO 3-WALZEM SOLAR |  | DG_WALZM_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 5.5
723 | POWERFIN KINGSBERY |  | DG_PFK_PFKPV | TRAVIS | SOLAR | SOUTH | 2017 | 2.6
724 | RENEWABLE ENERGY ALTERNATIVES-CCS1 |  | DG_COSERVSS_CSS1 | DENTON | SOLAR | NORTH | 2015 | 2
725 | STERLING |  | DG_STRLING_STRLING | HUNT | SOLAR | NORTH | 2018 | 10
726 | SUNEDISON RABEL ROAD SOLAR |  | DG_VALL1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9
727 | SUNEDISON VALLEY ROAD SOLAR |  | DG_VALL2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9
728 | SUNEDISON CPS3 SOMERSET 1 SOLAR |  | DG_SOME1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5.6
729 | SUNEDISON SOMERSET 2 SOLAR |  | DG_SOME2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5
730 | WALNUT SPRINGS |  | DG_WLNTSPRG_1UNIT | BOSQUE | SOLAR | NORTH | 2016 | 10
731 | WEST MOORE II |  | DG_WMOOREII_WMOOREII | GRAYSON | SOLAR | NORTH | 2018 | 5
732 | WHITESBORO |  | DG_WBORO_WHTSBORO | GRAYSON | SOLAR | NORTH | 2017 | 5
733 | WHITESBORO II |  | DG_WBOROII_WHBOROII | GRAYSON | SOLAR | NORTH | 2017 | 5
734 | WHITEWRIGHT |  | DG_WHTRT_WHTRGHT | FANNIN | SOLAR | NORTH | 2017 | 10
735 | WHITNEY SOLAR |  | DG_WHITNEY_SOLAR1 | BOSQUE | SOLAR | NORTH | 2017 | 10
736 | YELLOW JACKET SOLAR |  | DG_YLWJACKET_YLWJACKET | BOSQUE | SOLAR | NORTH | 2018 | 5
737 | Operational Capacity Total (Solar) | [6 empty] | 3624.4
738 | Solar Peak Average Capacity Percentage |  | SOLAR_PEAK_PCT | % |  |  |  | 66
739
740 | Operational Resources (Storage)
741 | BLUE SUMMIT BATTERY |  | BLSUMMIT_BATTERY | WILBARGER | STORAGE | WEST | 2017 | 30
742 | BRP ODESSA SW (DGR) |  | BRPODESA_UNIT1 | ECTOR | STORAGE | WEST | 2020 | 10
743 | CASTLE GAP BATTERY |  | CASL_GAP_BATTERY1 | UPTON | STORAGE | WEST | 2019 | 9.9
744 | FLAT TOP BATTERY (DGR) |  | FLTBES_BESS1 | REEVES | STORAGE | WEST | 2020 | 9.9
745 | INADALE ESS |  | INDL_ESS | NOLAN | STORAGE | WEST | 2018 | 9.9
746 | NOTREES BATTERY FACILITY |  | NWF_NBS | WINKLER | STORAGE | WEST | 2013 | 33.7
747 | OCI ALAMO 1 |  | OCI_ALM1_ASTRO1 | BEXAR | STORAGE | SOUTH | 2016 | 1
748 | PORT LAVACA BATTERY (DGR) |  | PTLBES_BESS1 | CALHOUN | STORAGE | SOUTH | 2019 | 9.9
749 | PROSPECT STORAGE (DGR) |  | WCOLLDG_BSS_U1 | BRAZORIA | STORAGE | HOUSTON | 2019 | 9.9
750 | PYRON ESS |  | PYR_ESS | SCURRY | STORAGE | WEST | 2018 | 9.9
751 | RABBIT HILL ENERGY STORAGE PROJECT (DGR) |  | RHESS2_ESS_1 | WILLIAMSON | STORAGE | SOUTH | 2020 | 9.9
752 | WORSHAM BATTERY (DGR) |  | WRSBES_BESS1 | REEVES | STORAGE | WEST | 2020 | 9.9
753 | KINGSBERY ENERGY STORAGE SYSTEM |  | DG_KB_ESS_KB_ESS | TRAVIS | STORAGE | SOUTH | 2017 | 1.5
754 | MU ENERGY STORAGE SYSTEM |  | DG_MU_ESS_MU_ESS | TRAVIS | STORAGE | SOUTH | 2018 | 1.5
755 | TOS BATTERY STORAGE (DGR) |  | TOSBATT_UNIT1 | MIDLAND | STORAGE | WEST | 2017 | 2
756 | YOUNICOS FACILITY |  | DG_YOUNICOS_YINC1_1 | TRAVIS | STORAGE | SOUTH | 2015 | 2
757 | Operational Capacity Total (Storage) | [6 empty] | 160.9
758 | Storage Peak Average Capacity Percentage |  | STORAGE_PEAK_PCT | % |  |  |  | 0
759
760 | Reliability Must-Run (RMR) Capacity |  | RMR_CAP_CONT |  |  |  |  | 0
761
762 | Capacity Pending Retirement |  | PENDRETIRE_CAP |  |  |  |  | 0
763
764 | Non-Synchronous Tie Resources
765 | EAST TIE |  | DC_E | FANNIN | OTHER | NORTH |  | 600
766 | NORTH TIE |  | DC_N | WILBARGER | OTHER | WEST |  | 220
767 | LAREDO VFT TIE |  | DC_L | WEBB | OTHER | SOUTH |  | 100
768 | SHARYLAND RAILROAD TIE |  | DC_R | HIDALGO | OTHER | SOUTH |  | 300
769 | Non-Synchronous Ties Total | [6 empty] | 1220
770 | Non-Synchronous Ties Peak Average Capacity Percentage |  | DCTIE_PEAK_PCT | % |  |  |  | 68.65
771
772 | Planned Thermal Resources with Executed SGIA, Air Permit, GHG Permit and Proof of Adequate Water Supplies
773 | AIR PRODUCTS GCA | 21INR0012 |  | GALVESTON | GAS-ST | HOUSTON | 2022 | 0
774 | MIRAGE | 17INR0022 |  | HARRIS | GAS-GT | HOUSTON | 2020 | 0
775 | PES1 | 20INR0206 |  | HARRIS | GAS-GT | HOUSTON | 2020 | 0
776 | TOPAZ POWER PLANT | 20INR0231 |  | GALVESTON | GAS-GT | HOUSTON | 2021 | 0
777 | Planned Capacity Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 0
778
779 | Planned Wind Resources with Executed SGIA
780 | CHALUPA WIND | 20INR0042 |  | CAMERON | WIND-C | COASTAL | 2020 | 0
781 | CRANEL WIND | 19INR0112 |  | REFUGIO | WIND-C | COASTAL | 2020 | 0
782 | EAST RAYMOND WIND | 18INR0059 |  | WILLACY | WIND-C | COASTAL | 2021 | 0
783 | EL ALGODON ALTO W | 15INR0034 |  | SAN PATRICIO | WIND-C | COASTAL | 2021 | 0
784 | ESPIRITU WIND | 17INR0031 |  | CAMERON | WIND-C | COASTAL | 2020 | 0
785 | LAS MAJADAS WIND | 17INR0035 |  | WILLACY | WIND-C | COASTAL | 2020 | 0
786 | MONTE ALTO I | 19INR0022 |  | WILLACY | WIND-C | COASTAL | 2021 | 0
787 | PALMAS ALTAS WIND | 17INR0037 |  | CAMERON | WIND-C | COASTAL | 2020 | 144.9
788 | SHAFFER (PATRIOT WIND/PETRONILLA) | 11INR0062 |  | NUECES | WIND-C | COASTAL | 2020 | 226
789 | WEST RAYMOND (EL TRUENO) WIND | 20INR0088 |  | WILLACY | WIND-C | COASTAL | 2020 | 0
790 | HART WIND | 16INR0033 |  | CASTRO | WIND-P | PANHANDLE | 2022 | 0
791 | AJAX WIND | 20INR0142 |  | WILBARGER | WIND-O | WEST | 2021 | 0
792 | APOGEE WIND | 21INR0467 |  | HASKELL | WIND-O | WEST | 2021 | 0
793 | AQUILLA LAKE 2 WIND | 20INR0256 |  | HILL | WIND-O | NORTH | 2021 | 0
794 | AQUILLA LAKE WIND | 19INR0145 |  | HILL | WIND-O | NORTH | 2021 | 0
795 | AVIATOR WIND | 19INR0156 |  | COKE | WIND-O | WEST | 2020 | 525
796 | BAIRD NORTH WIND | 20INR0083 |  | CALLAHAN | WIND-O | WEST | 2021 | 0
797 | BARROW RANCH (JUMBO HILL WIND) | 18INR0038 |  | ANDREWS | WIND-O | WEST | 2020 | 160
798 | BIG SAMPSON WIND | 16INR0104 |  | CROCKETT | WIND-O | WEST | 2021 | 0
799 | BLACKJACK CREEK WIND | 20INR0068 |  | BEE | WIND-O | SOUTH | 2021 | 0
800 | CACTUS FLATS WIND | 16INR0086 |  | CONCHO | WIND-O | WEST | 2020 | 148.4
801 | CANYON WIND | 18INR0030 |  | SCURRY | WIND-O | WEST | 2021 | 0
802 | COYOTE WIND | 17INR0027b |  | SCURRY | WIND-O | WEST | 2020 | 0
803 | EDMONDSON RANCH WIND | 18INR0043 |  | GLASSCOCK | WIND-O | WEST | 2021 | 0
804 | FOXTROT WIND | 20INR0129 |  | KARNES | WIND-O | SOUTH | 2022 | 0
805 | GRIFFIN TRAIL WIND | 20INR0052 |  | KNOX | WIND-O | WEST | 2021 | 0
806 | HARALD (BEARKAT WIND B) | 15INR0064b |  | GLASSCOCK | WIND-O | WEST | 2020 | 162.1
807 | HIDALGO II WIND | 19INR0053 |  | HIDALGO | WIND-O | SOUTH | 2020 | 51
808 | HIGH LONESOME W | 19INR0038 |  | CROCKETT | WIND-O | WEST | 2020 | 0
809 | HIGH LONESOME WIND PHASE II | 20INR0262 |  | CROCKETT | WIND-O | WEST | 2020 | 0
810 | HUTT WIND | 21INR0005 |  | MIDLAND | WIND-O | WEST | 2021 | 0
811 | KONTIKI 1 WIND (ERIK) | 19INR0099a |  | GLASSCOCK | WIND-O | WEST | 2023 | 0
812 | KONTIKI 2 WIND (ERNEST) | 19INR0099b |  | GLASSCOCK | WIND-O | WEST | 2023 | 0
813 | VENADO WIND | 16INR0111 |  | STARR | WIND-O | SOUTH | 2020 | 0
814 | LORAINE WINDPARK PHASE III | 18INR0068 |  | MITCHELL | WIND-O | WEST | 2021 | 0
815 | MARYNEAL WINDPOWER | 18INR0031 |  | NOLAN | WIND-O | WEST | 2021 | 0
816 | MAVERICK CREEK I | 20INR0045 |  | CONCHO | WIND-O | WEST | 2020 | 0
817 | MAVERICK CREEK II | 20INR0046 |  | CONCHO | WIND-O | WEST | 2021 | 0
818 | MESTENO WIND | 16INR0081 |  | STARR | WIND-O | SOUTH | 2020 | 0
819 | MONARCH CREEK WIND | 21INR0263 |  | THROCKMORTON | WIND-O | WEST | 2021 | 0
820 | OVEJA WIND | 18INR0033 |  | IRION | WIND-O | WEST | 2020 | 300
821 | PRAIRIE HILL WIND | 19INR0100 |  | MCLENNAN | WIND-O | NORTH | 2020 | 0
822 | PRIDDY WIND | 16INR0085 |  | MILLS | WIND-O | NORTH | 2021 | 0
823 | RELOJ DEL SOL WIND | 17INR0025 |  | ZAPATA | WIND-O | SOUTH | 2020 | 0
824 | ROADRUNNER CROSSING WIND 1 | 19INR0117 |  | EASTLAND | WIND-O | NORTH | 2021 | 0
825 | RTS 2 WIND (HEART OF TEXAS WIND) | 18INR0016 |  | MCCULLOCH | WIND-O | SOUTH | 2020 | 179.9
826 | SAGE DRAW WIND | 19INR0163 |  | LYNN | WIND-O | WEST | 2020 | 338
827 | TG EAST WIND | 19INR0052 |  | KNOX | WIND-O | WEST | 2021 | 0
828 | VERA WIND | 19INR0051 |  | KNOX | WIND-O | WEST | 2020 | 208.8
829 | VERA WIND V110 | 20INR0305 |  | KNOX | WIND-O | WEST | 2020 | 34
830 | WHITE MESA WIND | 19INR0128 |  | CROCKETT | WIND-O | WEST | 2021 | 0
831 | WHITEHORSE WIND | 19INR0080 |  | FISHER | WIND-O | WEST | 2020 | 418.9
832 | WILDWIND | 20INR0033 |  | COOKE | WIND-O | NORTH | 2020 | 0
833 | WKN AMADEUS WIND | 14INR0009 |  | FISHER | WIND-O | WEST | 2020 | 0
834 | Planned Capacity Total (Wind) | [6 empty] | 2897
835
836 | Planned Wind Capacity Sub-total (Coastal Counties) |  | WIND_PLANNED_C |  |  |  |  | 370.9
837 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PL_PEAK_PCT_C | % |  |  |  | 35
838
839 | Planned Wind Capacity Sub-total (Panhandle Counties) |  | WIND_PLANNED_P |  |  |  |  | 0
840 | Wind Peak Average Capacity Percentage (Panhandle) |  | WIND_PL_PEAK_PCT_P | % |  |  |  | 43
841
842 | Planned Wind Capacity Sub-total (Other counties) |  | WIND_PLANNED_O |  |  |  |  | 2526.1
843 | Wind Peak Average Capacity Percentage (Other) |  | WIND_PL_PEAK_PCT_O | % |  |  |  | 38
844
845 | Planned Solar Resources with Executed SGIA
846 | ANSON SOLAR | 19INR0081 |  | JONES | SOLAR | WEST | 2020 | 0
847 | ARAGORN SOLAR | 19INR0088 |  | CULBERSON | SOLAR | WEST | 2021 | 0
848 | AZURE SKY SOLAR | 21INR0477 |  | HASKELL | SOLAR | WEST | 2021 | 0
849 | BLUEBELL SOLAR II | 20INR0204 |  | STERLING | SOLAR | WEST | 2021 | 0
850 | BRAVEPOST SOLAR | 20INR0053 |  | TOM GREEN | SOLAR | WEST | 2022 | 0
851 | BRIGHTSIDE SOLAR | 18INR0060 |  | BEE | SOLAR | SOUTH | 2021 | 0
852 | CONIGLIO SOLAR | 20INR0037 |  | FANNIN | SOLAR | NORTH | 2021 | 0
853 | CORAZON SOLAR PHASE I | 15INR0044 |  | WEBB | SOLAR | SOUTH | 2021 | 0
854 | CORAZON SOLAR PHASE II | 22INR0257 |  | WEBB | SOLAR | SOUTH | 2022 | 0
855 | COTTONWOOD BAYOU | 19INR0134 |  | BRAZORIA | SOLAR | COASTAL | 2021 | 0
856 | CROWDED STAR SOLAR | 20INR0241 |  | JONES | SOLAR | WEST | 2021 | 0
857 | CROWDED STAR SOLAR II | 22INR0274 |  | JONES | SOLAR | WEST | 2022 | 0
858 | DANCIGER SOLAR | 20INR0098 |  | BRAZORIA | SOLAR | COASTAL | 2022 | 0
859 | DANISH FIELDS SOLAR I | 20INR0069 |  | WHARTON | SOLAR | SOUTH | 2021 | 0
860 | DANISH FIELDS SOLAR II | 21INR0016 |  | WHARTON | SOLAR | SOUTH | 2021 | 0
861 | DANISH FIELDS SOLAR III | 21INR0017 |  | WHARTON | SOLAR | SOUTH | 2021 | 0
862 | ELARA SOLAR | 21INR0276 |  | FRIO | SOLAR | SOUTH | 2021 | 0
863 | EMERALD GROVE SOLAR (PECOS SOLAR POWER I) | 15INR0059 |  | PECOS | SOLAR | WEST | 2021 | 0
864 | EUNICE SOLAR | 20INR0219 |  | ANDREWS | SOLAR | WEST | 2020 | 0
865 | FORT BEND SOLAR | 18INR0053 |  | FORT BEND | SOLAR | HOUSTON | 2021 | 0
866 | GALLOWAY 1 SOLAR | 19INR0121 |  | CONCHO | SOLAR | WEST | 2021 | 0
867 | GALLOWAY 2 SOLAR | 21INR0431 |  | CONCHO | SOLAR | WEST | 2022 | 0
868 | GARNET SOLAR | 20INR0021 |  | WILLIAMSON | SOLAR | SOUTH | 2020 | 0
869 | GREASEWOOD SOLAR | 19INR0034 |  | PECOS | SOLAR | WEST | 2020 | 0
870 | GREEN HOLLY SOLAR | 21INR0021 |  | DAWSON | SOLAR | WEST | 2022 | 0
871 | HORIZON SOLAR | 21INR0261 |  | FRIO | SOLAR | SOUTH | 2021 | 0
872 | HOVEY (BARILLA SOLAR 1B) | 12INR0059b |  | PECOS | SOLAR | WEST | 2020 | 7.4
873 | IMPACT SOLAR | 19INR0151 |  | LAMAR | SOLAR | NORTH | 2020 | 0
874 | IP TITAN | 20INR0032 |  | CULBERSON | SOLAR | WEST | 2021 | 0
875 | JUNO SOLAR PHASE I | 21INR0026 |  | BORDEN | SOLAR | WEST | 2021 | 0
876 | JUNO SOLAR PHASE II | 21INR0501 |  | BORDEN | SOLAR | WEST | 2021 | 0
877 | KELLAM SOLAR | 20INR0261 |  | VAN ZANDT | SOLAR | NORTH | 2020 | 0
878 | LILY SOLAR | 19INR0044 |  | KAUFMAN | SOLAR | NORTH | 2021 | 0
879 | LONG DRAW SOLAR | 18INR0055 |  | BORDEN | SOLAR | WEST | 2020 | 0
880 | LONG POINT SOLAR | 19INR0042 |  | BRAZORIA | SOLAR | COASTAL | 2021 | 0
881 | MISAE SOLAR | 18INR0045 |  | CHILDRESS | SOLAR | PANHANDLE | 2020 | 240.8
882 | MISAE SOLAR II | 20INR0091 |  | CHILDRESS | SOLAR | PANHANDLE | 2022 | 0
883 | MORROW LAKE SOLAR | 19INR0155 |  | FRIO | SOLAR | SOUTH | 2022 | 0
884 | MUSTANG CREEK SOLAR | 18INR0050 |  | JACKSON | SOLAR | SOUTH | 2021 | 0
885 | MYRTLE SOLAR | 19INR0041 |  | BRAZORIA | SOLAR | COASTAL | 2021 | 0
886 | NAZARETH SOLAR | 16INR0049 |  | CASTRO | SOLAR | PANHANDLE | 2022 | 0
887 | NORTON SOLAR | 19INR0035 |  | RUNNELS | SOLAR | WEST | 2022 | 0
888 | OLD 300 SOLAR CENTER | 21INR0406 |  | FORT BEND | SOLAR | HOUSTON | 2021 | 0
889 | OLD HICKORY SOLAR | 20INR0236 |  | JACKSON | SOLAR | SOUTH | 2021 | 0
890 | OXY SOLAR | 19INR0184 |  | ECTOR | SOLAR | WEST | 2020 | 16.2
891 | PFLUGERVILLE SOLAR | 15INR0090 |  | TRAVIS | SOLAR | SOUTH | 2021 | 0
892 | PHOENIX SOLAR | 19INR0091 |  | FANNIN | SOLAR | NORTH | 2021 | 0
893 | PINE FOREST SOLAR | 20INR0203 |  | HOPKINS | SOLAR | NORTH | 2022 | 0
894 | PROSPERO SOLAR II | 21INR0229 |  | ANDREWS | SOLAR | WEST | 2021 | 0
895 | RAMBLER SOLAR | 19INR0114 |  | TOM GREEN | SOLAR | WEST | 2020 | 200
896 | RAMSEY SOLAR | 20INR0130 |  | WHARTON | SOLAR | SOUTH | 2021 | 0
897 | RAYOS DEL SOL | 19INR0045 |  | CAMERON | SOLAR | COASTAL | 2021 | 0
898 | RE MAPLEWOOD 2A SOLAR | 17INR0020a |  | PECOS | SOLAR | WEST | 2021 | 0
899 | RE MAPLEWOOD 2B SOLAR | 17INR0020b |  | PECOS | SOLAR | WEST | 2021 | 0
900 | RIPPEY SOLAR | 20INR0031 |  | COOKE | SOLAR | NORTH | 2020 | 0
901 | RODEO SOLAR | 19INR0103 |  | ANDREWS | SOLAR | WEST | 2021 | 0
902 | SBRANCH SOLAR PROJECT | 22INR0205 |  | WHARTON | SOLAR | SOUTH | 2022 | 0
903 | SHAKES SOLAR | 19INR0073 |  | ZAVALA | SOLAR | SOUTH | 2021 | 0
904 | SODA LAKE SOLAR 2 | 20INR0143 |  | CRANE | SOLAR | WEST | 2022 | 0
905 | SPARTA SOLAR | 22INR0352 |  | BEE | SOLAR | SOUTH | 2022 | 0
906 | STRATEGIC SOLAR 1 | 20INR0081 |  | ELLIS | SOLAR | NORTH | 2021 | 0
907 | SUN VALLEY | 19INR0169 |  | HILL | SOLAR | NORTH | 2022 | 0
908 | TAYGETE II SOLAR | 21INR0233 |  | PECOS | SOLAR | WEST | 2021 | 0
909 | TAYGETE SOLAR | 20INR0054 |  | PECOS | SOLAR | WEST | 2021 | 0
910 | TEXAS SOLAR NOVA | 19INR0001 |  | KENT | SOLAR | WEST | 2022 | 0
911 | TIMBERWOLF POI A | 20INR0226 |  | UPTON | SOLAR | WEST | 2022 | 0
912 | TRES BAHIAS SOLAR | 20INR0266 |  | CALHOUN | SOLAR | COASTAL | 2021 | 0
913 | UPTON SOLAR | 16INR0114 |  | UPTON | SOLAR | WEST | 2021 | 0
914 | VANCOURT SOLAR | 21INR0213 |  | CAMERON | SOLAR | COASTAL | 2021 | 0
915 | WAGYU SOLAR | 18INR0062 |  | BRAZORIA | SOLAR | COASTAL | 2020 | 120
916 | WESTORIA SOLAR | 20INR0101 |  | BRAZORIA | SOLAR | COASTAL | 2021 | 0
917 | Planned Capacity Total (Solar) | [6 empty] | 584.4
918 | Solar Peak Average Capacity Percentage |  | SOLAR_PL_PEAK_PCT | % |  |  |  | 66
919
920 | Planned Storage Resources with Executed SGIA
921 | AZURE SKY BESS | 21INR0476 |  | HASKELL | STORAGE | WEST | 2021 | 0
922 | BAT CAVE | 21INR0365 |  | MASON | STORAGE | SOUTH | 2021 | 0
923 | CHISHOLM GRID | 20INR0089 |  | TARRANT | STORAGE | NORTH | 2021 | 0
924 | EUNICE STORAGE | 20INR0220 |  | ANDREWS | STORAGE | WEST | 2020 | 0
925 | GAMBIT | 21INR0364 |  | BRAZORIA | STORAGE | COASTAL | 2021 | 0
926 | LILY STORAGE | 20INR0294 |  | KAUFMAN | STORAGE | NORTH | 2021 | 0
927 | MADERO GRID | 21INR0244 |  | HIDALGO | STORAGE | SOUTH | 2021 | 0
928 | NORTH FORK | 20INR0276 |  | WILLIAMSON | STORAGE | SOUTH | 2021 | 0
929 | QUEEN BESS | 20INR0281 |  | UPTON | STORAGE | WEST | 2022 | 0
930 | SILICON HILL STORAGE | 20INR0291 |  | TRAVIS | STORAGE | SOUTH | 2021 | 0
931 | BRP ALVIN (DGR) |  | BRPALVIN_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2020 | 10
932 | BRP ANGELTON (DGR) |  | BRPANGLE_UNIT1 | BRAZORIA | STORAGE | HOUSTON | 2020 | 10
933 | BRP BRAZORIA (DGR) |  | BRP_BRAZ_UNIT1 | BRAZORIA | STORAGE | HOUSTON | 2020 | 10
934 | BRP DICKINSON (DGR) |  | BRP_DIKN_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2020 | 10
935 | BRP HEIGHTS (DGR) |  | BRHEIGHT_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2020 | 10
936 | BRP LOOP 463 (DGR) |  | BRP_LOOP_UNIT1 | VICTORIA | STORAGE | SOUTH | 2020 | 0
937 | BRP MAGNOLIA (DGR) |  | BRPMAGNO_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2020 | 10
938 | BRP RANCHTOWN (DGR) |  | BRP_RNCH_UNIT1 | BEXAR | STORAGE | SOUTH | 2020 | 0
939 | BRP SWEENY (DGR) |  | BRP_SWNY_UNIT1 | BRAZORIA | STORAGE | HOUSTON | 2020 | 0
940 | COMMERCE ST ESS (DGR) |  | X443ESS1_SWRI | BEXAR | STORAGE | SOUTH | 2019 | 10
941 | FLOWER VALLEY BATTERY (DGR) |  | FLVABES1_FLATU1 | REEVES | STORAGE | WEST | 2020 | 0
942 | HOEFSROAD BESS (DGR) |  | HRBESS_BESS | REEVES | STORAGE | NORTH | 2020 | 0
943 | JOHNSON CITY BESS (DGR) |  | JC_BAT_UNIT_1 | BLANCO | STORAGE | SOUTH | 2020 | 2.3
944 | SWOOSE BATTERY (DGR) |  | SWOOSE1_SWOOSEU1 | WARD | STORAGE | WEST | 2020 | 0
945 | Planned Capacity Total (Storage) | [6 empty] | 72.3
946 | Storage Peak Average Capacity Percentage |  | STORAGE_PL_PEAK_PCT | % |  |  |  | 0
947
948 | Inactive Planned Resources
949 | FRIENDSWOOD II | 19INR0180 |  | BRAZORIA | GAS-GT | COASTAL | 2021 | 0
950 | HALYARD WHARTON ENERGY CENTER | 16INR0044 |  | WHARTON | GAS-GT | SOUTH | 2021 | 0
951 | CHOCOLATE BAYOU W | 16INR0074 |  | BRAZORIA | WIND-C | COASTAL | 2022 | 0
952 | GOODNIGHT WIND | 14INR0033 |  | ARMSTRONG | WIND-P | PANHANDLE | 2021 | 0
953 | MARIAH DEL ESTE | 13INR0010a |  | PARMER | WIND-P | PANHANDLE | 2020 | 0
954 | NORTHDRAW WIND | 13INR0025 |  | RANDALL | WIND-P | PANHANDLE | 2020 | 150
955 | PANHANDLE WIND 3 | 14INR0030c |  | CARSON | WIND-P | PANHANDLE | 2022 | 0
956 | WILDROSE WIND (SWISHER WIND) | 13INR0038 |  | SWISHER | WIND-P | PANHANDLE | 2021 | 0
957 | LOMA PINTA WIND | 16INR0112 |  | LA SALLE | WIND-O | SOUTH | 2021 | 0
958 | AGATE SOLAR | 20INR0023 |  | ELLIS | SOLAR | NORTH | 2020 | 60
959 | SPINEL SOLAR | 20INR0025 |  | MEDINA | SOLAR | SOUTH | 2020 | 0
960 | ROUGHNECK STORAGE | 19INR0176 |  | BRAZORIA | STORAGE | COASTAL | 2021 | 0
961 | Inactive Planned Capacity Total | [6 empty] | 210
962
963 | Seasonal Mothballed Resources
964 | GREGORY POWER PARTNERS GT1 (AS OF 10/17/2019, AVAILABLE 5/1 THROUGH 9/30) |  | LGE_LGE_GT1 | SAN PATRICIO | GAS-CC | COASTAL | 2000 | 152
965 | GREGORY POWER PARTNERS GT2 (AS OF 10/17/2019, AVAILABLE 5/1 THROUGH 9/30) |  | LGE_LGE_GT2 | SAN PATRICIO | GAS-CC | COASTAL | 2000 | 151
966 | GREGORY POWER PARTNERS STG (AS OF 10/17/2019,AVAILABLE 5/1 THROUGH 9/30) |  | LGE_LGE_STG | SAN PATRICIO | GAS-CC | COASTAL | 2000 | 75
967 | SPENCER STG U4 (AS OF 10/3/2018, AVAILABLE 5/20 THROUGH 10/10) |  | SPNCER_SPNCE_4 | DENTON | GAS-ST | NORTH | 1966 | 57
968 | SPENCER STG U5 (AS OF 10/3/2018, AVAILABLE 5/20 THROUGH 10/10) |  | SPNCER_SPNCE_5 | DENTON | GAS-ST | NORTH | 1973 | 61
969 | Total Seasonal Mothballed Capacity | [6 empty] | 496
970
971 | Mothballed Resources
972 | J T DEELY U1 (AS OF 12/31/2018) |  | CALAVERS_JTD1_M | BEXAR | COAL | SOUTH | 1977 | 430
973 | J T DEELY U2 (AS OF 12/31/2018) |  | CALAVERS_JTD2_M | BEXAR | COAL | SOUTH | 1978 | 420
974 | Total Mothballed Capacity | [6 empty] | 850
975
976 | Retiring Resources Unavailable to ERCOT (since last CDR/SARA)
977 | Total Retiring Capacity | [6 empty] | 0
Notes:
Capacity changes due to planned repower/upgrade projects are reflected in the operational units' ratings upon (1) receipt and ERCOT approval of a new Resource Asset Registration Form (RARF). Projects associated with interconnection change requests that change the MW capacity are indicated with a code in the “Generation Interconnection Project Code” column of operational units.
Although seasonal capacity ratings for battery energy storage systems are reported above, the ratings are not included in the operational/planned capacity formulae. These resources are assumed to provide regulation reserves rather than sustained capacity available to meet system peak loads.
Unit Names with a (DGR) suffix are Distribution Generation Resources. A DGR fully participates in ERCOT's markets, but is connected to the Distribution System and is currently not required to go through the GINR application process.

## Background
Release Date: September 2, 2020
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Background
The Seasonal Assessment of Resource Adequacy (SARA) report is a deterministic approach to considering the impact of potential variables that may affect the sufficiency of installed resources to meet the peak electrical demand on the ERCOT System during a particular season.
The standard approach to assessing resource adequacy for one or more years into the future is to account for projected load and resources on a normalized basis and to require sufficient reserves (resources in excess of peak demand, on this normalized basis) to cover the uncertainty in peak demand and resource availability to meet a probabilistic reliability standard.
For seasonal assessments that look ahead less than a year, specific information may be available (such as seasonal climate forecasts or anticipated common-mode events such as drought) which can be used to consider the range of resource adequacy in a more deterministic manner.
The SARA report focuses on the availability of sufficient operating reserves to avoid emergency actions such as deployment of voluntary load reduction resources. It uses an operating reserve threshold of 2,300 MW to indicate the risk that an Energy Emergency Alert Level 1 (EEA1) may be triggered during the time of the forecasted seasonal peak load. This threshold level is intended to be roughly analogous to the 2,300 MW Physical Responsive Capability (PRC) threshold for EEA1. However, PRC is a real-time capability measure for Resources that can quickly respond to system disturbances. In contrast, the SARA operating reserve reflects additional capability assumed to be available before energy emergency procedures are initiated, such as from Resources qualified to provide non-spinning reserves. Additionally, the amount of operating reserves available may increase relative to what is included in the SARA report due to the market responding to wholesale market price increases and anticipated capacity scarcity conditions. Given these considerations, ERCOT believes that the 2,300 MW reserve capacity threshold is a reasonable indicator for the risk of Energy Emergency Alerts given the uncertainties in predicting system conditions months in advance.
The SARA report is intended to illustrate the range of resource adequacy outcomes that might occur. It serves as a situational awareness tool for ERCOT operational planning purposes, and helps fulfill the "extreme weather" resource adequacy assessment requirement per Public Utility Commission of Texas rule 25.362(i)(2)(H). In addition to a base scenario, several other scenarios are developed by varying the value of load forecast and resource availability parameters. The variation in these parameters is based on historic ranges of the parameter values or known changes expected in the near-term. The SARA report is not intended to indicate the likelihood of any of these scenario outcomes.