## Slide 1: DWG Report to ROS September, 2020
DWG Webex Meeting held on 8/11/2020
2020 DWG flatstart case has started
Ongoing review of feedbacks and comments on CMLD language proposal for DWG procedure manual and PGRR
Next DWG meeting on September 30th, 2020

## Slide 2: Issue with Acceleration factor in Generic Models
Issue with Acceleration factor in PSS/e Renewable Energy Generator/Converter Generic model (REGCAU1/REGCAU2)
Convergence issue and case crashing
Why?? More IBR 2nd generation generic models in 2020 FS cases as compared to 2019 FS cases
Python script was developed to change acceleration factor of REGCAU1/REGCAU2 to 0.7 if it is originally 0
Changing the acceleration factor improve network convergence in dynamic simulation
Incorporate changes in future stability studies
Discussion about incorporating changes in current and future FS cases

## Slide 3: DG Modeling consideration for DWG
Looking at how DGR, SODG, and UDG aggregation can be modeled in dynamic studies?
How do you decide the model type and parameterization for DGs?
Issue of DERs/DGs + Composite load model (CMLD)?
UFLS/UVLS models that reflect DG?
Other issues pertaining to DG representation in Dynamic studies

## Slide 4: DWG MOD-26/27 Summary
Per Planning Guide and DWG Procedure Manual, a Resource Entity shall submit new or updated dynamic data within 30 days of the update
Per NERC MOD-26/27, Generator Owners need to verify the models and data and provide the data to its Transmission Planner
With support from TSPs, ERCOT tracks the MOD-026/27 verifications/updates and the corresponding RARF updates
Only 22 out of 49 (less than 50%) MOD-26/27 model updates in 2020 were submitted to RARF without requiring additional ERCOT follow-up

## Slide 5: QUESTIONS???