## Slide 1
ERCOT Frequency Control Report
August 2020
ERCOT
Operations Planning
PDCWG | September 9th, 2020

## Slide 2: Summary of August 2020
CPS1: 170.49%
Current CPS1 12-Month Rolling Average: 175.57%
1 BAAL Exceedance
4 hourly CPS1 score below 100%
BAAL-003 Events have updated through 2019
2019 BAAL-003 FRM Performance: -811.14
2020 RMS1 Statistics
  Mean: 16.14 mHz
  Min: 12.25 mHz
  Max: 22.6 mHz
Energy Statistics
  Total Energy: 40,757,122 MWh
  Wind Energy: 6,441,373 MWh
  Percent Energy from Wind: 15.80%
  Solar Energy: 1,002,605 MWh
  Percent Energy from Solar: 2.46%
Minimum System Inertia
  Mean: 283, 054 MW*s
  Max: 316,104 MW*s on Aug 16th
  Min: 253,877 MW*s on Aug 8th
Notes: 2018 BAAL-003 FRM Performance: -843.17

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
Aug-20 CPS1 (%): 170.49
Notes: Outliers:
1. 86.14% @ 8/5/2020 17:00
  Expected Gen Dev:
  Large exp. Gen. dev of -1377 @ 17:22 mostly due to solar
  Wind/Solar Ramp: Solar ramp from 2236 to 2440 MW within 10 minutes.
  Regulation: Regulation up exhausted for approximately half of the hour
  SCED Offset : Enabled by operator to offset over 700MW of ACE
85.33% @ 8/28/2020 18:00
Frequency Event: @ 18:39, loss of about 186 MWs lost, and nadir of 59.928Hz
  Expected Gen Dev:
  Large exp. Gen. dev of -1421 @ 18:45 mostly due to thermal units shutting down
  Wind/Solar Ramp: Solar ramp from 2805to 1834 MW between 18:30and 19:00
  Regulation: Regulation up exhausted from 18:27-18:37 and 18:53-18:56
3. 98.61% @ 8/30/2020 17:00
  Expected Gen Dev:
  Large exp. Gen. dev of -948 @ 17:23 mostly due to solar ramps and thermal units shutting down
  Wind/Solar Ramp: Solar ramp from 3247 MW to 2736 MW between 17:00 and 17:30
  Regulation: Regulation up exhausted for most of the hour
4. 5.78% @ 8/31/2020 21:00
  Expected Gen Dev:
  Large exp. Gen. dev of -1816 @ 21:17 mostly due to wind and thermal units. Negative exp. Gen. dev throughout the hour.
  Wind/Solar Ramp: There are 5 SCED intervals with wind forecast over-forecast error greater than 100 MW/5min (PWRR capped out to 30MW/min)
  Regulation: Regulation up exhausted for half of the hour

## Slide 5: BAAL Exceedances & Violations
There was 1 BAAL exceedance in Aug
Notes: 1 on 8/2/2020

## Slide 6: 15-Minute Average CPS1%
Aug-20 CPS1 (%): 170.49

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 175.57%

## Slide 8: Daily RMS1 of ERCOT Frequency by Year

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2019 BAL-003 Selected Events – Update
Notes: BAL-003

## Slide 19: Op. Year 2018 BAL-003 FRM Performance - Update
Notes: OP2018: FRO = -381.0, FRM_median = -843.17, FRM_average = -959.7
OP2019: FRO = -381.0, FRM_median = -811.14, FRM_average = -892.5
OP2020: FRO = -425.0,

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 40,757,122 MWh

## Slide 22: Total Energy from Wind Generation
Notes: 6,441,373 MWh

## Slide 23: % Energy from Wind Generation
Notes: 15.80%

## Slide 24: Total Energy From Solar Generation
Notes: 1,002,605 MWh

## Slide 25: % Energy from Solar Generation
Notes: 2.46%

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia = 253,877 MW*s on 8/8/2020
Previous Minimum was 128,759 MW*s on 11/18/2018.
Data:
Mean: 283,054
Max: 316,104 on Aug 16th
Min: 253,877 on Aug 8th

## Slide 28: Questions?
Thank you!