## Slide 1
DGR (Battery) equivalent impedance expectation
7/28/2020

## Slide 2: Simplest model
Real equipment like circuit breaker is needed between line and node1
  To isolate DGR to grid
no pseudo-equipment is needed between
  DGR and node1
  CLR and node1
Advantage
  Minimize pseudo-equipment
  Simplify operation model
  Facilitate outage coordination
node1
Breaker
Line
DGR
CLR
node2

## Slide 3: RARF – sample RARF Planning Gen Data

## Slide 4: Impedance modeling issue
Impedance does not reflect equivalent impedance of entire generating unit
  RARF “Planning – GEN” tab
  one battery-inverter module
  Impedance does not reflect impedance of entire generating unit
  does not have pad-mount step up transformer data
    Transformer impedance derived from test report or word document which is not part of RARF data
  does not have GenUnit-Battery-inverter-transformer configuration
    Estimate based on one-line
    Example 1 unit with 4 batteries, each batteries connect to one inverter, each inverter to one transformer

## Slide 5: Impedance modeling issue cont’d
Other generators using GEN FORM has equivalent impedance
impedance data in RARF not accurately reflected in ERCOT models affecting downstream systems

## Slide 6: Equivalent impedance example
Module1
Module2
Module3
Module4
R=0.02 p.u.
X=1.02 p.u.
R=0.02 p.u.
X=1.02 p.u.
R=0.02 p.u.
X=1.02 p.u.
R=0.02 p.u.
X=1.02 p.u.
R=0.08 p.u.
X=4.08 p.u.
R=0.08 p.u.
X=4.08 p.u.
R=0.08 p.u.
X=4.08 p.u.
R=0.08 p.u.
X=4.08 p.u.

## Slide 7: Equivalent impedance example cont’d
Test Step-up Transformer Specifications
  Voltage
    Low Side: 0.5 kV
    High Side: 12.5 kV
  MVA ratings: 2.75 MVA
  Positive sequence impedances: 6%
  Zero sequence impedance: 5%
  X/R: 10
  Available Taps: 5 (±2 x 3%)
=
=
.

## Slide 8: Equivalent impedance example cont’d

## Slide 9: Equivalent impedance example cont’d

## Slide 10: Q & A
QUESTIONS?