## Sheet 1
Data Entry
Max Allowed % Watt Line Cu Loss: | 0.001%
Ohms per Foot: | 2.3619e-05
PT ratio (xxx:1): | 1800
CT ratio (xxx:1): | 200
Meter Number of Elements (2 or 3): | 3
Meter Class Amps: | 20
Meter Rated Voltage: | 120
Results
Max uncompensated distance (feet): | 45.7252

## Sheet 2
Data Entry
Distance (feet): | 45.72
Ohms per Foot: | 2.3619e-05
PT ratio (xxx:1): | 1800
CT ratio (xxx:1): | 200
Meter Number of Elements (2 or 3): | 3
Meter Class Amps: | 20
Meter Rated Voltage: | 120
Results
% Watt Line Cu Loss | 0.0009999%