## Slide 1
Load Resource Participation in the ERCOT Region

## Slide 2: Main Discussion Topics
Definitions
Ancillary Services in the ERCOT Region
Load Resource Characteristics
Registration and Modeling
Qualification and Testing
Real Time Energy Market
Ancillary Service Participation
Performance Analysis and Compliance Activities
Q and A

## Slide 3: A Few Definitions and Acronyms
Resources fall into two basic categories:
  Generation Resources (GR)
  Load Resources (LR)
    Controllable Load Resource (CLR)
    Non-Controllable Load Resource (NCLR)
Resources Entities
  The controlling entity for the Resources
  Responsible for Registration
  Needs to establish a partnership with a Qualified Scheduling Entity
Qualified Scheduling Entities (QSE)
  Submits offers for the Resources into the Day Ahead Market
  Maintains Current Operating Plan
  Schedules the Resources
  Dispatch Controller for the Resources
  Responsible for Settlement of Day Ahead Market Activities

## Slide 4: Ancillary Services in ERCOT
Responsive Reserve Service
  Used to arrest frequency decay in the first seconds of a significant frequency deviation
  Can also provide energy and load Interruption during an Energy Emergency Alert (EEA)
  Can be provided by Generation Resources or Load Resources
  When deployed manually (LR only) the Resources need to have a 10 minute response to a dispatch instruction
Regulation Service
  Conventional Reg Up and Reg Down
  Fast Responding Regulation Service Up and Down
  Can by provided by Generation Resources and Controllable Load Resources
Non-Spinning Reserve
  Provided by Generation Resources that can be off-line or on-line
  Provided by Controllable Load Resources
  Thirty minute response to a dispatch instruction

## Slide 5: CLR Characteristics
Almost all LRs participating in the AS market today are Non-Controllable LRs (controlled by high-set UFR) and do not follow Base Points.
  Recently, several data centers have begun participating as Controllable Load Resources (CLRs) with software control systems used to follow Base Points.
CLRs can be transmission or distribution connected.
The charging side of Energy Storage Resources (ESR) currently register as CLRs.
  ERCOT will be going to a single model of ESR starting in 2024.
Most Load Resources are single site Load Resources.
  Aggregations within a single Load Zone are allowed but have not been successful in becoming qualified. Issues have been related to how telemetry will be validated. Currently only allowed for Non-Spinning Reserve Service and participation in Real Time Market for Energy.

## Slide 6: Registration and Modeling of Load Resources
Resource Entity submits Asset Registration Form to ERCOT.
Load Resources are mapped to an existing transmission load point in the ERCOT Model.
Mapping includes Resource telemetry from the QSE to ERCOT such as:
  Net Power Consumption (current Load)
  Resource Status
  AS Responsibility and Schedule
  Max Power Consumption and Low Power Consumption (similar to HSL and LSL for generators)
  Circuit Breaker
  Telemetry needs to be updated every 2 seconds
When the CLR is behind a meter where other firm load exists, telemetry comes from the load that is being controlled and not the POI.

## Slide 7: CLR Qualification
Basic Requirements:
  Need to be registered and modeled in ERCOT Systems.
  Need to have revenue grade meter capable of recording 15 minute interval data.
  Data needs to be submitted at least monthly into ERCOT systems
  Provide a one line diagram for the Resource including connections all the way to the transmission Load transformer.
  Provide a test report demonstrating their droop characteristics (see section 8C of the Operating Guides).
  Provide test data to show the CLR is capable of sustaining their Load for at least one hour.
Pass an initial SCED qualification test by responding to ERCOT issued basepoint changes that will ramp the resource between it’s MPC and LPC, including some holding periods.
Telemetry must be validated annually.

## Slide 8: CLRs in the Real Time Market (RTM) for Energy
CLR must be represented by the same QSE that represents the Load Serving Entity.
QSE submits a “Bid to Buy” which represents the energy price above which the CLR will drop Load.
The CLR then gets dispatched economically by the Market Management System.
Dispatch instructions typically take place every 5 minutes and result in a linear ramp during this SCED cycle.
The CLR must be capable of reducing or increasing consumption to any level between their MPC and LPC within seconds of ERCOT instruction.

## Slide 9: CLRs in the Real Time Market (RTM) for Energy
Real Time Energy Price | Basepoint sent to Resource
$250/MWh | 0MW
$70/MWh | 0MW
$65/MWh | 2MW
$40/MWh | 8MW
$20/MWh | 10MW
$-50/MWh | 10MW

## Slide 10: CLRs in the Real Time Market (RTM) for Energy
CLRs need to respond automatically to frequency deviations outside a deadband of 0.36 Hz.
  The response must be based on their measured droop performance, similar to the governor on a generator.
RTM performance is measured by CLR Energy Deployment Performance (CLREDP) Metrics.
Base Point Deviation Charges can result for over or under consumption.

## Slide 11: CLR Participation in the Ancillary Services Markets
CLRs are awarded the same as GRs and face similar requirements.
CLRs can participate in Reg Up, Reg Dn, RRS and NSRS.
The portion of the CLR’s load that can provide AS is based on its droop settings and can be limited from 20% to 100% of the MPC.
Deployment of CLRs providing RRS or NSRS releases the capacity to be deployed by SCED in the RTM.
  SCED engine dispatches the Load based on Bid to Buy curves.
Deployment of Regulation is done by Load Frequency Control (LFC) in addition to any signals from SCED.
  This signal is sent to the QSE and not the Resource directly.
Performance for AS is included in the CLREDP metrics.

## Slide 12: CLR participation in Responsive Reserve Service (RRS)
CLRs participate as part of the GR portion of RRS
Total quantity of RRS is dependent on time of year and time of day.
Total amount will vary from 2300 MW to 3200 MW.
  More procured in off-peak hours and off-peak months.
Minimum amount of 1150 MW must come from GRs/CLRs.
Remaining balance can come from Non-Controllable Load Resources (NCLRs) but is limited to 60% of the total.
Awards are made on a Resource specific basis – NCLRs are frequently prorated in terms of the quantity awarded.
Proration occurs when there are multiple offers at the price at the top of the offer stack.
  Offer variance makes this very rare for GRs and CLRs.

## Slide 13: CLR Participation in the Ancillary Services Markets
ERCOT maintains tools to monitor AS Performance in Real Time.
Operators will call QSEs with any type of performance issue.
QSE can move capacity from one Resource to another with ERCOT permission – GR/CLR can replace a NCLR or GR/CLR, but a NCLR can only replace another NCLR.
Operators will issue a SASM if a QSE has an extended shortage and cannot replace it – if the cause is a “Failure to Provide” the QSE will be held responsible for the financial difference.

## Slide 14: CLR Performance Analysis
ERCOT maintains tools to monitor AS Performance in Real Time.
Operators will call QSEs with any type of performance issue.
QSE can move capacity from one Resource to another with ERCOT permission – GR/CLR can replace a NCLR or GR/CLR, but a NCLR can only replace another NCLR.
Operators will issue a SASM if a QSE has an extended shortage and cannot replace it – if the cause is a “Failure to Provide” the QSE will be held responsible for the financial difference.
The Performance, Disturbance, Compliance Working Group (PDCWG) reviews the performance of all Resources for Frequency Measureable Events.
Failure to meet performance requirements can result in the Resources losing their qualification to provide Ancillary Services.

## Slide 15: CLR Performance Analysis
Telemetry used for performance analysis, not meter data.
Resource/Metric | Protocol Reference | X (%) | Y (MW)
Base Point Deviation, Over-Consumption, Controllable Load Resource | 6.6.5.1.1.3 | 25 | 2
Base Point Deviation, Under-Consumption, Controllable Load Resource | 6.6.5.1.1.4 | 15 | 2
Base Point Deviation, Over-Consumption, Controllable Load Resource with Ancillary Service responsibility | 6.6.5.1.1.3 | 15 | 2
Base Point Deviation, Under-Consumption, Controllable Load Resource with Ancillary Service Responsibility | 6.6.5.1.1.4 | 10 | 2
CLREDP | 8.1.1.4.1(9) | 25 | 2
CLREDP with Ancillary Service Responsibility | 8.1.1.4.1(9) | 15 | 2

## Slide 16: Questions?

## Slide 17: Appendix
ERCOT Contacts:
  Mark Patterson – Manager of Demand Integration – mpatterson@ercot.com
  Steve Krein – Senior Market Engineer – skrein@ercot.com
  Shane Thomas – Market Operations Engineer – sthomas@ercot.com
Links to Web–Based Training: http://www.ercot.com/services/training
  Good introductory courses and Wholesale Market Operations for Resources
Links to General Info on Load Resource participation at ERCOT: http://www.ercot.com/services/programs/load/laar
  Qualification Test Procedures
  Monthly and Annual Reports on Demand Response
Links to Day Ahead Market Info: http://www.ercot.com/mktinfo/dam
  Market reports
  Under Key Documents – Methodology for Determining Minimum Ancillary Service Requirements