## Slide 1
Transformer Rating Error and Potential Price Correction – Analysis of Price and Settlement Impacts
David Maggio
Director, Market Design & Analytics
TAC
9/23/2020

## Slide 2: Background - Timeline
February 12, 2020 – A modeling update was made in the ERCOT Network Model, where dynamic ratings were added to the model for three transmission transformers.
  Before the change, all transformers were modeled as having static ratings. There had been interest in having dynamic ratings for certain transformers. ERCOT had worked with a TSP to update the ratings for the transformers using the existing, built-in system functionality.
  Software Error- While applying the new dynamic ratings to the intended transformers, they were also erroneously applied to three unrelated 345/138 kV transformers. One transformer each at stations BLESSING, COLETO and LA PALMA.
  The reason for the error is that the identifiers used to map dynamically rated transformers were not fully unique between applications. This issue was triggered from dynamically rated transformers but impacted transformers ratings which are not dynamically rated.
  The number of transformers impacted was limited given that most transformer names are fairly unique and most transformers are not dynamically rated.
    July 7, 2020 – ERCOT identified the root cause of the error and the impacted transformers and implemented emergency changes in the production models. ERCOT also notified the market that Operating Day (OD) July 7, 2020 for the Day-Ahead Market (DAM) was under investigation.
July 8, 2020 – ERCOT issued Market Notice M-A070820-01 regarding incorrect ratings affecting the DAM and Real-Time Market (RTM) and continued investigating other days that may have been impacted. ERCOT also performed a price correction for OD July 7, 2020 for the DAM before price became final.

## Slide 3: Background – Impacts to the DAM and RTM
After reviewing all binding transmission constraints in DAM during the relevant time window, ERCOT found that there were 67 ODs for the DAM that had at least one constraint binding on one of the impacted transformers. These ODs occurred between February 14, 2020 and July 7, 2020.
After reviewing all binding transmission constraints in RTM during the relevant time window, ERCOT found only one OD for the RTM that had a constraint binding on one of the impacted transformers. This OD was July 1, 2020.
As the Market Notice M-A070820-01 was issued on July 8, 2020. The RTM and DAM between 6/8/2020 and 7/8/2020 are eligible for price correction with ERCOT Board review.

## Slide 4: Price Correction Impact Review
ERCOT’s analysis used original settled quantities with corrected prices based on DAM and RTM reruns, with the corrected transformer ratings.
  Note: The Settlement data provided herein is an estimate; final Settlement amounts may differ.
All Settlement amounts are net amounts due to/from ERCOT in $ thousands. Negative amounts are increased payments to Market Participants; positive amounts are increased charges.
The % amount is the absolute value of the % of impact to the previously settled net amount due to/from ERCOT.
In addition to the DAM impacts detailed herein:
  Balancing account impacts resulting in an overpayment to load of approximately $8K for June, and an underpayment to load of approximately $15K for July. The amounts paid/refunded due to resettlement will depend on the Balancing Account balance at the time of resettlement.
  Minimal changes to Real-Time Settlements due to Ancillary Service charges that will be reconciled based on actual Load Ratio Shares.

## Slide 5: Price Correction Study for the DAM
Market: DAM
Impacted ODs: 6/8/20-6/12/20, 6/15/20-6/17/20, 6/19/20-6/20/20, 6/24/20-6/25/20, 6/28/20-7/6/20
Price Correction Methodology: ERCOT reran the DAM on these ODs with the corrected ratings for the impacted transformers.
The following slides include analysis of the price and Settlement impacts of the DAM price correction using the new DAM solution.
  Quantities (awarded MWs) do not change; only prices.

## Slide 6: Potential DAM Price Correction Price Impacts
OD | Number of constraints with the impacted transformers | Count of Changes in Price for the 4 Hubs and 4 Competitive Load Zones across all Hourly Intervals of the Affected ODs |  |  |  |  |  |  | 
 |  | < -$10/MWh | >= -$10/MWh & < -$1/MWh | >= -$1/MWh & < -$0.1/MWh | >= -$0.1/MWh & < $0.1/MWh* | >= $0.1/MWh & < $1/MWh | >= $1/MWh & < $10/MWh | >= $10/MWh | No Change
6/8/2020 | 2 | 0 | 24 | 56 | 58 | 9 | 0 | 0 | 45
6/9/2020 | 8 | 0 | 19 | 52 | 55 | 21 | 0 | 0 | 45
6/10/2020 | 1 | 0 | 0 | 26 | 82 | 51 | 0 | 0 | 33
6/11/2020 | 1 | 0 | 0 | 38 | 76 | 43 | 25 | 0 | 10
6/12/2020 | 3 | 0 | 0 | 24 | 71 | 42 | 24 | 0 | 31
6/15/2020 | 2 | 0 | 16 | 48 | 22 | 55 | 51 | 0 | 0
6/16/2020 | 6 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 160
6/17/2020 | 7 | 0 | 0 | 0 | 64 | 48 | 0 | 0 | 80
6/19/2020 | 3 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 167
Note: a positive value indicates that the corrected or proposed price is higher than the original price.
* This column does not include prices that were not affected.

## Slide 7: Potential DAM Price Correction Price Impacts
OD | Number of constraints with the impacted transformers | Count of Changes in Price for the 4 Hubs and 4 Competitive Load Zones across all Hourly Intervals of the Affected ODs |  |  |  |  |  |  | 
 |  | < -$10/MWh | >= -$10/MWh & < -$1/MWh | >= -$1/MWh & < -$0.1/MWh | >= -$0.1/MWh & < $0.1/MWh* | >= $0.1/MWh & < $1/MWh | >= $1/MWh & < $10/MWh | >= $10/MWh | No Change
6/20/2020 | 4 | 0 | 0 | 1 | 44 | 1 | 0 | 0 | 146
6/24/2020 | 2 | 0 | 0 | 40 | 59 | 48 | 16 | 0 | 29
6/25/2020 | 1 | 0 | 0 | 56 | 63 | 0 | 0 | 0 | 73
6/28/2020 | 3 | 0 | 0 | 1 | 101 | 42 | 0 | 0 | 48
6/29/2020 | 5 | 0 | 0 | 7 | 78 | 38 | 1 | 0 | 68
6/30/2020 | 2 | 0 | 0 | 1 | 53 | 1 | 0 | 0 | 137
7/1/2020 | 8 | 0 | 0 | 2 | 72 | 1 | 0 | 0 | 117
7/2/2020 | 5 | 0 | 0 | 4 | 60 | 5 | 0 | 0 | 123
7/3/2020 | 9 | 0 | 8 | 30 | 77 | 52 | 0 | 0 | 25
Note: a positive value indicates that the corrected or proposed price is higher than the original price.
* This column does not include prices that were not affected.

## Slide 8: Potential DAM Price Correction Price Impacts
** For 7/7/2020, corrected DAM prices were posted prior to becoming final.
OD | Number of constraints with the impacted transformers | Count of Changes in Price for the 4 Hubs and 4 Competitive Load Zones across all Hourly Intervals of the Affected ODs |  |  |  |  |  |  | 
 |  | < -$10/MWh | >= -$10/MWh & < -$1/MWh | >= -$1/MWh & < -$0.1/MWh | >= -$0.1/MWh & < $0.1/MWh* | >= $0.1/MWh & < $1/MWh | >= $1/MWh & < $10/MWh | >= $10/MWh | No change
7/4/2020 | 7 | 0 | 1 | 0 | 83 | 6 | 0 | 0 | 102
7/5/2020 | 14 | 0 | 0 | 10 | 73 | 10 | 0 | 0 | 99
7/6/2020 | 16 | 0 | 0 | 23 | 82 | 16 | 0 | 0 | 71
7/7/2020** | 15 | 0 | 0 | 28 | 70 | 2 | 0 | 0 | 92
Note: a positive value indicates that the corrected or proposed price is higher than the original price.
* This column does not include prices that were not affected.

## Slide 9: Potential DAM Price Correction Settlement Impacts
 | Energy Purchases |  | Energy Sales |  | PTP Purchases |  | CRR Settlements |  | AS Payments |  | Make-whole Payment | 
6/8/2020 | (214.1) | 0.4% | 211.0 | 0.4% | 6.9 | 0.5% | (7.9) | 0.4% | 6.3 | 0.2% | (0.4) | 97.4%
6/9/2020 | (566.1) | 2.6% | 569.5 | 2.8% | 15.2 | 0.4% | (21.9) | 0.6% | 42.3 | 5.2% | 0.0 | 0.0%
6/10/2020 | 5.1 | 0.0% | (5.0) | 0.0% | 0.0 | 0.0% | (0.2) | 0.0% | 0.9 | 0.2% | 0.0 | 0.0%
6/11/2020 | 262.6 | 2.0% | (260.9) | 2.1% | 17.1 | 1.0% | (19.9) | 0.9% | (13.2) | 3.0% | 0.0 | 0.0%
6/12/2020 | 465.9 | 3.4% | (462.9) | 3.4% | 9.1 | 0.9% | (10.5) | 0.7% | (19.7) | 4.5% | 0.0 | 0.0%
6/15/2020 | 893.5 | 5.8% | (895.8) | 6.0% | 14.7 | 1.3% | (9.3) | 0.7% | (33.3) | 6.7% | 0.4 | 84.2%
6/16/2020 | (0.0) | 0.0% | (0.1) | 0.0% | (0.9) | 0.0% | 1.1 | 0.0% | (0.0) | 0.0% | (0.0) | 0.0%
6/17/2020 | 61.5 | 0.5% | (59.2) | 0.5% | 1.5 | 0.0% | (2.6) | 0.1% | (2.5) | 0.6% | (0.0) | 0.8%
6/19/2020 | (0.2) | 0.0% | 0.5 | 0.0% | (0.4) | 0.0% | (0.3) | 0.0% | (0.0) | 0.0% | 0.0 | 0.0%
Note: all Settlement amounts are net amounts due to/from ERCOT in $ thousands.

## Slide 10: Potential DAM Price Correction Settlement Impacts
 | Energy Purchases |  | Energy Sales |  | PTP Purchases |  | CRR Settlements |  | AS Payments |  | Make-whole Payment | 
6/20/2020 | (0.1) | 0.0% | (0.2) | 0.0% | 0.3 | 0.0% | 0.8 | 0.1% | (0.0) | 0.0% | 0.0 | 0.0%
6/24/2020 | 118.2 | 0.9% | (117.6) | 0.9% | 1.7 | 0.7% | (1.2) | 0.4% | (0.4) | 0.1% | 0.0 | 100.0%
6/25/2020 | (42.9) | 0.3% | 42.6 | 0.4% | (0.2) | 0.0% | 0.3 | 0.0% | 0.7 | 0.2% | 0.0 | 0.0%
6/28/2020 | 51.4 | 0.5% | (52.6) | 0.6% | 0.5 | 0.0% | 0.7 | 0.0% | (2.1) | 0.6% | (0.5) | 1.0%
6/29/2020 | 61.4 | 0.5% | (68.4) | 0.6% | (6.6) | 0.3% | 11.2 | 0.4% | (3.5) | 0.8% | 0.0 | 0.1%
6/30/2020 | (1.2) | 0.0% | (0.6) | 0.0% | (3.7) | 0.2% | 4.5 | 0.1% | 0.0 | 0.0% | 0.0 | 0.0%
7/1/2020 | (1.5) | 0.0% | 3.2 | 0.0% | (4.6) | 0.2% | 3.5 | 0.2% | 0.1 | 0.0% | (0.0) | 0.0%
7/2/2020 | 3.8 | 0.0% | (6.9) | 0.0% | (1.0) | 0.1% | 4.2 | 0.3% | 0.1 | 0.0% | 0.0 | 0.0%
7/3/2020 | (4.4) | 0.0% | 13.7 | 0.1% | (16.4) | 1.7% | 11.5 | 1.1% | (0.6) | 0.1% | 0.0 | 0.0%
Note: all Settlement amounts are net amounts due to/from ERCOT in $ thousands.

## Slide 11: Potential DAM Price Correction Settlement Impacts
 | Energy Purchases |  | Energy Sales |  | PTP Purchases |  | CRR Settlements |  | AS Payments |  | Make-whole Payment | 
7/4/2020 | 13.9 | 0.1% | (5.1) | 0.0% | (1.3) | 0.1% | (4.1) | 0.3% | (0.1) | 0.0% | 0.0 | 0.0%
7/5/2020 | (1.3) | 0.0% | 6.0 | 0.0% | (12.3) | 1.5% | 9.2 | 1.0% | 0.5 | 0.1% | 0.0 | 0.0%
7/6/2020 | 11.5 | 0.1% | 0.7 | 0.0% | (23.8) | 2.5% | 17.1 | 1.5% | (0.0) | 0.0% | 0.0 | 0.0%
7/7/2020* | (35.8) | 0.2% | 49.7 | 0.3% | (5.0) | 0.5% | (0.3) | 0.0% | (2.6) | 0.6% | 0.0 | 0.0%
* For 7/7/2020, corrected DAM prices were posted prior to becoming final.
Note: all Settlement amounts are net amounts due to/from ERCOT in $ thousands.

## Slide 12: DAM Price Correction Settlement Impacts on Counter-Parties
OD | Maximum Impact to Counter-Parties |  | OD | Maximum Impact to Counter-Parties | 
 | Maximum Amount* | Maximum Percentage** |  | Maximum Amount* | Maximum Percentage**
6/8/2020 | 10.67 | 40.3% | 6/20/2020 | 0.29 | NA
6/9/2020 | 35.25 | 56.5% | 6/24/2020 | 3.33 | 589.6%
6/10/2020 | 1.19 | 0.7% | 6/25/2020 | 4.17 | 1.1%
6/11/2020 | 7.97 | 72.3% | 6/28/2020 | 7.20 | 461.2%
6/12/2020 | 14.49 | 33.5% | 6/29/2020 | 4.12 | 14.0%
6/15/2020 | 30.06 | 234.2% | 6/30/2020 | 0.37 | NA
6/16/2020 | 0.15 | NA | 7/1/2020 | 1.21 | 1.8%
6/17/2020 | 6.06 | 6.5% | 7/2/2020 | 1.99 | 40.3%
6/19/2020 | 0.45 | NA | 7/3/2020 | 8.62 | 102.4%
** The maximum of percentage change to any single Counter-Party with impact more than $500 (set as NA when no single counter party has impact more than $500)
* The maximum of absolute impact to any single Counter-Party in $ thousands

## Slide 13: DAM Price Correction Settlement Impacts on Counter-Parties
OD | Maximum Impact to Counter-Parties |  | OD | Maximum Impact to Counter-Parties | 
 | Maximum Amount* | Maximum Percentage** |  | Maximum Amount* | Maximum Percentage**
7/4/2020 | 2.93 | 2.2% | 7/6/2020 | 7.66 | 36.6%
7/5/2020 | 4.29 | 8.2% | 7/7/2020*** | 8.54 | 122.1%
** The maximum of percentage change to any single Counter-Party with impact more than $500 (set as NA when no single counter party has impact more than $500)
* The maximum of absolute impact to any single Counter-Party in $ thousands
*** For 7/7/2020, corrected DAM prices were posted prior to becoming final.

## Slide 14: Potential Price Correction
Market: RTM
Impacted ODs: 7/1/2020
Price Correction Methodology: ERCOT reran the impacted SCED intervals with correct ratings on the impacted transformers.
The following slides include analysis of the price and Settlement impacts of RTM price correction using the new RTM solution.

## Slide 15: Potential RTM Price Correction Price Impacts
N | Number of impacted Settlement Intervals | Count of Changes in Price for the 4 Hubs and 4 Competitive Load Zones across all 15-minute Settlement Intervals of the Affected ODs |  |  |  |  |  |  | 
 |  | < -$10/MWh | >= -$10/MWh & < -$1/MWh | >= -$1/MWh & < -$0.1/MWh | >= -$0.1/MWh & < $0.1/MWh* | >= $0.1/MWh & < $1/MWh | >= $1/MWh & < $10/MWh | >= $10/MWh | No Change
7/1/2020 | 8 | 8 | 15 | 10 | 2 | 11 | 18 | 0 | 0
Note: a positive value indicates that the corrected or proposed price is higher than the original price.
* This column does not include prices that were not affected.

## Slide 16: Potential RTM Price Correction Settlement Impacts
 | Energy Imbalance |  | PTP Obligation |  | RENA |  | Emergency Energy | 
7/1/2020 | (303.4) | 19.9% | 518.1 | 29.4% | (213.7) | 62.0% | 60.1 | 1814.2%
OD | Maximum Impact to Counter-Parties | 
 | Maximum Amount* | Maximum Percentage**
7/1/2020 | 46.9 | 1359.6%
* The maximum of absolute impact to any single Counter Party in $ thousands
** The maximum of percentage change to any single Counter-Party with impact more than $500 (set as NA when no single counter party has impact more than $500)