## Slide 1
DGR ICCP Requirements
7/18/2020

## Slide 2: DGR ICCP Requirements
Background
Example: “Physically” In The Field
Example: How It Gets Modeled
Example: “Known” Telemetry
Example: “Troublemaking” Telemetry
Example: “Ideal” Telemetry Layout
Example: What if no Load Telemetry?
Q/A

## Slide 3: Background
Stuff
DGR
Transmission Network
Distribution Network
There is currently 10 DGRs in the
Network Operations Model
Multiple TSPs have reached out
to ERCOT in regards clarification on
Telemetry is required by the TSP.
ERCOT Operations personnel been told
one thing but Modeling told another.

## Slide 4: Example: “Physically” In The Field
Line
Transmission Network
Feeders (to load)
TSP Station
DESR Station
+
-
+
-
+
-
+
-
Inv1
Inv2
Inv3
Inv4
XF 34.5 kV/.55 kV
34.5 kV
34.5 kV
138 kV
XF 138 kV/34.5 kV

## Slide 5: Example: How It Gets Modeled
Line
Transmission Network
TSP Station
DESR Station
34.5 kV
34.5 kV
138 kV
XF 138 kV/34.5 kV
DGR
+
-
+
-
+
-
+
-
Inv1
Inv2
Inv3
Inv4
XF 34.5 kV/.55 kV
Feeders (to load)
CIM LOAD

## Slide 6: Example: “Known” Telemetry
Line
Transmission Network
TSP Station
DESR Station
34.5 kV
34.5 kV
138 kV
XF 138 kV/34.5 kV
DGR
+
-
+
-
+
-
+
-
Inv1
Inv2
Inv3
Inv4
XF 34.5 kV/.55 kV
Feeders (to load)
CIM LOAD
MW and MVAR Telemetry
MW and MVAR Telemetry

## Slide 7: Example: “Troublemaking” Telemetry
Line
Transmission Network
TSP Station
DESR Station
34.5 kV
34.5 kV
138 kV
XF 138 kV/34.5 kV
DGR
+
-
+
-
+
-
+
-
Inv1
Inv2
Inv3
Inv4
XF 34.5 kV/.55 kV
Feeders (to load)
CIM LOAD
???

## Slide 8: Example: “Troublemaking” Telemetry, Con’t
Transmission Network
TSP Station
34.5 kV
138 kV
XF 138 kV/34.5 kV
CIM LOAD
???
ERCOT has no clear indication of what is
available.
Some TSPs mapping the same points from
the low side of the transformer.
Some TSPs mapping DGR telemetry.

## Slide 9: Example: “Ideal” Telemetry Mapping
Line
Transmission Network
TSP Station
DESR Station
34.5 kV
34.5 kV
138 kV
XF 138 kV/34.5 kV
DGR
CIM LOAD
CIM Load MW and MVAR telemetry of all non DGR feeders
Low side of XFMR MW and MVAR telemetry.
DESR end of the Line MW and MVAR telemetry
TSP end of the Line MW and MVAR telemetry

## Slide 10: Example: “Ideal” Telemetry Mapping, Con’t
Line
Transmission Network
TSP Station
DESR Station
34.5 kV
34.5 kV
138 kV
XF 138 kV/34.5 kV
DGR
CIM LOAD
20 MW
11 MW
9 MW
9 MW
Gives the best visibility to ERCOT.
“Should” provide less amount of error in the State Estimator.
Telemetry

## Slide 11: Example: What if no Load Telemetry?
Line
Transmission Network
TSP Station
DESR Station
34.5 kV
34.5 kV
138 kV
XF 138 kV/34.5 kV
DGR
CIM LOAD
Low side of XFMR MW and MVAR telemetry.
DESR end of the Line MW and MVAR telemetry
TSP end of the Line MW and MVAR telemetry

## Slide 12: Example: What if no Load Telemetry?, Con’t
Line
Transmission Network
TSP Station
DESR Station
34.5 kV
34.5 kV
138 kV
XF 138 kV/34.5 kV
DGR
CIM LOAD
20 MW
11 MW
9 MW
9 MW
Telemetry
State Estimator Estimation
State Estimator should be able to calculate the load.

## Slide 13: Q & A
QUESTIONS?