## Slide 1
Energy Storage Resource
Responsive Reserve Service
Qualification Process
Operations Analysis
4/15/2020

## Slide 2: Topics
Summary
RRS AS Qualification Test
NDCRC Primary Frequency Response Test
RRS Hourly Capability Test
RRS MW Qualification Amount Calculation
Timeline

## Slide 3: Summary
ESRs looking to obtain RRS qualification will have to submit the following tests for evaluation by ERCOT
  RRS AS Qualification Test
  NDCRC Primary Frequency Response Test
  RRS Hourly Capability Test
ERCOT will evaluate the three tests and will identify RRS qualification as well as the RRS Percentage Limit for the Resource
RRS Percentage Limits will be identified through a model change request

## Slide 4: RRS AS Qualification Test
Qualification tests allow the Resource Entity and QSE to demonstrate the minimum capabilities necessary to deploy an AS
The RRS test is performed during a continuous 8 hour window per Protocols Section 8.1.1.2.1.2 (8)
Test Evaluation
  ESR GR and CLR are tested separately
  Must verify that the QSE updated its AS Schedule for the Resource desiring qualification within 15 seconds of the RRS signal deployment

## Slide 5: NDCRC Primary Frequency Response Test
Separate tests will be performed for the ESR-GR and ESR-CLR
Tests will show Resource’s response to a +/-0.2Hz frequency offset from the deadband
The Actual PFR will be measured against the Expected PFR and used to identify a Passed or Failed test
The submitted values will be used to identify a calculated droop which is used in determining the RRS Percentage Limit for the Resource

## Slide 6: RRS Hourly Capability Test
General capacity testing must be used to verify a Resource’s Net Dependable Capability (Protocols Section 8.1.1.1 (2))
QSE provides ERCOT the start and end timestamps for when the ESR-GR and ESR-CLR provided a sustained hour long output
  ESR-GR will inject
  ESR-CLR will charge
ERCOT will use telemetry data received to evaluate the MW level at which the Resource may be qualified
  Identified MW capability is compared against the submitted HSL to identify a potential RRS Percentage Limit

## Slide 7: RRS Hourly Capability Test Cont.
When evaluating the hourly capability test, ERCOT is expecting the following:
  The resource will not respond to frequency deviations during the sustained hour long testing period
  The submitted data for the Resource’s hourly capability test shall not include the periods where the Resource is ramping up to the qualification MW amount and ramping down to pretest output levels
  The 5th percentile will be used to identify the hourly capability of the Resource

## Slide 8: Calculating the RRS Percentage Limit
An RRS Percentage Limit will be identified once the RRS AS Qualification Test, RRS Hourly Capability Test, and NDCRC PFR Tests are submitted
RRS Percentage Limit is initially identified as the minimum of:
  RRS Percentage Limit derived from the NDCRC calculated droop
  RRS Percentage Limit derived from the RRS Hourly Capability Test

## Slide 9: Finalize RRS Qualification Process
ERCOT will finalize the RRS Percentage Limit and RRS Qualification status for the qualifying Resource within 7 days of receiving all three requisite tests
The RRS Percentage Limit will be incorporated into the model through the next available snapshot
  Typically, a model is pushed into production about two weeks after the snapshot is taken
Once the RRS Percentage Limit is incorporated into the production model, RRS AS offers may be submitted into DAM with accordance to the new updated RRS Percentage Limits
  RRS Qualified Resources will initially have the default RRS Percentage Limit of 20%
  MW offers will be limited by the identified RRS Percentage Limit

## Slide 10: Timeline
3 Requisite Tests submitted
Current Day
CD + 7 BD
ERCOT will provide qualification results and submit Model CR
CD + 14 – 21 Days
Updated RRS Percentage Limits Incorporated into Model and Visible to DAM
* Current Day (CD), Business Days (BD)

## Slide 11: Questions?
Thank you!

## Slide 12: Acronyms Used
AS – Ancillary Service
CLR – Controllable Load Resource
CR – Change Request
DAM – Day Ahead Market
ESR – Energy Storage Resource
GR – Generation Resource
NDCRC – Net Dependable Capability and Reactive Capability
QSE – Qualified Service Entity
RRS – Responsive Reserve Service