## Slide 1: MWG Update to WMS
October 7, 2020
Presented by: Gabriel Godinez
MWG Chair

## Slide 2: ERCOT Analysis of Line Loss Data
Philosophical agreement on the acceptability to ignore small line distances.
Solution proposed implementing max expected current at site (based on load/generation) versus max CT current.
  Current formulas for determining watts copper loss in a radial line use CT ratio as maximum expected current.
  ERCOT agreed to consider the concept and will bring back their review at the next MWG meeting.
Action Item: ERCOT review language for a potential SMOG change based on % watt copper less than 0.001%. Including in the review the impact of using maximum current based on the site generation/load.

## Slide 3: WSL Configuration Examples and Calculations spreadsheet
Interactive sheet provides various scenarios of ESR/WSL and illustrates ERCOT data aggregation calculations.
Request for participants to work through examples and provide feedback on anything they see that seems unexpected.

## Slide 4: Review Design Proposal Section D Draft and Instructions
TDSP question on why there is a Box 40, ESR Auxiliary Load Normal Expected Value.
  Action Item: ERCOT to discuss internally the requirement of Box 40 and either provide a recommendation to remove the field or provide detailed reasoning for the field to remain at the next MWG.
Discussion on instruction section from Numbers 41-43.
  Edits made to numbers 42 & 43 updating requirements.
  More edits might be needed to ensure required information is detailed properly.

## Slide 5: SMOG Language Changes to Support NPRR1020
To provide optionality, edits were made to support calculation of WSL being done in either the EPS meter or in the ERCOT Data Aggregation System.
One concept that requires further discussion: Standalone meter to record auxiliary load calculation. More to come.
Questions regarding how communications to resource entity will be handled if the only issue is the value coming to the EPS meter.
Action Item: ERCOT to discuss internally to formulate a recommendation regarding how loss of telemetry will be communicated to the resource entity.

## Slide 6: SMOG Language Changes to Support NPRR1020 (cont’d)
Edits made to ensure clarity that the calculated auxiliary load values are sent to both primary and backup meter.
Some minor concepts to resolve, such as sample rate for aux load calculation.
Action Item: ERCOT and TDSPs review within their respective organizations to have recommendations regarding sample rates for auxiliary load calculation.

## Slide 7: New or Other Business Items
ERCOT provided remarks on expectations regarding meter data and requests to modify the data.
  Any requests to zero the recorded EPS meter data should have specific reason that can be justified by technical analysis.

## Slide 8: Upcoming Meeting
Next MWG WebEx scheduled for 10/20/20 @ 1:00 pm.