| SMOGRR Number | 023 | SMOGRR Title | Updates to Nameplate Information Requirements |
| --- | --- | --- | --- |
| Date of Decision |  | October 7, 2020 |  |
| Action |  | Recommended Approval |  |
| Timeline |  | Normal |  |
| Proposed Effective Date |  | November 1, 2020 |  |
| Priority and Rank Assigned |  | Not Applicable |  |
| Settlement Metering Operating Guide Sections Requiring Revision |  | 3.2.3, Site Approval Request Package 7.5.2, Nameplate Data 7.5.6, Insulating Oil (if present) (delete) |  |
| Related Documents Requiring Revision/Related Revision Requests |  | None |  |
| Revision Description |  | This Settlement Metering Operating Guide Revision Request (SMOGRR) provides an option for certification of nameplates of newly installed or replaced instrument transformers by a professional engineer when nameplate photos cannot be physically accessed because the instrument transformers are installed inside other equipment apparatus, replaces a list of instrument transformer nameplate data requirements with a reference to the Institute of Electrical and Electronics Engineers (IEEE) standards, and deletes Section 7.5.6. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | This SMOGRR (1) allows a Transmission and/or Distribution Service Provider (TDSP) to complete site certification, and ERCOT to approve a site, when nameplate photos of instrument transformers cannot be obtained, (2) aligns nameplate information requirements with industry requirements, and (3) recognizes that polychlorinated biphenyl content in insulating oil is no longer allowed in the manufacture of instrument transformers. |  |
| WMS Decision |  | On 9/2/20, WMS voted via roll call to recommend approval of SMOGRR023 as submitted. There was one abstention from the Independent Generator (Luminant) Market Segment. All Market Segments were present for the vote. On 10/7/20, WMS voted unanimously via roll call to endorse and forward to TAC the 9/2/20 WMS Report and Impact Analysis for SMOGRR023. All Market Segments were present for the vote. |  |
| Summary of WMS Discussion |  | On 9/2/20, there was no discussion. On 10/7/20, there was no discussion. |  |

| Sponsor |  |
| --- | --- |
| Name | Don Tucker |
| E-mail Address | Donald.Tucker@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-3913 |
| Cell Number |  |
| Market Segment | ERCOT |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Brittney Albracht |
| E-Mail Address | Brittney.Albracht@ercot.com |
| Phone Number | 512-225-7027 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| None |  |

Market Rules Notes

None

Proposed Guide Language Revision

### 3.2.3	Site Approval Request Package

(1)	The Site Approval Request Package should be provided within 60 days after the site has been certified and must include:

(a)	Site Certification Form;

(b)	EPS Meter Test Report;

(c)	Copy of Meter Programming File;

(d)	TDSP meter multiplier calculation sheet as prescribed in Section 3.3, Calculation Sheet Requirements;

(e)	TDSP pulse multiplier calculation sheet as prescribed in Section 3.3;

(f)	TDSP transformer and line loss compensation calculation sheet as prescribed in Section 3.3;

(g)	Certification of instrument transformers.  Such certification shall include the nameplate information and either a manufacturer’s certificate of test (preferred) or certification by a professional engineer registered in the State of Texas.  Such certification shall include the criteria used to certify that such instrument transformer’s accuracy is in compliance with Protocol Section 10, Metering, and this Settlement Metering Operating Guide (SMOG);

(h)	Redlined or final as built detailed one-line drawings of the complete metering facility and a three line drawing detailing the metering circuit with TDSP EPS Meter Inspector’s initials.  Note:  If a redlined version is supplied, the final as built drawings shall be submitted within 45 days of the submittal of the Site Approval Request Package;

(i)	Readable photos of the nameplates of newly installed or replaced instrument transformers.  When instrument transformers are physically located inside an apparatus and nameplate photos cannot be provided, a statement bearing the seal of a professional engineer registered in the State of Texas must be submitted instead of the nameplate photos.  Such statement shall provide all nameplate information for the instrument transformer(s), a certification that the information provided represents the installed equipment, and the basis for the certification; and

(j)	Other information as required.

### 7.5.2	Nameplate Data

(1)	Nameplate information should conform to IEEE C57.13 in effect at the time of instrument transformer manufacture.