## Slide 1
ERCOT Frequency Control Report
September 2020
ERCOT
Operations Planning
PDCWG | October 14th, 2020

## Slide 2: Summary of September 2020
CPS1: 173.56%
Current CPS1 12-Month Rolling Average: 172.43%
0 BAAL Exceedance
2 hourly CPS1 score below 100%
BAAL-003 Events have updated through 2019
2019 BAAL-003 FRM Performance: -811.14
2020 RMS1 Statistics
  Mean: 16.05 mHz
  Min: 12.25 mHz
  Max: 22.6 mHz
Energy Statistics
  Total Energy: 32,735,862 MWh
  Wind Energy: 5,026,960 MWh
  Percent Energy from Wind: 15.36%
  Solar Energy: 782,376 MWh
  Percent Energy from Solar: 2.39%
Minimum System Inertia
  Mean: 238, 595 MW*s
  Max: 285,477 MW*s on Sep 3rd
  Min: 168,441 MW*s on Sep 27th
Notes: 2018 BAAL-003 FRM Performance: -843.17

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
Sep-20 CPS1 (%): 173.56
Notes: Outliers:
1. 95.70% @ 9/11/2020 17:00
  Expected Gen Dev:
  Large exp. Gen. dev of -739 MW @ 17:59 mostly due to solar
  Large exp. Gen. dev of -605 MW @ 17:23 mostly due to solar
  Wind/Solar Ramp:
  A 520 MW Solar down-ramp within a 23 minute period in the middle of the hour.
  A 206 MW Solar down-ramp within a 5 minute period at the end of the hour.
  Regulation: Regulation up exhausted for over half of the hour
70.10% @ 9/28/2020 18:00
  Expected Gen Dev:
  Expected gen dev remains negative throughout the entire hour.
  Large exp. Gen. dev of -1969 @ 18:39 mostly due to solar and wind units
  Large exp. Gen. dev of -2262 @ 18:39 mostly due to solar and wind units
  Wind/Solar Ramp: Wind and solar consistently ramp down sharply during the second half of the hour.
  Solar ramps down from 1452 MW to 438 MW between 18:30and 19:00
  Wind ramp down from 13443 MW to 11799 MW between 18:30 and 19:00.
  Regulation: Regulation up exhausted for the most part of the hour.
  Manual SCED Rest: A manual SCED reset at 18:47 due to frequency drag, reg up fully deployed and renewables sharply ramping down.

## Slide 5: BAAL Exceedances & Violations
There was 0 BAAL exceedance in Sep

## Slide 6: 15-Minute Average CPS1%
Sep-20 CPS1 (%): 173.56

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 172.43%

## Slide 8: Daily RMS1 of ERCOT Frequency by Year

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2019 BAL-003 Selected Events – Update
Notes: BAL-003

## Slide 19: Op. Year 2018 BAL-003 FRM Performance - Update
Notes: OP2018: FRO = -381.0, FRM_median = -843.17, FRM_average = -959.7
OP2019: FRO = -381.0, FRM_median = -811.14, FRM_average = -892.5
OP2020: FRO = -425.0,

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 32,735,862 MWh

## Slide 22: Total Energy from Wind Generation
Notes: 5,026,960 MWh

## Slide 23: % Energy from Wind Generation
Notes: 15.36%

## Slide 24: Total Energy From Solar Generation
Notes: 782,376 MWh

## Slide 25: % Energy from Solar Generation
Notes: 2.39%

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia = 168,441 MW*s on 9/27/2020
Previous Minimum was 128,759 MW*s on 11/18/2018.
Data:
Mean: 238,595
Max: 285,477 on Sep 3rd
Min: 168,441 on Sep 27th

## Slide 28: Questions?
Thank you!