## D. Auxiliary load telemetry DETAILS

Telemetry Details Form:

Specific information for each ESR Auxiliary Load Telemetry being supplied to an EPS meter included in the EPS Metering Design Proposal.  A “Auxiliary Load Telemetry Details” form will need to be completed for each EPS meter point that has ESR Auxiliary Load Telemetry supplied. This section should be duplicated and additional copies of Section D should be used for each ESR Auxiliary Load Telemetry provided to an EPS meter. The information in this section should be provided by the resource owner to the TDSP.

G

- Unit or Load Name:

This field refers to the individual meter point that the ESR Auxiliary Load Telemetry is being supplied to.  This name should match the TDSP supplied name from B22.

- TDSP Project #:

A number assigned by the TDSP to each EPS Metering Design Proposal.  This number should be limited to ten (10) alphanumeric characters and should match the number assigned in box A10.

- Meter ID as shown on TDSP one-line:

This should be the name of the meter that will be supplied ESR Auxiliary Load Telemetry as listed on the TDSP one-line diagrams supplied with the Design Proposal. This name should match the TDSP supplied name from B25.

- ESR Auxiliary Load Max Expected Value

The maximum of load value that the resource entity expect the ESR auxiliary load to draw while the ESR is charging.

- WSL Calculation Location: Meter or Data Aggregation

Indicate if the wholesale storage load value will be calculated in the EPS meter or if it will be performed in the ERCOT Data Aggregation system. If the WSL will be calculated in the meter, supporting documents showing how the calculations will be performed in compliance with Protocol 11.1.6(3)(a) and SMOG 4.1(1)(d). Supporting documents should be listed in box D48 “Additional Comments\Documents”.

- Confirmation that ESR Auxiliary Load Cannot be Separately Metered

Documentation describing the reason that the auxiliary load meets the requirement of Protocol 10.2.4(1) and cannot be separately metered and must be calculated. This shall include a one-line drawing that includes facility details necessary to understand the calculation and data flow.

- Load calculation Equipment and Methodology

A description of the equipment and method used to determine the auxiliary load value and telemeter the auxiliary load value to the appropriate EPS meter shall be provided. This description shall include how the calculated auxiliary load will always be equal to or greater than the true auxiliary load, the equipment used in determining the auxiliary load calculation, and the accuracy of equipment used. If a zero load value will be telemetered while the ESR is discharging, the methodology for determining when zero will be telemetered must be included in the description.

- Description of performed or planned testing to support accuracy

A description of the anticipated annual audit process, any laboratory or field testing that has already been performed, information on anticipated equipment, and other information. Laboratory or field testing may include but is not limited to highly accelerated life testing or removal and replacement of a sample of equipment on a regular basis for testing. Regardless of the methodologies used, a chosen methodology must be sufficiently useful for a Texas Professional Engineer to use in required affidavit.

- Provided By

Name of the Resource Entity representative that is providing the supporting documents. This may be multiple contacts.

- Date Provided

Date the Resource Entity contact in D45 provided the supporting documents.

- Contact Email Address(es)

Contact email address for the Resource Entity representative(s) listed in D44.

- Contact Phone Number(s)

- Contact phone number(s) for the Resource Entity representative(s) listed in D44.

- Additional Comments\Documents

Provide any clarifying comments or names of additional supporting documents.