## Slide 1
Ancillary Service Methodology
Preliminary Quantities For 2021
Oct 27, 2020
WMWG
ERCOT Staff

## Slide 2: Stakeholder Discussion Timeline
September 08, 2020 – PDCWG (Visit 1)
September 21, 2020 – WMWG (Visit 1)
October 14, 2020 – PDCWG (Visit 2)
October 19, 2020 – WMWG (Visit 2)
October 23, 2020 – OWG
November 04, 2020 - WMS
November 05, 2020 - ROS
November 18, 2020 - TAC
December 8, 2020 - BoD

## Slide 3: Scope of Discussion
ERCOT is not recommending any changes to the methodologies for determining Responsive Reserve Service (RRS) for 2021.
  The quantities for RRS, RRS-PFR and RRS-LR posted in the spreadsheets use a RRS-PFR limit of 1150 MW.
  ERCOT is working with NERC to update ERCOT’s Resource Contingency Criteria (RCC) to 2805 MW in NERC's 2020 BAL-003 Interconnection Frequency Response Obligation (IFRO) assessment for 2021. As a result of this, ERCOT expects that the minimum RRS-PFR limit for 2021 may change.
ERCOT is recommending changes to the methodologies used for computing Non-Spin and Regulation reserves for 2021 to account for growth in installed PVGR capacity.
The Ancillary Service (A/S) quantities for 2021 contained in this presentation are based on the methodology that was approved in December 2018.
  The quantities for 2021 reflect moving forward the historic data on which these are based, unless otherwise noted.
  Spreadsheets that contain the associated quantities for January through September of 2021 have been posted on the meeting page for this WMWG meeting.
ERCOT is seeking stakeholder feedback for changes to the 2021 A/S Methodology.

## Slide 4
Responsive Reserve Service

## Slide 5: Responsive Service Methodology (RRS) - 2021
The preliminary RRS quantities for January 2021 through September 2021 in subsequent slides have been computed using 2019 and 2020 system inertia conditions and RRS table updated in 2020.
  The RRS table tracks RRS requirements for different inertia conditions. This table was updated in 2020 to use a Resource Contingency Criteria of 2805 MW in associated studies.
  The quantities for RRS, RRS-PFR and RRS-LR posted in the spreadsheets use a RRS-PFR limit of 1150 MW. ERCOT is working with NERC to update ERCOT’s Resource Contingency Criteria (RCC) to 2805 MW in NERC's 2020 BAL-003 Interconnection Frequency Response Obligation (IFRO) assessment for 2021. As a result of this, ERCOT expects that the minimum RRS-PFR limit for 2021 may change.

## Slide 6: RRS Table - 2020
 | Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4 | Scenario 5 | Scenario 6 | Scenario 7 | Scenario 8 | Scenario 9 | Scenario 10 | Scenario 11 | Scenario 12
LR/PFR | 2.35:1 | 2.2:1 | 2.06:1 | 1.94:1 | 1.83:1 | 1.74:1 | 1.65:1 | 1.58:1 | 1.51:1 | 1.44:1 | 1.39:1 | 1.33:1
Inertia (GW∙s) | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240
PFR Req. (no LR) (MW) | 5960 | 5563 | 5200 | 4892 | 4622 | 4329 | 4114 | 3920 | 3744 | 3522 | 3314 | 3139
*RRS (MW) | 3293 | 3234 | 3178 | 3128 | 3086 | 2998 | 2959 | 2908 | 2868 | 2797 | 2707 | 2645
 | Scenario 13 | Scenario 14 | Scenario 15 | Scenario 16 | Scenario 17 | Scenario 18 | Scenario 19 | Scenario 20 | Scenario 21 | Scenario 22 | Scenario 23 | Scenario 24 | Scenario 25
LR/PFR | 1.28:1 | 1.24:1 | 1.19:1 | 1.15:1 | 1.12:1 | 1.08:1 | 1.04:1 | 1.01:1 | 1:1 | 1:1 | 1:1 | 1:1 | 1:1
Inertia (GW∙s) | 250 | 260 | 270 | 280 | 290 | 300 | 310 | 320 | 330 | 340 | 350 | 360 | 370
PFR Req. (no LR) (MW) | 3004 | 2890 | 2784 | 2686 | 2595 | 2510 | 2421 | 2353 | 2290 | 2230 | 2173 | 2119 | 2068
*RRS (MW) | 2598 | 2553 | 2523 | 2486 | 2440 | 2409 | 2372 | 2341 | 2290 | 2230 | 2173 | 2119 | 2068
*RRS quantity is calculated with limit of 60% limit on LRs and min RRS-PFR limit of 1150 MW.
**Red font in table above identifies study scenario where RRS needed < 2300 MW. 2300 MW floor will be used in RRS requirement determination.
***Generation mix (CCs, Gas, SC, Coal, Steam) providing 1150 MW of PFR has been aligned with actual historic system operations.
Inertia < 250 GW·s: 30% Coal + 70% Rest. Inertia ≥ 250 GW·s: 15% Coal + 85% Rest

## Slide 7: RRS January
Notes: Trends between blue and red are fairly similar.
Max Change in HE7-10 is 71 MW
On an average decrease of 18 MW

## Slide 8: RRS March
Notes: Trends between blue and red are fairly similar.
Max Change in HE7-10 is 51 MW
On an average decrease of 36 MW

## Slide 9: RRS June
Notes: Trends between blue and red are fairly similar.
Max Change in HE3-6 is 109 MW
On an average decrease of 48 MW

## Slide 10: Hourly Average RRS Comparison
Notes: On an average red is similar to blue.
On an average largest increase in red is 53 MW in May

## Slide 11
Regulation

## Slide 12: Regulation Service Methodology - 2021
ERCOT is proposing to create and incorporate Solar Adjustment tables into the Regulation Service Methodology similar to the Wind Adjustment tables.
  Solar Adjustment tables will track incremental MWs of Regulation needed to account for additional variability per 1000 MW increase in installed solar capacity.
The preliminary Regulation quantities for January 2021 through September 2021 in subsequent slides have been computed using current methodology (2019 and 2020 five-minute net load variability), updated Wind Adjustment tables and the proposed Solar Adjustment tables.

## Slide 13: Wind Adjustment Tables - 2021
Notes: Avg Reg Up adjustment for wind is 3 MW
Avg Reg Down adjustment for wind is 2 MW

## Slide 14: Projected Solar Installed Capacity
ERCOT’s Resource Capacity Trends report has been projecting large increases in installed solar installed capacity in the next two years.
  ERCOT currently has 3,275 MW of installed solar capacity with an additional 930 MW grid synchronized, awaiting commercial operations approval. ERCOT projects to add additional 7,529 MW of solar capacity by end of 2021.
*Chart is based on the May Resource Capacity Trends report.
  Increasing solar installed capacities will result in increased solar MW ramping due to diurnal solar pattern
  Majority of new solar projects are expected to be concentrated in the regions where existing PVGR resources are located, resulting in potential for larger MW impacts due to clouds
  This will result in increased reliance on Regulation during solar MW ramping periods

## Slide 15: Trend in Solar ramp and Regulation Exhaustion
As solar installed capacity has increased, the magnitude of 5-minute solar ramps have increased and there have been more instances where regulation has been exhausted.
Notes: For each year, 5-min solar ramp rate values were examined in bins of 10 MWs (as tracked on x-axis) and the average rate of intervals during which regulation was exhausted (i.e. remaining regulation was less than 5 MW) was computed (as tracked on y-axis). For example using the dot (400, 0.5) in the 2020 graphic below as an example - this dot represents that in 2020, regulation was exhausted in 50% of the time during which the ramp was between 390 and 400 MW.

## Slide 16: Trends in Hourly Average CPS1
Visible declining trend in hourly average CPS1 during evening/sunset hours. Not low enough to trigger more Regulation in those hours per current methodology.
Notes: If it is determined that during the course of the year that the ERCOT monthly average for CPS1 score was less than 140% for a specific month, ERCOT will apply an extra 10% of both Reg-Up and Reg-Down for hours in which the CPS1 score was less than 140%. Additionally, if the ERCOT 12-month rolling average CPS1 score is less than 140%, for the next month ERCOT will procure an extra 10% of both Reg-Up and Reg-Down for hours in which the hourly CPS1 score was less than 140%. This value will increase to 20% if the CPS1 score falls below 100%.

## Slide 17: Solar Adjustment Tables - 2021
Solar Adjustment Tables track incremental MWs of Regulation needed to account for additional variability per 1000 MW increase in installed Wind capacity.
  Heat map below demonstrates the preliminary adjustment needed before the implementation of SCR811.
Reg-Up Adjustment Pre SCR811
Reg-Down Adjustment Pre SCR811
Mean: 15.57 MW per 1000 MW additional solar capacity
Mean: 15.9 MW per 1000 MW additional solar capacity

## Slide 18: 5-min Net-load Variations
Pre SCR 811 Method
Only Short Term Load and Wind ramps are included in Net Load variation assessment similar to current GTBD practice
Post SCR 811 Method
Solar ramp is also included along with Short Term Load and Wind ramps in Net Load variation assessment.

## Slide 19: Solar Adjustment Tables - 2021
Solar Adjustment Tables track incremental MWs of Regulation needed to account for additional variability per 1000 MW increase in installed Wind capacity.
  Heat map below demonstrates the preliminary adjustment needed after the implementation of SCR811.
Reg-Up Adjustment Post SCR811
Reg-Down Adjustment Post SCR811
Mean: 4.76 MW per 1000 MW additional solar capacity
Mean: 5.0 MW per 1000 MW additional solar capacity

## Slide 20: Solar Adjustment Tables - 2021
Notes: Avg Reg Up adjustment for solar pre SCR811 is 16 MW, post SCR811 is 5 MW
Avg Reg Down adjustment for solar pre SCR811 is 16 MW, post SCR811 is 5 MW

## Slide 21: Regulation Up January
Notes: Trends between blue and orange are fairly similar. Largest change is 51 MW in HE13.
Max increase between orange and red is 155 MW in HE17. On an average increase of 38 MW
Max between orange and green is 47 MW in HE16. On an average increase of 12 MW

## Slide 22: Regulation Up March
Notes: Trends between blue and orange are fairly similar. Largest change is 71 MW in HE23.
Max increase between orange and red is 220 MW in HE18. On an average increase of 58 MW
Max between orange and green is 60 MW in HE16,HE17. On an average increase of 23 MW

## Slide 23: Regulation Up June
Notes: Trends between blue and orange are fairly similar. Largest change is 90 MW in HE19.
Max increase between orange and red is 275 MW in HE19. On an average increase of 89 MW
Max between orange and green is 70 MW in HE15. On an average increase of 21 MW

## Slide 24: Regulation Down January
Notes: Trends between blue and orange are fairly similar. Largest change is 27 MW in HE21.
Max increase between orange and red is 165 MW in HE10. On an average increase of 40 MW
Max between orange and green is 44 MW in HE15. On an average increase of 13 MW

## Slide 25: Regulation Down March
Notes: Trends between blue and orange are fairly similar. Largest change is 36 MW in HE22.
Max increase between orange and red is 158 MW in HE9. On an average increase of 69 MW
Max between orange and green is 71 MW in HE16. On an average increase of 26 MW

## Slide 26: Regulation Down June
Notes: Trends between blue and orange are fairly similar. Largest change is 103 MW in HE14.
Max increase between orange and red is 279 MW in HE9. On an average increase of 91 MW
Max between orange and green is 71 MW in HE17. On an average increase of 23 MW

## Slide 27: Hourly Average Regulation Comparison
Notes: Reg Up
On an average blue and orange are fairly similar
On an average largest increase between orange and red is 89 MW in June
On an average largest increase between green and red is 23 MW in Feb-May
Reg Down
On an average blue and orange are fairly similar
On an average largest increase between orange and red is 91 MW in June
On an average largest increase between green and red is 26 MW in Mar, April

## Slide 28
Non Spin Reserve

## Slide 29: Non Spinning Reserve Methodology (Non-Spin) - 2021
ERCOT is proposing to create and incorporate a Solar Over-Forecast Error Adjustment table.
  Solar Over-Forecast Error Adjustment Table track estimated increase in solar over forecast error per 1000 MW increase in installed solar capacity.
The preliminary Non-Spin quantities for January 2021 through September 2021 in subsequent slides have been computed using current methodology (2018, 2019 and 2020 Net load and Net load Forecast), updated Wind Over-Forecast Error Adjustment table and the proposed Solar Over-Forecast Error Adjustment table.

## Slide 30: Wind Over-Forecast Error Adjustment Table - 2021
Wind Over-Forecast Error Adjustment Table track estimated increase in wind over forecast error per 1000 MW increase in installed wind capacity.
  This table has been updated for 2021.
Max: 41 MW per 1000 MW additional Wind capacity
Mean: 34 MW per 1000 MW additional Wind capacity

## Slide 31: PVGR Forecasting Performance
As solar installed capacity is increasing the Mean Absolute Error (MAE) of both hour-ahead and day-ahead solar forecast is increasing.
MAE: mean absolute error

## Slide 32: Solar Over-Forecast Error Adjustment Table - 2021
Solar Over-Forecast Error Adjustment Table track estimated increase in solar over forecast error per 1000 MW increase in installed solar capacity.
Max: 63 MW per 1000 MW additional solar capacity
Mean: 16 MW per 1000 MW additional solar capacity

## Slide 33: Non-Spin January
Notes: Max Change between 2020 and 2021 in HE19-22 is 146 MW. On an average decrease of 70 MW
Max between 2021 and Adj in HE11-14 is 121 MW. On an average increase of 40 MW
Between 2020 and Adj On an average decrease of 30 MW

## Slide 34: Non-Spin March
Notes: Max Change between 2020 and 2021 in HE11-14 is 136 MW. On an average decrease of 42 MW
Max between 2021 and Adj in HE15-18 is 209 MW. On an average increase of 80 MW
Between 2020 and Adj On an average increase of 38 MW

## Slide 35: Non-Spin June
Notes: Max Change between 2020 and 2021 in HE11-14 is 86 MW. On an average decrease of 8 MW
Max between 2021 and Adj in HE15-18 is 224 MW. On an average increase of 91 MW
Between 2020 and Adj On an average increase of 83 MW

## Slide 36: Hourly Average Non-Spin Comparison
Notes: On an average orange is lower than blue
On an average largest increase in red is 92 MW in May

## Slide 37
Suggestions?