## List
Area | # | Name | Model Status Summary | Unit Name
South Texas | 05INR0015a | Gulf Wind | Minor performance issues | TGW_T1 & TGW_T2
South Texas | 06INR0022ab | Penascal Wind Farm | Lacks PPC Representation. Performance issues | PENA_UNIT1, PENA_UNIT2 & PENA3_UNIT3
South Texas | 06INR0022c | Baffin Wind | Lacks PPC representation | BAFFIN_UNIT1 & BAFFIN_UNIT2
South Texas | 09INR0082 | Cedro Hill Wind | Overall good response | CEDROHIL_CHW1 & CEDROHIL_CHW2
South Texas | 10INR0060 | Redfish Wind (Magic Valley) | Minor performance issues | REDFISH_MV1A & REDFISH_MV1B
South Texas | 11INR0033 | Los Vientos 1A | Lacks PPC Representation. Performance issues | LV1_LV1A
South Texas | 11INR0033 | Los Vientos 1B | Lacks PPC Representation. Performance issues | LV1_LV1B
South Texas | 11INR0057 | Cameron County Wind | Model usable but lacks certain features | CAMWIND_UNIT1
South Texas | 11INR0062 | Patriot Wind | Missing model. Following up since July 2020 | PATWIND_UNIT1
South Texas | 11INR0091 | Whitetail Wind Energy Project | Overall good response | EXGNWTL_WIND_1
South Texas | 12INR0068 | Sendero Wind | Overall good response | EXGNSND_WIND_1
South Texas | 13INR0052 | Los Vientos III (DVAR) | No PPC model. Poor dynamic response. | LV3_UNIT_1
South Texas | 13INR0055 | Javelina Wind | Performance issue. No AVR during HVRT | BORDAS_JAVEL18 & BORDAS_JAVEL20
South Texas | 14INR0013 | San Roman Wind 1 | Performance issue. Trips during HVRT. OEM investigating | SANROMAN_WIND_1
South Texas | 14INR0041a | Bruennings Breeze | Lacks PPC Representation | BBREEZE_UNIT1 & BBREEZE_UNIT2
South Texas | 14INR0045 | Torrecillas Wind | Overall good response | TORCILAS_TORCILAS_2_5 & TORCILAS_TORCILAS_2_3
South Texas | 15INR0021 | Los Vientos V | Lacks PPC Representation and poor dynamic response | LV5_UNIT_1
South Texas | 15INR0035 | Stella 1 Wind | Lacks PPC Representation | STELLA_UNIT1
South Texas | 15INR0037 | Los Vientos IV | Lacks PPC Representation and poor dynamic response | LV4_UNIT_1
South Texas | 15INR0044 | Corazon Solar | Future unit. No model available | CORAZON_UNIT1
South Texas | 15INR0049 | Albercas Wind (Javelina 2) | Performance issue. No AVR during HVRT | BORDAS2_JAVEL2_A, BORDAS2_JAVEL2_B & BORDAS2_JAVEL2_C
South Texas | 16INR0024 | Hidalgo & Starr Wind | Minor performance issues | MIRASOLE_MIR11, MIRASOLE_MIR12 & MIRASOLE_MIR21
South Texas | 16INR0055 | Chapman Ranch Wind I | Minor performance issues | SANTACRU_UNIT1 & SANTACRU_UNIT2
South Texas | 16INR0081 | Mesteno Wind | Model does not represent the plant. Working with RE since July 2020 | MESTENO_UNIT_1
South Texas | 16INR0111 | Las Lomas Wind | Performance issues. SSR study currently ongoing. | VENADO_UNIT1, VENADO_UNIT2
South Texas | 17INR0005 | Cabezon Wind | Overall good response | CABEZON_WIND1 & CABEZON_WIND2
South Texas | 17INR0025 | Reloj Del Sol Wind | Minor performance issues | RELOJ_UNIT1, RELOJ_UNIT2, RELOJ_UNIT3, RELOJ_UNIT4
South Texas | 17INR0031 | Espiritu Wind | Overall good response | ESPIRITU_UNIT1
South Texas | 17INR0035 | Las Majadas Wind | Overall good response | LMAJADAS_UNIT1, LMAJADAS_UNIT2, LMAJADAS_UNIT3
South Texas | 17INR0037 | Palmas Altas Wind | Minor performance/efficiency issues. New model provided on 10/19 | PALMWIND_UNIT1
South Texas | 18INR0059 | East Raymond Wind | Minor performance issues | EL_RAYO_UNIT1, EL_RAYO_UNIT2
South Texas | 19INR0045 | Rayos Del Sol | Significant performance issues with current model
South Texas | 19INR0053 | Hidalgo II Wind | Minor performance issues | MIRASOLE_MIR13
South Texas | 20INR0042 | Chalupa Wind | Overall good response | CHALUPA_UNIT1, CHALUPA_UNIT2
South Texas | 20INR0088 | West Raymond (El Trueno) Wind | Minor performance issues. | TRUENO_UNIT1, TRUENO_UNIT2
South Texas | 21INR0244 | Madero Grid | Minor performance issues | MADERO_UNIT1

## Summary
South Texas
# of Renewable Generation Resources | 36
No Identified Deficiencies in Model | 8
Minor performance/efficiency issues | 13
Missing PPC/major performance issues but otherwise usable | 12
Model not usable or no model submitted | 3