## Slide 1
Proposed Ancillary Service Methodology and
Preliminary Quantities For 2021
Nov 4, 2020
WMS
ERCOT Staff

## Slide 2: Stakeholder Discussion Timeline
September 08, 2020 – PDCWG (Visit 1)
September 21, 2020 – WMWG (Visit 1)
October 14, 2020 – PDCWG (Visit 2)
October 27, 2020 – WMWG (Visit 2)
November 04, 2020 - WMS
November 05, 2020 - ROS
November 18, 2020 - TAC
December 8, 2020 - BoD

## Slide 3: Scope of Discussion
Following is a summary of the proposed changes in the methodologies for determining Ancillary Service (A/S) quantities for 2021.
  ERCOT is not recommending any changes to the methodologies used for determining Responsive Reserve Service (RRS).
    ERCOT is proposing to change the minimum RRS-PFR limit for 2021 to 1420 MW based on preliminary results from NERC’s updated BAL-003 Interconnection Frequency Response Obligation (IFRO) assessment for 2021. This preliminary IFRO analysis for 2021 reflects of an update to ERCOT’s Resource Contingency Criteria from 2750 MW to 2805 MW.
  ERCOT is recommending changes to the methodologies used for computing Non-Spin and Regulation reserves to account for growth in installed PVGR capacity.
  The A/S quantities for 2021 contained in this presentation are based on the methodology that was approved in December 2019. The quantities for 2021 reflect moving forward the historic data on which these are based, unless otherwise noted.
A redline version of the draft methodology and spreadsheets that contain the associated quantities for January through September of 2021 have been posted on the meeting page for this meeting.

## Slide 4
Responsive Reserve Service

## Slide 5: Responsive Service Methodology (RRS) - 2021
The preliminary RRS quantities for January 2021 through September 2021 in subsequent slides have been computed using 2019 and 2020 system inertia conditions and RRS table updated in 2020.
  ERCOT is proposing to change the minimum RRS-PFR limit for 2021 to 1420 MW based on preliminary results from NERC’s updated BAL-003 Interconnection Frequency Response Obligation (IFRO) assessment for 2021. This preliminary IFRO analysis for 2021 reflects of an update to ERCOT’s Resource Contingency Criteria from 2750 MW to 2805 MW.
  The RRS table tracks RRS requirements for different inertia conditions. This table was updated for 2021 to use a minimum RRS-PFR limit of 1420 MW.

## Slide 6: RRS Table - 2021
 | Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4 | Scenario 5 | Scenario 6 | Scenario 7 | Scenario 8 | Scenario 9 | Scenario 10 | Scenario 11 | Scenario 12
LR/PFR | 2.35:1 | 2.2:1 | 2.06:1 | 1.94:1 | 1.83:1 | 1.74:1 | 1.65:1 | 1.58:1 | 1.51:1 | 1.44:1 | 1.39:1 | 1.33:1
Inertia (GW∙s) | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240
PFR Req. (no LR) (MW) | 5960 | 5563 | 5200 | 4892 | 4622 | 4329 | 4114 | 3920 | 3744 | 3522 | 3314 | 3139
*RRS Curr IFRO (MW) | 3293 | 3234 | 3178 | 3128 | 3086 | 2998 | 2959 | 2908 | 2868 | 2797 | 2707 | 2645
**RRS Upd IFRO (MW) | 3352 | 3303 | 3255 | 3210 | 3170 | 3092 | 3053 | 3002 | 2959 | 2880 | 2783 | 2712
 | Scenario 13 | Scenario 14 | Scenario 15 | Scenario 16 | Scenario 17 | Scenario 18 | Scenario 19 | Scenario 20 | Scenario 21 | Scenario 22 | Scenario 23 | Scenario 24 | Scenario 25
LR/PFR | 1.28:1 | 1.24:1 | 1.19:1 | 1.15:1 | 1.12:1 | 1.08:1 | 1.04:1 | 1.01:1 | 1:1 | 1:1 | 1:1 | 1:1 | 1:1
Inertia (GW∙s) | 250 | 260 | 270 | 280 | 290 | 300 | 310 | 320 | 330 | 340 | 350 | 360 | 370
PFR Req. (no LR) (MW) | 3004 | 2890 | 2784 | 2686 | 2595 | 2510 | 2421 | 2353 | 2290 | 2230 | 2173 | 2119 | 2068
*RRS Curr IFRO (MW) | 2598 | 2553 | 2523 | 2486 | 2440 | 2409 | 2372 | 2341 | 2290 | 2230 | 2173 | 2119 | 2068
**RRS Upd IFRO (MW) | 2658 | 2605 | 2566 | 2521 | 2469 | 2429 | 2383 | 2344 | 2290 | 2230 | 2173 | 2119 | 2068
*RRS quantity is calculated for RCC of 2805 with limit of 60% limit on LRs and min RRS-PFR limit of 1150 MW.
**RRS quantity is calculated for RCC of 2805 with limit of 60% limit on LRs and min RRS-PFR limit of 1420 MW.
***Red font in table above identifies study scenario where RRS needed < 2300 MW. 2300 MW floor will be used in RRS requirement determination.
****Generation mix (CCs, Gas, SC, Coal, Steam) providing 1150 MW of PFR has been aligned with actual historic system operations.
Inertia < 250 GW·s: 30% Coal + 70% Rest. Inertia ≥ 250 GW·s: 15% Coal + 85% Rest

## Slide 7: RRS March
Notes: Trends between blue and red are fairly similar.
Max Change between blue and red in HE7-10 is 51 MW. On an average decrease of 36 MW
Max Change between red and gray in HE7-10 is 94 MW. On an average increase of 91 MW
Max Change between blue and gray in HE15-18 is 91 MW. On an average increase of 54 MW

## Slide 8: RRS June
Notes: Trends between blue and red are fairly similar.
Max Change between blue and red in HE3-6 is 109 MW. On an average increase of 48 MW
Max Change between red and gray in HE3-6 is 76 MW. On an average increase of 40 MW
Max Change between blue and gray in HE3-6 is 185 MW. On an average increase of 88 MW

## Slide 9: Hourly Average RRS Comparison
Notes: On an average red is similar to blue.
On an average largest increase between red and blue is 53 MW in May
On an average largest increase between gray and red is 91 MW in Feb, Mar
On an average largest increase between gray and blue is 126 MW in May

## Slide 10
Regulation

## Slide 11: Regulation Service Methodology - 2021
ERCOT is proposing to create and incorporate Solar Adjustment tables into the Regulation Service Methodology similar to the Wind Adjustment tables.
  Solar Adjustment tables will track incremental MWs of Regulation needed to account for additional variability per 1000 MW increase in installed solar capacity.
The preliminary Regulation quantities for January 2021 through September 2021 in subsequent slides have been computed using current methodology (2019 and 2020 five-minute net load variability), updated Wind Adjustment tables and the proposed Solar Adjustment tables.

## Slide 12: Solar Adjustment Tables - 2021
Notes: Avg Reg Up adjustment for solar pre SCR811 is 16 MW, post SCR811 is 5 MW
Avg Reg Down adjustment for solar pre SCR811 is 16 MW, post SCR811 is 5 MW

## Slide 13: Wind Adjustment Tables - 2021
Notes: Avg Reg Up adjustment for wind is 3 MW
Avg Reg Down adjustment for wind is 2 MW

## Slide 14: Regulation Up March
Notes: Trends between blue and orange are fairly similar. Largest change is 71 MW in HE23.
Max increase between orange and red is 220 MW in HE18. On an average increase of 58 MW
Max increase between orange and green is 60 MW in HE16,HE17. On an average increase of 23 MW

## Slide 15: Regulation Up June
Notes: Trends between blue and orange are fairly similar. Largest change is 90 MW in HE19.
Max increase between orange and red is 275 MW in HE19. On an average increase of 89 MW
Max increase between orange and green is 70 MW in HE15. On an average increase of 21 MW

## Slide 16: Regulation Down March
Notes: Trends between blue and orange are fairly similar. Largest change is 36 MW in HE22.
Max increase between orange and red is 158 MW in HE9. On an average increase of 69 MW
Max increase between orange and green is 71 MW in HE16. On an average increase of 26 MW

## Slide 17: Regulation Down June
Notes: Trends between blue and orange are fairly similar. Largest change is 103 MW in HE14.
Max increase between orange and red is 279 MW in HE9. On an average increase of 91 MW
Max increase between orange and green is 71 MW in HE17. On an average increase of 23 MW

## Slide 18: Hourly Average Regulation Comparison
Notes: Reg Up
On an average blue and orange are fairly similar
On an average largest increase between orange and red is 89 MW in June
On an average largest increase between green and red is 23 MW in Feb-May
Reg Down
On an average blue and orange are fairly similar
On an average largest increase between orange and red is 91 MW in June
On an average largest increase between green and red is 26 MW in Mar, April

## Slide 19
Non Spin Reserve

## Slide 20: Non Spinning Reserve Methodology (Non-Spin) - 2021
ERCOT is proposing to create and incorporate a Solar Over-Forecast Error Adjustment table.
  Solar Over-Forecast Error Adjustment Table track estimated increase in solar over forecast error per 1000 MW increase in installed solar capacity.
The preliminary Non-Spin quantities for January 2021 through September 2021 in subsequent slides have been computed using current methodology (2018, 2019 and 2020 Net load and Net load Forecast), updated Wind Over-Forecast Error Adjustment table and the proposed Solar Over-Forecast Error Adjustment table.

## Slide 21: Solar Over-Forecast Error Adjustment Table - 2021
Solar Over-Forecast Error Adjustment Table track estimated increase in solar over forecast error per 1000 MW increase in installed solar capacity.
Max: 63 MW per 1000 MW additional solar capacity
Mean: 16 MW per 1000 MW additional solar capacity

## Slide 22: Wind Over-Forecast Error Adjustment Table - 2021
Wind Over-Forecast Error Adjustment Table track estimated increase in wind over forecast error per 1000 MW increase in installed wind capacity.
  This table has been updated for 2021.
Max: 41 MW per 1000 MW additional Wind capacity
Mean: 34 MW per 1000 MW additional Wind capacity

## Slide 23: Non-Spin March
Notes: Max change between 2020 and 2021 in HE11-14 is 136 MW. On an average decrease of 42 MW
Max change between 2021 and Adj in HE15-18 is 209 MW. On an average increase of 80 MW
Between 2020 and Adj on an average increase of 38 MW

## Slide 24: Non-Spin June
Notes: Max change between 2020 and 2021 in HE11-14 is 86 MW. On an average decrease of 8 MW
Max change between 2021 and Adj in HE15-18 is 224 MW. On an average increase of 91 MW
Between 2020 and Adj on an average increase of 83 MW

## Slide 25: Hourly Average Non-Spin Comparison
Notes: On an average orange is lower than blue
On an average largest increase in red is 92 MW in May

## Slide 26
Discussion

## Slide 27: Projected Solar Installed Capacity
ERCOT’s Resource Capacity Trends report has been projecting large increases in installed solar installed capacity in the next two years.
  ERCOT currently has 3,275 MW of installed solar capacity with an additional 930 MW grid synchronized, awaiting commercial operations approval. ERCOT projects to add additional 7,529 MW of solar capacity by end of 2021.
*Chart is based on the May Resource Capacity Trends report.
  Increasing solar installed capacities will result in increased solar MW ramping due to diurnal solar pattern
  Majority of new solar projects are expected to be concentrated in the regions where existing PVGR resources are located, resulting in potential for larger MW impacts due to clouds
  This will result in increased reliance on Regulation during solar MW ramping periods

## Slide 28: Trend in Solar ramp and Regulation Exhaustion
As solar installed capacity has increased, the magnitude of 5-minute solar ramps have increased and there have been more instances where regulation has been exhausted.
Notes: For each year, 5-min solar ramp rate values were examined in bins of 10 MWs (as tracked on x-axis) and the average rate of intervals during which regulation was exhausted (i.e. remaining regulation was less than 5 MW) was computed (as tracked on y-axis). For example using the dot (400, 0.5) in the 2020 graphic below as an example - this dot represents that in 2020, regulation was exhausted in 50% of the time during which the ramp was between 390 and 400 MW.

## Slide 29: Trends in Hourly Average CPS1
Visible declining trend in hourly average CPS1 during evening/sunset hours. Not low enough to trigger more Regulation in those hours per current methodology.
Notes: If it is determined that during the course of the year that the ERCOT monthly average for CPS1 score was less than 140% for a specific month, ERCOT will apply an extra 10% of both Reg-Up and Reg-Down for hours in which the CPS1 score was less than 140%. Additionally, if the ERCOT 12-month rolling average CPS1 score is less than 140%, for the next month ERCOT will procure an extra 10% of both Reg-Up and Reg-Down for hours in which the hourly CPS1 score was less than 140%. This value will increase to 20% if the CPS1 score falls below 100%.

## Slide 30: Solar Adjustment Tables - 2021
Solar Adjustment Tables track incremental MWs of Regulation needed to account for additional variability per 1000 MW increase in installed solar capacity.
  Heat map below demonstrates the preliminary adjustment needed before the implementation of SCR811.
Reg-Up Adjustment Pre SCR811
Reg-Down Adjustment Pre SCR811
Mean: 15.57 MW per 1000 MW additional solar capacity
Mean: 15.9 MW per 1000 MW additional solar capacity

## Slide 31: Solar Adjustment Tables - 2021
Solar Adjustment Tables track incremental MWs of Regulation needed to account for additional variability per 1000 MW increase in installed solar capacity.
  Heat map below demonstrates the preliminary adjustment needed after the implementation of SCR811.
Reg-Up Adjustment Post SCR811
Reg-Down Adjustment Post SCR811
Mean: 4.76 MW per 1000 MW additional solar capacity
Mean: 5.0 MW per 1000 MW additional solar capacity

## Slide 32: PVGR Forecasting Performance
As solar installed capacity is increasing the Mean Absolute Error (MAE) of both hour-ahead and day-ahead solar forecast is increasing.
MAE: mean absolute error