## 2020 RRS
Note that the 2020 quantities are based on the 2020 RRS table that was built using Resource Contingency Criteria (RCC) of 2805 MW and the minimum RRS-PFR limit of 1150 MW has been used.
2020-01-01 | [6 empty] | 2020-02-01 | [6 empty] | 2020-03-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | Total Equivalent PFRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | Total Equivalent PFRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | Total Equivalent PFRs
1 | 2998 | 1199 | 1799 | 1.74 | 60% | 4329.26 | 1 | 2998 | 1199 | 1799 | 1.74 | 60% | 4329.26 | 1 | 3086 | 1234 | 1852 | 1.83 | 60% | 4623.16
2 | 2998 | 1199 | 1799 | 1.74 | 60% | 4329.26 | 2 | 2998 | 1199 | 1799 | 1.74 | 60% | 4329.26 | 2 | 3086 | 1234 | 1852 | 1.83 | 60% | 4623.16
3 | 2959 | 1184 | 1776 | 1.65 | 60% | 4114.4 | 3 | 2998 | 1199 | 1799 | 1.74 | 60% | 4329.26 | 3 | 3086 | 1234 | 1852 | 1.83 | 60% | 4623.16
4 | 2959 | 1184 | 1776 | 1.65 | 60% | 4114.4 | 4 | 2998 | 1199 | 1799 | 1.74 | 60% | 4329.26 | 4 | 3086 | 1234 | 1852 | 1.83 | 60% | 4623.16
5 | 2959 | 1184 | 1776 | 1.65 | 60% | 4114.4 | 5 | 2998 | 1199 | 1799 | 1.74 | 60% | 4329.26 | 5 | 3086 | 1234 | 1852 | 1.83 | 60% | 4623.16
6 | 2959 | 1184 | 1776 | 1.65 | 60% | 4114.4 | 6 | 2998 | 1199 | 1799 | 1.74 | 60% | 4329.26 | 6 | 3086 | 1234 | 1852 | 1.83 | 60% | 4623.16
7 | 2797 | 1150 | 1647 | 1.44 | 58.9% | 3521.68 | 7 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 7 | 2959 | 1184 | 1775 | 1.65 | 60% | 4112.75
8 | 2797 | 1150 | 1647 | 1.44 | 58.9% | 3521.68 | 8 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 8 | 2959 | 1184 | 1775 | 1.65 | 60% | 4112.75
9 | 2797 | 1150 | 1647 | 1.44 | 58.9% | 3521.68 | 9 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 9 | 2959 | 1184 | 1775 | 1.65 | 60% | 4112.75
10 | 2797 | 1150 | 1647 | 1.44 | 58.9% | 3521.68 | 10 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 10 | 2959 | 1184 | 1775 | 1.65 | 60% | 4112.75
11 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 11 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 11 | 2908 | 1163 | 1745 | 1.58 | 60% | 3920.1
12 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 12 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 12 | 2908 | 1163 | 1745 | 1.58 | 60% | 3920.1
13 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 13 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 13 | 2908 | 1163 | 1745 | 1.58 | 60% | 3920.1
14 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 14 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 14 | 2908 | 1163 | 1745 | 1.58 | 60% | 3920.1
15 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 15 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 15 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18
16 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 16 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 16 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18
17 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 17 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 17 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18
18 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 18 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 18 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18
19 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 19 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 19 | 2908 | 1163 | 1745 | 1.58 | 60% | 3920.1
20 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 20 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 20 | 2908 | 1163 | 1745 | 1.58 | 60% | 3920.1
21 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 21 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 21 | 2908 | 1163 | 1745 | 1.58 | 60% | 3920.1
22 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 22 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 22 | 2908 | 1163 | 1745 | 1.58 | 60% | 3920.1
23 | 2998 | 1199 | 1799 | 1.74 | 60% | 4329.26 | 23 | 2998 | 1199 | 1799 | 1.74 | 60% | 4329.26 | 23 | 3086 | 1234 | 1852 | 1.83 | 60% | 4623.16
24 | 2998 | 1199 | 1799 | 1.74 | 60% | 4329.26 | 24 | 2998 | 1199 | 1799 | 1.74 | 60% | 4329.26 | 24 | 3086 | 1234 | 1852 | 1.83 | 60% | 4623.16
2020-04-01 | [6 empty] | 2020-05-01 | [6 empty] | 2020-06-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | Total Equivalent PFRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | Total Equivalent PFRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | Total Equivalent PFRs
1 | 3086 | 1234 | 1852 | 1.83 | 60% | 4623.16 | 1 | 2797 | 1150 | 1647 | 1.44 | 58.9% | 3521.68 | 1 | 2553 | 1150 | 1403 | 1.24 | 55% | 2889.72
2 | 3086 | 1234 | 1852 | 1.83 | 60% | 4623.16 | 2 | 2797 | 1150 | 1647 | 1.44 | 58.9% | 3521.68 | 2 | 2553 | 1150 | 1403 | 1.24 | 55% | 2889.72
3 | 3086 | 1234 | 1852 | 1.83 | 60% | 4623.16 | 3 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 3 | 2598 | 1150 | 1448 | 1.28 | 55.7% | 3003.44
4 | 3086 | 1234 | 1852 | 1.83 | 60% | 4623.16 | 4 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 4 | 2598 | 1150 | 1448 | 1.28 | 55.7% | 3003.44
5 | 3086 | 1234 | 1852 | 1.83 | 60% | 4623.16 | 5 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 5 | 2598 | 1150 | 1448 | 1.28 | 55.7% | 3003.44
6 | 3086 | 1234 | 1852 | 1.83 | 60% | 4623.16 | 6 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 6 | 2598 | 1150 | 1448 | 1.28 | 55.7% | 3003.44
7 | 2998 | 1199 | 1799 | 1.74 | 60% | 4329.26 | 7 | 2707 | 1150 | 1557 | 1.39 | 57.5% | 3314.23 | 7 | 2523 | 1150 | 1373 | 1.19 | 54.4% | 2783.87
8 | 2998 | 1199 | 1799 | 1.74 | 60% | 4329.26 | 8 | 2707 | 1150 | 1557 | 1.39 | 57.5% | 3314.23 | 8 | 2523 | 1150 | 1373 | 1.19 | 54.4% | 2783.87
9 | 2998 | 1199 | 1799 | 1.74 | 60% | 4329.26 | 9 | 2707 | 1150 | 1557 | 1.39 | 57.5% | 3314.23 | 9 | 2523 | 1150 | 1373 | 1.19 | 54.4% | 2783.87
10 | 2998 | 1199 | 1799 | 1.74 | 60% | 4329.26 | 10 | 2707 | 1150 | 1557 | 1.39 | 57.5% | 3314.23 | 10 | 2523 | 1150 | 1373 | 1.19 | 54.4% | 2783.87
11 | 2908 | 1163 | 1745 | 1.58 | 60% | 3920.1 | 11 | 2553 | 1150 | 1403 | 1.24 | 55% | 2889.72 | 11 | 2372 | 1150 | 1222 | 1.04 | 51.5% | 2420.88
12 | 2908 | 1163 | 1745 | 1.58 | 60% | 3920.1 | 12 | 2553 | 1150 | 1403 | 1.24 | 55% | 2889.72 | 12 | 2372 | 1150 | 1222 | 1.04 | 51.5% | 2420.88
13 | 2908 | 1163 | 1745 | 1.58 | 60% | 3920.1 | 13 | 2553 | 1150 | 1403 | 1.24 | 55% | 2889.72 | 13 | 2372 | 1150 | 1222 | 1.04 | 51.5% | 2420.88
14 | 2908 | 1163 | 1745 | 1.58 | 60% | 3920.1 | 14 | 2553 | 1150 | 1403 | 1.24 | 55% | 2889.72 | 14 | 2372 | 1150 | 1222 | 1.04 | 51.5% | 2420.88
15 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 15 | 2523 | 1150 | 1373 | 1.19 | 54.4% | 2783.87 | 15 | 2341 | 1150 | 1191 | 1.01 | 50.9% | 2352.91
16 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 16 | 2523 | 1150 | 1373 | 1.19 | 54.4% | 2783.87 | 16 | 2341 | 1150 | 1191 | 1.01 | 50.9% | 2352.91
17 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 17 | 2523 | 1150 | 1373 | 1.19 | 54.4% | 2783.87 | 17 | 2341 | 1150 | 1191 | 1.01 | 50.9% | 2352.91
18 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 18 | 2523 | 1150 | 1373 | 1.19 | 54.4% | 2783.87 | 18 | 2341 | 1150 | 1191 | 1.01 | 50.9% | 2352.91
19 | 2908 | 1163 | 1745 | 1.58 | 60% | 3920.1 | 19 | 2553 | 1150 | 1403 | 1.24 | 55% | 2889.72 | 19 | 2372 | 1150 | 1222 | 1.04 | 51.5% | 2420.88
20 | 2908 | 1163 | 1745 | 1.58 | 60% | 3920.1 | 20 | 2553 | 1150 | 1403 | 1.24 | 55% | 2889.72 | 20 | 2372 | 1150 | 1222 | 1.04 | 51.5% | 2420.88
21 | 2908 | 1163 | 1745 | 1.58 | 60% | 3920.1 | 21 | 2553 | 1150 | 1403 | 1.24 | 55% | 2889.72 | 21 | 2372 | 1150 | 1222 | 1.04 | 51.5% | 2420.88
22 | 2908 | 1163 | 1745 | 1.58 | 60% | 3920.1 | 22 | 2553 | 1150 | 1403 | 1.24 | 55% | 2889.72 | 22 | 2372 | 1150 | 1222 | 1.04 | 51.5% | 2420.88
23 | 3086 | 1234 | 1852 | 1.83 | 60% | 4623.16 | 23 | 2797 | 1150 | 1647 | 1.44 | 58.9% | 3521.68 | 23 | 2553 | 1150 | 1403 | 1.24 | 55% | 2889.72
24 | 3086 | 1234 | 1852 | 1.83 | 60% | 4623.16 | 24 | 2797 | 1150 | 1647 | 1.44 | 58.9% | 3521.68 | 24 | 2553 | 1150 | 1403 | 1.24 | 55% | 2889.72
2020-07-01 | [6 empty] | 2020-08-01 | [6 empty] | 2020-09-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | Total Equivalent PFRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | Total Equivalent PFRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | Total Equivalent PFRs
1 | 2440 | 1150 | 1290 | 1.12 | 52.9% | 2594.8 | 1 | 2409 | 1150 | 1259 | 1.08 | 52.3% | 2509.72 | 1 | 2553 | 1150 | 1403 | 1.24 | 55% | 2889.72
2 | 2440 | 1150 | 1290 | 1.12 | 52.9% | 2594.8 | 2 | 2409 | 1150 | 1259 | 1.08 | 52.3% | 2509.72 | 2 | 2553 | 1150 | 1403 | 1.24 | 55% | 2889.72
3 | 2486 | 1150 | 1336 | 1.15 | 53.7% | 2686.4 | 3 | 2440 | 1150 | 1290 | 1.12 | 52.9% | 2594.8 | 3 | 2553 | 1150 | 1403 | 1.24 | 55% | 2889.72
4 | 2486 | 1150 | 1336 | 1.15 | 53.7% | 2686.4 | 4 | 2440 | 1150 | 1290 | 1.12 | 52.9% | 2594.8 | 4 | 2553 | 1150 | 1403 | 1.24 | 55% | 2889.72
5 | 2486 | 1150 | 1336 | 1.15 | 53.7% | 2686.4 | 5 | 2440 | 1150 | 1290 | 1.12 | 52.9% | 2594.8 | 5 | 2553 | 1150 | 1403 | 1.24 | 55% | 2889.72
6 | 2486 | 1150 | 1336 | 1.15 | 53.7% | 2686.4 | 6 | 2440 | 1150 | 1290 | 1.12 | 52.9% | 2594.8 | 6 | 2553 | 1150 | 1403 | 1.24 | 55% | 2889.72
7 | 2409 | 1150 | 1259 | 1.08 | 52.3% | 2509.72 | 7 | 2372 | 1150 | 1222 | 1.04 | 51.5% | 2420.88 | 7 | 2523 | 1150 | 1373 | 1.19 | 54.4% | 2783.87
8 | 2409 | 1150 | 1259 | 1.08 | 52.3% | 2509.72 | 8 | 2372 | 1150 | 1222 | 1.04 | 51.5% | 2420.88 | 8 | 2523 | 1150 | 1373 | 1.19 | 54.4% | 2783.87
9 | 2409 | 1150 | 1259 | 1.08 | 52.3% | 2509.72 | 9 | 2372 | 1150 | 1222 | 1.04 | 51.5% | 2420.88 | 9 | 2523 | 1150 | 1373 | 1.19 | 54.4% | 2783.87
10 | 2409 | 1150 | 1259 | 1.08 | 52.3% | 2509.72 | 10 | 2372 | 1150 | 1222 | 1.04 | 51.5% | 2420.88 | 10 | 2523 | 1150 | 1373 | 1.19 | 54.4% | 2783.87
11 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 11 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 11 | 2409 | 1150 | 1259 | 1.08 | 52.3% | 2509.72
12 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 12 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 12 | 2409 | 1150 | 1259 | 1.08 | 52.3% | 2509.72
13 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 13 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 13 | 2409 | 1150 | 1259 | 1.08 | 52.3% | 2509.72
14 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 14 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 14 | 2409 | 1150 | 1259 | 1.08 | 52.3% | 2509.72
15 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 15 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 15 | 2372 | 1150 | 1222 | 1.04 | 51.5% | 2420.88
16 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 16 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 16 | 2372 | 1150 | 1222 | 1.04 | 51.5% | 2420.88
17 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 17 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 17 | 2372 | 1150 | 1222 | 1.04 | 51.5% | 2420.88
18 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 18 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 18 | 2372 | 1150 | 1222 | 1.04 | 51.5% | 2420.88
19 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 19 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 19 | 2409 | 1150 | 1259 | 1.08 | 52.3% | 2509.72
20 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 20 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 20 | 2409 | 1150 | 1259 | 1.08 | 52.3% | 2509.72
21 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 21 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 21 | 2409 | 1150 | 1259 | 1.08 | 52.3% | 2509.72
22 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 22 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 22 | 2409 | 1150 | 1259 | 1.08 | 52.3% | 2509.72
23 | 2440 | 1150 | 1290 | 1.12 | 52.9% | 2594.8 | 23 | 2409 | 1150 | 1259 | 1.08 | 52.3% | 2509.72 | 23 | 2553 | 1150 | 1403 | 1.24 | 55% | 2889.72
24 | 2440 | 1150 | 1290 | 1.12 | 52.9% | 2594.8 | 24 | 2409 | 1150 | 1259 | 1.08 | 52.3% | 2509.72 | 24 | 2553 | 1150 | 1403 | 1.24 | 55% | 2889.72
2020-10-01 | [6 empty] | 2020-11-01 | [6 empty] | 2020-12-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | Total Equivalent PFRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | Total Equivalent PFRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | Total Equivalent PFRs
1 | 2908 | 1163 | 1745 | 1.58 | 60% | 3920.1 | 1 | 3086 | 1234 | 1852 | 1.83 | 60% | 4623.16 | 1 | 2998 | 1199 | 1799 | 1.74 | 60% | 4329.26
2 | 2908 | 1163 | 1745 | 1.58 | 60% | 3920.1 | 2 | 3086 | 1234 | 1852 | 1.83 | 60% | 4623.16 | 2 | 2998 | 1199 | 1799 | 1.74 | 60% | 4329.26
3 | 2959 | 1184 | 1775 | 1.65 | 60% | 4112.75 | 3 | 2998 | 1199 | 1799 | 1.74 | 60% | 4329.26 | 3 | 2959 | 1184 | 1775 | 1.65 | 60% | 4112.75
4 | 2959 | 1184 | 1775 | 1.65 | 60% | 4112.75 | 4 | 2998 | 1199 | 1799 | 1.74 | 60% | 4329.26 | 4 | 2959 | 1184 | 1775 | 1.65 | 60% | 4112.75
5 | 2959 | 1184 | 1775 | 1.65 | 60% | 4112.75 | 5 | 2998 | 1199 | 1799 | 1.74 | 60% | 4329.26 | 5 | 2959 | 1184 | 1775 | 1.65 | 60% | 4112.75
6 | 2959 | 1184 | 1775 | 1.65 | 60% | 4112.75 | 6 | 2998 | 1199 | 1799 | 1.74 | 60% | 4329.26 | 6 | 2959 | 1184 | 1775 | 1.65 | 60% | 4112.75
7 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 7 | 2908 | 1163 | 1745 | 1.58 | 60% | 3920.1 | 7 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18
8 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 8 | 2908 | 1163 | 1745 | 1.58 | 60% | 3920.1 | 8 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18
9 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 9 | 2908 | 1163 | 1745 | 1.58 | 60% | 3920.1 | 9 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18
10 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 10 | 2908 | 1163 | 1745 | 1.58 | 60% | 3920.1 | 10 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18
11 | 2707 | 1150 | 1557 | 1.39 | 57.5% | 3314.23 | 11 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 11 | 2797 | 1150 | 1647 | 1.44 | 58.9% | 3521.68
12 | 2707 | 1150 | 1557 | 1.39 | 57.5% | 3314.23 | 12 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 12 | 2797 | 1150 | 1647 | 1.44 | 58.9% | 3521.68
13 | 2707 | 1150 | 1557 | 1.39 | 57.5% | 3314.23 | 13 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 13 | 2797 | 1150 | 1647 | 1.44 | 58.9% | 3521.68
14 | 2707 | 1150 | 1557 | 1.39 | 57.5% | 3314.23 | 14 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 14 | 2797 | 1150 | 1647 | 1.44 | 58.9% | 3521.68
15 | 2645 | 1150 | 1495 | 1.33 | 56.5% | 3138.35 | 15 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 15 | 2797 | 1150 | 1647 | 1.44 | 58.9% | 3521.68
16 | 2645 | 1150 | 1495 | 1.33 | 56.5% | 3138.35 | 16 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 16 | 2797 | 1150 | 1647 | 1.44 | 58.9% | 3521.68
17 | 2645 | 1150 | 1495 | 1.33 | 56.5% | 3138.35 | 17 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 17 | 2797 | 1150 | 1647 | 1.44 | 58.9% | 3521.68
18 | 2645 | 1150 | 1495 | 1.33 | 56.5% | 3138.35 | 18 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 18 | 2797 | 1150 | 1647 | 1.44 | 58.9% | 3521.68
19 | 2707 | 1150 | 1557 | 1.39 | 57.5% | 3314.23 | 19 | 2908 | 1163 | 1745 | 1.58 | 60% | 3920.1 | 19 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18
20 | 2707 | 1150 | 1557 | 1.39 | 57.5% | 3314.23 | 20 | 2908 | 1163 | 1745 | 1.58 | 60% | 3920.1 | 20 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18
21 | 2707 | 1150 | 1557 | 1.39 | 57.5% | 3314.23 | 21 | 2908 | 1163 | 1745 | 1.58 | 60% | 3920.1 | 21 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18
22 | 2707 | 1150 | 1557 | 1.39 | 57.5% | 3314.23 | 22 | 2908 | 1163 | 1745 | 1.58 | 60% | 3920.1 | 22 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18
23 | 2908 | 1163 | 1745 | 1.58 | 60% | 3920.1 | 23 | 3086 | 1234 | 1852 | 1.83 | 60% | 4623.16 | 23 | 2998 | 1199 | 1799 | 1.74 | 60% | 4329.26
24 | 2908 | 1163 | 1745 | 1.58 | 60% | 3920.1 | 24 | 3086 | 1234 | 1852 | 1.83 | 60% | 4623.16 | 24 | 2998 | 1199 | 1799 | 1.74 | 60% | 4329.26

## 2021 RRS
Note ERCOT is working with NERC to include an update to ERCOT's Resource Contingency Criteria (RCC) (from 2750 MW to 2805 MW) in NERC's 2020 BAL-003 Interconnection Frequency Response Obligation (IFRO) assessment for 2021. As a result of this ERCOT expects that the minimum RRS-PFR limit for 2021 may change. These preliminary 2021 quantities are based on the 2020 RRS table that was built using Resource Contingency Criteria (RCC) of 2805 MW and the minimum RRS-PFR limit of 1150 MW.
2021-01-01 | [6 empty] | 2021-02-01 | [6 empty] | 2021-03-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | Total Equivalent PFRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | Total Equivalent PFRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | Total Equivalent PFRs
1 | 2959 | 1184 | 1775 | 1.65 | 59.99% | 4112.75 | 1 | 3086 | 1234 | 1852 | 1.83 | 60.01% | 4623.16 | 1 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 4329.26
2 | 2959 | 1184 | 1775 | 1.65 | 59.99% | 4112.75 | 2 | 3086 | 1234 | 1852 | 1.83 | 60.01% | 4623.16 | 2 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 4329.26
3 | 2959 | 1184 | 1775 | 1.65 | 59.99% | 4112.75 | 3 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 4329.26 | 3 | 3086 | 1234 | 1852 | 1.83 | 60.01% | 4623.16
4 | 2959 | 1184 | 1775 | 1.65 | 59.99% | 4112.75 | 4 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 4329.26 | 4 | 3086 | 1234 | 1852 | 1.83 | 60.01% | 4623.16
5 | 2959 | 1184 | 1775 | 1.65 | 59.99% | 4112.75 | 5 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 4329.26 | 5 | 3086 | 1234 | 1852 | 1.83 | 60.01% | 4623.16
6 | 2959 | 1184 | 1775 | 1.65 | 59.99% | 4112.75 | 6 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 4329.26 | 6 | 3086 | 1234 | 1852 | 1.83 | 60.01% | 4623.16
7 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 7 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 7 | 2908 | 1163 | 1745 | 1.58 | 60.01% | 3920.1
8 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 8 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 8 | 2908 | 1163 | 1745 | 1.58 | 60.01% | 3920.1
9 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 9 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 9 | 2908 | 1163 | 1745 | 1.58 | 60.01% | 3920.1
10 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 10 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 10 | 2908 | 1163 | 1745 | 1.58 | 60.01% | 3920.1
11 | 2797 | 1150 | 1647 | 1.44 | 58.88% | 3521.68 | 11 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 11 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18
12 | 2797 | 1150 | 1647 | 1.44 | 58.88% | 3521.68 | 12 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 12 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18
13 | 2797 | 1150 | 1647 | 1.44 | 58.88% | 3521.68 | 13 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 13 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18
14 | 2797 | 1150 | 1647 | 1.44 | 58.88% | 3521.68 | 14 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 14 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18
15 | 2797 | 1150 | 1647 | 1.44 | 58.88% | 3521.68 | 15 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 15 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18
16 | 2797 | 1150 | 1647 | 1.44 | 58.88% | 3521.68 | 16 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 16 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18
17 | 2797 | 1150 | 1647 | 1.44 | 58.88% | 3521.68 | 17 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 17 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18
18 | 2797 | 1150 | 1647 | 1.44 | 58.88% | 3521.68 | 18 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 18 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18
19 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 19 | 2908 | 1163 | 1745 | 1.58 | 60.01% | 3920.1 | 19 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18
20 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 20 | 2908 | 1163 | 1745 | 1.58 | 60.01% | 3920.1 | 20 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18
21 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 21 | 2908 | 1163 | 1745 | 1.58 | 60.01% | 3920.1 | 21 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18
22 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 22 | 2908 | 1163 | 1745 | 1.58 | 60.01% | 3920.1 | 22 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18
23 | 2959 | 1184 | 1775 | 1.65 | 59.99% | 4112.75 | 23 | 3086 | 1234 | 1852 | 1.83 | 60.01% | 4623.16 | 23 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 4329.26
24 | 2959 | 1184 | 1775 | 1.65 | 59.99% | 4112.75 | 24 | 3086 | 1234 | 1852 | 1.83 | 60.01% | 4623.16 | 24 | 2998 | 1199 | 1799 | 1.74 | 60.01% | 4329.26
2021-04-01 | [6 empty] | 2021-05-01 | [6 empty] | 2021-06-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | Total Equivalent PFRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | Total Equivalent PFRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | Total Equivalent PFRs
1 | 3086 | 1234 | 1852 | 1.83 | 60.01% | 4623.16 | 1 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 1 | 2598 | 1150 | 1448 | 1.28 | 55.74% | 3003.44
2 | 3086 | 1234 | 1852 | 1.83 | 60.01% | 4623.16 | 2 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 2 | 2598 | 1150 | 1448 | 1.28 | 55.74% | 3003.44
3 | 3086 | 1234 | 1852 | 1.83 | 60.01% | 4623.16 | 3 | 2908 | 1163 | 1745 | 1.58 | 60.01% | 3920.1 | 3 | 2707 | 1150 | 1557 | 1.39 | 57.52% | 3314.23
4 | 3086 | 1234 | 1852 | 1.83 | 60.01% | 4623.16 | 4 | 2908 | 1163 | 1745 | 1.58 | 60.01% | 3920.1 | 4 | 2707 | 1150 | 1557 | 1.39 | 57.52% | 3314.23
5 | 3086 | 1234 | 1852 | 1.83 | 60.01% | 4623.16 | 5 | 2908 | 1163 | 1745 | 1.58 | 60.01% | 3920.1 | 5 | 2707 | 1150 | 1557 | 1.39 | 57.52% | 3314.23
6 | 3086 | 1234 | 1852 | 1.83 | 60.01% | 4623.16 | 6 | 2908 | 1163 | 1745 | 1.58 | 60.01% | 3920.1 | 6 | 2707 | 1150 | 1557 | 1.39 | 57.52% | 3314.23
7 | 2959 | 1184 | 1775 | 1.65 | 59.99% | 4112.75 | 7 | 2797 | 1150 | 1647 | 1.44 | 58.88% | 3521.68 | 7 | 2553 | 1150 | 1403 | 1.24 | 54.95% | 2889.72
8 | 2959 | 1184 | 1775 | 1.65 | 59.99% | 4112.75 | 8 | 2797 | 1150 | 1647 | 1.44 | 58.88% | 3521.68 | 8 | 2553 | 1150 | 1403 | 1.24 | 54.95% | 2889.72
9 | 2959 | 1184 | 1775 | 1.65 | 59.99% | 4112.75 | 9 | 2797 | 1150 | 1647 | 1.44 | 58.88% | 3521.68 | 9 | 2553 | 1150 | 1403 | 1.24 | 54.95% | 2889.72
10 | 2959 | 1184 | 1775 | 1.65 | 59.99% | 4112.75 | 10 | 2797 | 1150 | 1647 | 1.44 | 58.88% | 3521.68 | 10 | 2553 | 1150 | 1403 | 1.24 | 54.95% | 2889.72
11 | 2908 | 1163 | 1745 | 1.58 | 60.01% | 3920.1 | 11 | 2598 | 1150 | 1448 | 1.28 | 55.74% | 3003.44 | 11 | 2409 | 1150 | 1259 | 1.08 | 52.26% | 2509.72
12 | 2908 | 1163 | 1745 | 1.58 | 60.01% | 3920.1 | 12 | 2598 | 1150 | 1448 | 1.28 | 55.74% | 3003.44 | 12 | 2409 | 1150 | 1259 | 1.08 | 52.26% | 2509.72
13 | 2908 | 1163 | 1745 | 1.58 | 60.01% | 3920.1 | 13 | 2598 | 1150 | 1448 | 1.28 | 55.74% | 3003.44 | 13 | 2409 | 1150 | 1259 | 1.08 | 52.26% | 2509.72
14 | 2908 | 1163 | 1745 | 1.58 | 60.01% | 3920.1 | 14 | 2598 | 1150 | 1448 | 1.28 | 55.74% | 3003.44 | 14 | 2409 | 1150 | 1259 | 1.08 | 52.26% | 2509.72
15 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 15 | 2553 | 1150 | 1403 | 1.24 | 54.95% | 2889.72 | 15 | 2372 | 1150 | 1222 | 1.04 | 51.52% | 2420.88
16 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 16 | 2553 | 1150 | 1403 | 1.24 | 54.95% | 2889.72 | 16 | 2372 | 1150 | 1222 | 1.04 | 51.52% | 2420.88
17 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 17 | 2553 | 1150 | 1403 | 1.24 | 54.95% | 2889.72 | 17 | 2372 | 1150 | 1222 | 1.04 | 51.52% | 2420.88
18 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 18 | 2553 | 1150 | 1403 | 1.24 | 54.95% | 2889.72 | 18 | 2372 | 1150 | 1222 | 1.04 | 51.52% | 2420.88
19 | 2908 | 1163 | 1745 | 1.58 | 60.01% | 3920.1 | 19 | 2598 | 1150 | 1448 | 1.28 | 55.74% | 3003.44 | 19 | 2409 | 1150 | 1259 | 1.08 | 52.26% | 2509.72
20 | 2908 | 1163 | 1745 | 1.58 | 60.01% | 3920.1 | 20 | 2598 | 1150 | 1448 | 1.28 | 55.74% | 3003.44 | 20 | 2409 | 1150 | 1259 | 1.08 | 52.26% | 2509.72
21 | 2908 | 1163 | 1745 | 1.58 | 60.01% | 3920.1 | 21 | 2598 | 1150 | 1448 | 1.28 | 55.74% | 3003.44 | 21 | 2409 | 1150 | 1259 | 1.08 | 52.26% | 2509.72
22 | 2908 | 1163 | 1745 | 1.58 | 60.01% | 3920.1 | 22 | 2598 | 1150 | 1448 | 1.28 | 55.74% | 3003.44 | 22 | 2409 | 1150 | 1259 | 1.08 | 52.26% | 2509.72
23 | 3086 | 1234 | 1852 | 1.83 | 60.01% | 4623.16 | 23 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 23 | 2598 | 1150 | 1448 | 1.28 | 55.74% | 3003.44
24 | 3086 | 1234 | 1852 | 1.83 | 60.01% | 4623.16 | 24 | 2868 | 1150 | 1718 | 1.51 | 59.9% | 3744.18 | 24 | 2598 | 1150 | 1448 | 1.28 | 55.74% | 3003.44
2021-07-01 | [6 empty] | 2021-08-01 | [6 empty] | 2021-09-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | Total Equivalent PFRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | Total Equivalent PFRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | Total Equivalent PFRs
1 | 2440 | 1150 | 1290 | 1.12 | 52.87% | 2594.8 | 1 | 2409 | 1150 | 1259 | 1.08 | 52.26% | 2509.72 | 1 | 2553 | 1150 | 1403 | 1.24 | 54.95% | 2889.72
2 | 2440 | 1150 | 1290 | 1.12 | 52.87% | 2594.8 | 2 | 2409 | 1150 | 1259 | 1.08 | 52.26% | 2509.72 | 2 | 2553 | 1150 | 1403 | 1.24 | 54.95% | 2889.72
3 | 2523 | 1150 | 1373 | 1.19 | 54.42% | 2783.87 | 3 | 2440 | 1150 | 1290 | 1.12 | 52.87% | 2594.8 | 3 | 2645 | 1150 | 1495 | 1.33 | 56.52% | 3138.35
4 | 2523 | 1150 | 1373 | 1.19 | 54.42% | 2783.87 | 4 | 2440 | 1150 | 1290 | 1.12 | 52.87% | 2594.8 | 4 | 2645 | 1150 | 1495 | 1.33 | 56.52% | 3138.35
5 | 2523 | 1150 | 1373 | 1.19 | 54.42% | 2783.87 | 5 | 2440 | 1150 | 1290 | 1.12 | 52.87% | 2594.8 | 5 | 2645 | 1150 | 1495 | 1.33 | 56.52% | 3138.35
6 | 2523 | 1150 | 1373 | 1.19 | 54.42% | 2783.87 | 6 | 2440 | 1150 | 1290 | 1.12 | 52.87% | 2594.8 | 6 | 2645 | 1150 | 1495 | 1.33 | 56.52% | 3138.35
7 | 2440 | 1150 | 1290 | 1.12 | 52.87% | 2594.8 | 7 | 2372 | 1150 | 1222 | 1.04 | 51.52% | 2420.88 | 7 | 2553 | 1150 | 1403 | 1.24 | 54.95% | 2889.72
8 | 2440 | 1150 | 1290 | 1.12 | 52.87% | 2594.8 | 8 | 2372 | 1150 | 1222 | 1.04 | 51.52% | 2420.88 | 8 | 2553 | 1150 | 1403 | 1.24 | 54.95% | 2889.72
9 | 2440 | 1150 | 1290 | 1.12 | 52.87% | 2594.8 | 9 | 2372 | 1150 | 1222 | 1.04 | 51.52% | 2420.88 | 9 | 2553 | 1150 | 1403 | 1.24 | 54.95% | 2889.72
10 | 2440 | 1150 | 1290 | 1.12 | 52.87% | 2594.8 | 10 | 2372 | 1150 | 1222 | 1.04 | 51.52% | 2420.88 | 10 | 2553 | 1150 | 1403 | 1.24 | 54.95% | 2889.72
11 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 11 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 11 | 2440 | 1150 | 1290 | 1.12 | 52.87% | 2594.8
12 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 12 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 12 | 2440 | 1150 | 1290 | 1.12 | 52.87% | 2594.8
13 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 13 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 13 | 2440 | 1150 | 1290 | 1.12 | 52.87% | 2594.8
14 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 14 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 14 | 2440 | 1150 | 1290 | 1.12 | 52.87% | 2594.8
15 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 15 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 15 | 2372 | 1150 | 1222 | 1.04 | 51.52% | 2420.88
16 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 16 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 16 | 2372 | 1150 | 1222 | 1.04 | 51.52% | 2420.88
17 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 17 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 17 | 2372 | 1150 | 1222 | 1.04 | 51.52% | 2420.88
18 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 18 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 18 | 2372 | 1150 | 1222 | 1.04 | 51.52% | 2420.88
19 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 19 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 19 | 2440 | 1150 | 1290 | 1.12 | 52.87% | 2594.8
20 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 20 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 20 | 2440 | 1150 | 1290 | 1.12 | 52.87% | 2594.8
21 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 21 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 21 | 2440 | 1150 | 1290 | 1.12 | 52.87% | 2594.8
22 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 22 | 2300 | 1150 | 1150 | 1 | 50% | 2300 | 22 | 2440 | 1150 | 1290 | 1.12 | 52.87% | 2594.8
23 | 2440 | 1150 | 1290 | 1.12 | 52.87% | 2594.8 | 23 | 2409 | 1150 | 1259 | 1.08 | 52.26% | 2509.72 | 23 | 2553 | 1150 | 1403 | 1.24 | 54.95% | 2889.72
24 | 2440 | 1150 | 1290 | 1.12 | 52.87% | 2594.8 | 24 | 2409 | 1150 | 1259 | 1.08 | 52.26% | 2509.72 | 24 | 2553 | 1150 | 1403 | 1.24 | 54.95% | 2889.72
2021-10-01 | [6 empty] | 2021-11-01 | [6 empty] | 2021-12-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs |  | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs |  | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs
1 | [6 empty] | 1 | [6 empty] | 1
2 | [6 empty] | 2 | [6 empty] | 2
3 | [6 empty] | 3 | [6 empty] | 3
4 | [6 empty] | 4 | [6 empty] | 4
5 | [6 empty] | 5 | [6 empty] | 5
6 | [6 empty] | 6 | [6 empty] | 6
7 | [6 empty] | 7 | [6 empty] | 7
8 | [6 empty] | 8 | [6 empty] | 8
9 | [6 empty] | 9 | [6 empty] | 9
10 | [6 empty] | 10 | [6 empty] | 10
11 | [6 empty] | 11 | [6 empty] | 11
12 | [6 empty] | 12 | [6 empty] | 12
13 | [6 empty] | 13 | [6 empty] | 13
14 | [6 empty] | 14 | [6 empty] | 14
15 | [6 empty] | 15 | [6 empty] | 15
16 | [6 empty] | 16 | [6 empty] | 16
17 | [6 empty] | 17 | [6 empty] | 17
18 | [6 empty] | 18 | [6 empty] | 18
19 | [6 empty] | 19 | [6 empty] | 19
20 | [6 empty] | 20 | [6 empty] | 20
21 | [6 empty] | 21 | [6 empty] | 21
22 | [6 empty] | 22 | [6 empty] | 22
23 | [6 empty] | 23 | [6 empty] | 23
24 | [6 empty] | 24 | [6 empty] | 24

## 2021 RRS New IFRO
Note that ERCOT has been working with NERC to include an update to ERCOT's Resource Contingency Criteria (RCC) (from 2750 MW to 2805 MW) in NERC's 2020 BAL-003 Interconnection Frequency Response Obligation (IFRO) assessment for 2021. ERCOT's preliminary IFRO for 2021 is 471 MW/0.1 Hz. As a result of this ERCOT expects that the minimum RRS-PFR limit for 2021 will change to 1420 MW. These preliminary 2021 quantities are based on an updated 2021 RRS table that was built using RCC of 2805 MW and the minimum RRS-PFR limit of 1420 MW.
2021-01-01 | [6 empty] | 2021-02-01 | [6 empty] | 2021-03-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | Total Equivalent PFRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | Total Equivalent PFRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | Total Equivalent PFRs
1 | 3053 | 1420 | 1633 | 1.65 | 53.49% | 4114.45 | 1 | 3170 | 1420 | 1750 | 1.83 | 55.21% | 4622.5 | 1 | 3092 | 1420 | 1672 | 1.74 | 54.08% | 4329.28
2 | 3053 | 1420 | 1633 | 1.65 | 53.49% | 4114.45 | 2 | 3170 | 1420 | 1750 | 1.83 | 55.21% | 4622.5 | 2 | 3092 | 1420 | 1672 | 1.74 | 54.08% | 4329.28
3 | 3053 | 1420 | 1633 | 1.65 | 53.49% | 4114.45 | 3 | 3092 | 1420 | 1672 | 1.74 | 54.08% | 4329.28 | 3 | 3170 | 1420 | 1750 | 1.83 | 55.21% | 4622.5
4 | 3053 | 1420 | 1633 | 1.65 | 53.49% | 4114.45 | 4 | 3092 | 1420 | 1672 | 1.74 | 54.08% | 4329.28 | 4 | 3170 | 1420 | 1750 | 1.83 | 55.21% | 4622.5
5 | 3053 | 1420 | 1633 | 1.65 | 53.49% | 4114.45 | 5 | 3092 | 1420 | 1672 | 1.74 | 54.08% | 4329.28 | 5 | 3170 | 1420 | 1750 | 1.83 | 55.21% | 4622.5
6 | 3053 | 1420 | 1633 | 1.65 | 53.49% | 4114.45 | 6 | 3092 | 1420 | 1672 | 1.74 | 54.08% | 4329.28 | 6 | 3170 | 1420 | 1750 | 1.83 | 55.21% | 4622.5
7 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89 | 7 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89 | 7 | 3002 | 1420 | 1582 | 1.58 | 52.7% | 3919.56
8 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89 | 8 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89 | 8 | 3002 | 1420 | 1582 | 1.58 | 52.7% | 3919.56
9 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89 | 9 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89 | 9 | 3002 | 1420 | 1582 | 1.58 | 52.7% | 3919.56
10 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89 | 10 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89 | 10 | 3002 | 1420 | 1582 | 1.58 | 52.7% | 3919.56
11 | 2880 | 1420 | 1460 | 1.44 | 50.69% | 3522.4 | 11 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89 | 11 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89
12 | 2880 | 1420 | 1460 | 1.44 | 50.69% | 3522.4 | 12 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89 | 12 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89
13 | 2880 | 1420 | 1460 | 1.44 | 50.69% | 3522.4 | 13 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89 | 13 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89
14 | 2880 | 1420 | 1460 | 1.44 | 50.69% | 3522.4 | 14 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89 | 14 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89
15 | 2880 | 1420 | 1460 | 1.44 | 50.69% | 3522.4 | 15 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89 | 15 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89
16 | 2880 | 1420 | 1460 | 1.44 | 50.69% | 3522.4 | 16 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89 | 16 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89
17 | 2880 | 1420 | 1460 | 1.44 | 50.69% | 3522.4 | 17 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89 | 17 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89
18 | 2880 | 1420 | 1460 | 1.44 | 50.69% | 3522.4 | 18 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89 | 18 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89
19 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89 | 19 | 3002 | 1420 | 1582 | 1.58 | 52.7% | 3919.56 | 19 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89
20 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89 | 20 | 3002 | 1420 | 1582 | 1.58 | 52.7% | 3919.56 | 20 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89
21 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89 | 21 | 3002 | 1420 | 1582 | 1.58 | 52.7% | 3919.56 | 21 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89
22 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89 | 22 | 3002 | 1420 | 1582 | 1.58 | 52.7% | 3919.56 | 22 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89
23 | 3053 | 1420 | 1633 | 1.65 | 53.49% | 4114.45 | 23 | 3170 | 1420 | 1750 | 1.83 | 55.21% | 4622.5 | 23 | 3092 | 1420 | 1672 | 1.74 | 54.08% | 4329.28
24 | 3053 | 1420 | 1633 | 1.65 | 53.49% | 4114.45 | 24 | 3170 | 1420 | 1750 | 1.83 | 55.21% | 4622.5 | 24 | 3092 | 1420 | 1672 | 1.74 | 54.08% | 4329.28
2021-04-01 | [6 empty] | 2021-05-01 | [6 empty] | 2021-06-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | Total Equivalent PFRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | Total Equivalent PFRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | Total Equivalent PFRs
1 | 3170 | 1420 | 1750 | 1.83 | 55.21% | 4622.5 | 1 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89 | 1 | 2658 | 1420 | 1238 | 1.28 | 46.58% | 3004.64
2 | 3170 | 1420 | 1750 | 1.83 | 55.21% | 4622.5 | 2 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89 | 2 | 2658 | 1420 | 1238 | 1.28 | 46.58% | 3004.64
3 | 3170 | 1420 | 1750 | 1.83 | 55.21% | 4622.5 | 3 | 3002 | 1420 | 1582 | 1.58 | 52.7% | 3919.56 | 3 | 2783 | 1420 | 1363 | 1.39 | 48.98% | 3314.57
4 | 3170 | 1420 | 1750 | 1.83 | 55.21% | 4622.5 | 4 | 3002 | 1420 | 1582 | 1.58 | 52.7% | 3919.56 | 4 | 2783 | 1420 | 1363 | 1.39 | 48.98% | 3314.57
5 | 3170 | 1420 | 1750 | 1.83 | 55.21% | 4622.5 | 5 | 3002 | 1420 | 1582 | 1.58 | 52.7% | 3919.56 | 5 | 2783 | 1420 | 1363 | 1.39 | 48.98% | 3314.57
6 | 3170 | 1420 | 1750 | 1.83 | 55.21% | 4622.5 | 6 | 3002 | 1420 | 1582 | 1.58 | 52.7% | 3919.56 | 6 | 2783 | 1420 | 1363 | 1.39 | 48.98% | 3314.57
7 | 3053 | 1420 | 1633 | 1.65 | 53.49% | 4114.45 | 7 | 2880 | 1420 | 1460 | 1.44 | 50.69% | 3522.4 | 7 | 2605 | 1420 | 1185 | 1.24 | 45.49% | 2889.4
8 | 3053 | 1420 | 1633 | 1.65 | 53.49% | 4114.45 | 8 | 2880 | 1420 | 1460 | 1.44 | 50.69% | 3522.4 | 8 | 2605 | 1420 | 1185 | 1.24 | 45.49% | 2889.4
9 | 3053 | 1420 | 1633 | 1.65 | 53.49% | 4114.45 | 9 | 2880 | 1420 | 1460 | 1.44 | 50.69% | 3522.4 | 9 | 2605 | 1420 | 1185 | 1.24 | 45.49% | 2889.4
10 | 3053 | 1420 | 1633 | 1.65 | 53.49% | 4114.45 | 10 | 2880 | 1420 | 1460 | 1.44 | 50.69% | 3522.4 | 10 | 2605 | 1420 | 1185 | 1.24 | 45.49% | 2889.4
11 | 3002 | 1420 | 1582 | 1.58 | 52.7% | 3919.56 | 11 | 2658 | 1420 | 1238 | 1.28 | 46.58% | 3004.64 | 11 | 2429 | 1420 | 1009 | 1.08 | 41.54% | 2509.72
12 | 3002 | 1420 | 1582 | 1.58 | 52.7% | 3919.56 | 12 | 2658 | 1420 | 1238 | 1.28 | 46.58% | 3004.64 | 12 | 2429 | 1420 | 1009 | 1.08 | 41.54% | 2509.72
13 | 3002 | 1420 | 1582 | 1.58 | 52.7% | 3919.56 | 13 | 2658 | 1420 | 1238 | 1.28 | 46.58% | 3004.64 | 13 | 2429 | 1420 | 1009 | 1.08 | 41.54% | 2509.72
14 | 3002 | 1420 | 1582 | 1.58 | 52.7% | 3919.56 | 14 | 2658 | 1420 | 1238 | 1.28 | 46.58% | 3004.64 | 14 | 2429 | 1420 | 1009 | 1.08 | 41.54% | 2509.72
15 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89 | 15 | 2605 | 1420 | 1185 | 1.24 | 45.49% | 2889.4 | 15 | 2383 | 1420 | 963 | 1.04 | 40.41% | 2421.52
16 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89 | 16 | 2605 | 1420 | 1185 | 1.24 | 45.49% | 2889.4 | 16 | 2383 | 1420 | 963 | 1.04 | 40.41% | 2421.52
17 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89 | 17 | 2605 | 1420 | 1185 | 1.24 | 45.49% | 2889.4 | 17 | 2383 | 1420 | 963 | 1.04 | 40.41% | 2421.52
18 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89 | 18 | 2605 | 1420 | 1185 | 1.24 | 45.49% | 2889.4 | 18 | 2383 | 1420 | 963 | 1.04 | 40.41% | 2421.52
19 | 3002 | 1420 | 1582 | 1.58 | 52.7% | 3919.56 | 19 | 2658 | 1420 | 1238 | 1.28 | 46.58% | 3004.64 | 19 | 2429 | 1420 | 1009 | 1.08 | 41.54% | 2509.72
20 | 3002 | 1420 | 1582 | 1.58 | 52.7% | 3919.56 | 20 | 2658 | 1420 | 1238 | 1.28 | 46.58% | 3004.64 | 20 | 2429 | 1420 | 1009 | 1.08 | 41.54% | 2509.72
21 | 3002 | 1420 | 1582 | 1.58 | 52.7% | 3919.56 | 21 | 2658 | 1420 | 1238 | 1.28 | 46.58% | 3004.64 | 21 | 2429 | 1420 | 1009 | 1.08 | 41.54% | 2509.72
22 | 3002 | 1420 | 1582 | 1.58 | 52.7% | 3919.56 | 22 | 2658 | 1420 | 1238 | 1.28 | 46.58% | 3004.64 | 22 | 2429 | 1420 | 1009 | 1.08 | 41.54% | 2509.72
23 | 3170 | 1420 | 1750 | 1.83 | 55.21% | 4622.5 | 23 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89 | 23 | 2658 | 1420 | 1238 | 1.28 | 46.58% | 3004.64
24 | 3170 | 1420 | 1750 | 1.83 | 55.21% | 4622.5 | 24 | 2959 | 1420 | 1539 | 1.51 | 52.01% | 3743.89 | 24 | 2658 | 1420 | 1238 | 1.28 | 46.58% | 3004.64
2021-07-01 | [6 empty] | 2021-08-01 | [6 empty] | 2021-09-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | Total Equivalent PFRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | Total Equivalent PFRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | Total Equivalent PFRs
1 | 2469 | 1420 | 1049 | 1.12 | 42.49% | 2594.88 | 1 | 2429 | 1420 | 1009 | 1.08 | 41.54% | 2509.72 | 1 | 2605 | 1420 | 1185 | 1.24 | 45.49% | 2889.4
2 | 2469 | 1420 | 1049 | 1.12 | 42.49% | 2594.88 | 2 | 2429 | 1420 | 1009 | 1.08 | 41.54% | 2509.72 | 2 | 2605 | 1420 | 1185 | 1.24 | 45.49% | 2889.4
3 | 2566 | 1420 | 1146 | 1.19 | 44.66% | 2783.74 | 3 | 2469 | 1420 | 1049 | 1.12 | 42.49% | 2594.88 | 3 | 2712 | 1420 | 1292 | 1.33 | 47.64% | 3138.36
4 | 2566 | 1420 | 1146 | 1.19 | 44.66% | 2783.74 | 4 | 2469 | 1420 | 1049 | 1.12 | 42.49% | 2594.88 | 4 | 2712 | 1420 | 1292 | 1.33 | 47.64% | 3138.36
5 | 2566 | 1420 | 1146 | 1.19 | 44.66% | 2783.74 | 5 | 2469 | 1420 | 1049 | 1.12 | 42.49% | 2594.88 | 5 | 2712 | 1420 | 1292 | 1.33 | 47.64% | 3138.36
6 | 2566 | 1420 | 1146 | 1.19 | 44.66% | 2783.74 | 6 | 2469 | 1420 | 1049 | 1.12 | 42.49% | 2594.88 | 6 | 2712 | 1420 | 1292 | 1.33 | 47.64% | 3138.36
7 | 2469 | 1420 | 1049 | 1.12 | 42.49% | 2594.88 | 7 | 2383 | 1420 | 963 | 1.04 | 40.41% | 2421.52 | 7 | 2605 | 1420 | 1185 | 1.24 | 45.49% | 2889.4
8 | 2469 | 1420 | 1049 | 1.12 | 42.49% | 2594.88 | 8 | 2383 | 1420 | 963 | 1.04 | 40.41% | 2421.52 | 8 | 2605 | 1420 | 1185 | 1.24 | 45.49% | 2889.4
9 | 2469 | 1420 | 1049 | 1.12 | 42.49% | 2594.88 | 9 | 2383 | 1420 | 963 | 1.04 | 40.41% | 2421.52 | 9 | 2605 | 1420 | 1185 | 1.24 | 45.49% | 2889.4
10 | 2469 | 1420 | 1049 | 1.12 | 42.49% | 2594.88 | 10 | 2383 | 1420 | 963 | 1.04 | 40.41% | 2421.52 | 10 | 2605 | 1420 | 1185 | 1.24 | 45.49% | 2889.4
11 | 2300 | 1420 | 880 | 1 | 38.26% | 2300 | 11 | 2300 | 1420 | 880 | 1 | 38.26% | 2300 | 11 | 2469 | 1420 | 1049 | 1.12 | 42.49% | 2594.88
12 | 2300 | 1420 | 880 | 1 | 38.26% | 2300 | 12 | 2300 | 1420 | 880 | 1 | 38.26% | 2300 | 12 | 2469 | 1420 | 1049 | 1.12 | 42.49% | 2594.88
13 | 2300 | 1420 | 880 | 1 | 38.26% | 2300 | 13 | 2300 | 1420 | 880 | 1 | 38.26% | 2300 | 13 | 2469 | 1420 | 1049 | 1.12 | 42.49% | 2594.88
14 | 2300 | 1420 | 880 | 1 | 38.26% | 2300 | 14 | 2300 | 1420 | 880 | 1 | 38.26% | 2300 | 14 | 2469 | 1420 | 1049 | 1.12 | 42.49% | 2594.88
15 | 2300 | 1420 | 880 | 1 | 38.26% | 2300 | 15 | 2300 | 1420 | 880 | 1 | 38.26% | 2300 | 15 | 2383 | 1420 | 963 | 1.04 | 40.41% | 2421.52
16 | 2300 | 1420 | 880 | 1 | 38.26% | 2300 | 16 | 2300 | 1420 | 880 | 1 | 38.26% | 2300 | 16 | 2383 | 1420 | 963 | 1.04 | 40.41% | 2421.52
17 | 2300 | 1420 | 880 | 1 | 38.26% | 2300 | 17 | 2300 | 1420 | 880 | 1 | 38.26% | 2300 | 17 | 2383 | 1420 | 963 | 1.04 | 40.41% | 2421.52
18 | 2300 | 1420 | 880 | 1 | 38.26% | 2300 | 18 | 2300 | 1420 | 880 | 1 | 38.26% | 2300 | 18 | 2383 | 1420 | 963 | 1.04 | 40.41% | 2421.52
19 | 2300 | 1420 | 880 | 1 | 38.26% | 2300 | 19 | 2300 | 1420 | 880 | 1 | 38.26% | 2300 | 19 | 2469 | 1420 | 1049 | 1.12 | 42.49% | 2594.88
20 | 2300 | 1420 | 880 | 1 | 38.26% | 2300 | 20 | 2300 | 1420 | 880 | 1 | 38.26% | 2300 | 20 | 2469 | 1420 | 1049 | 1.12 | 42.49% | 2594.88
21 | 2300 | 1420 | 880 | 1 | 38.26% | 2300 | 21 | 2300 | 1420 | 880 | 1 | 38.26% | 2300 | 21 | 2469 | 1420 | 1049 | 1.12 | 42.49% | 2594.88
22 | 2300 | 1420 | 880 | 1 | 38.26% | 2300 | 22 | 2300 | 1420 | 880 | 1 | 38.26% | 2300 | 22 | 2469 | 1420 | 1049 | 1.12 | 42.49% | 2594.88
23 | 2469 | 1420 | 1049 | 1.12 | 42.49% | 2594.88 | 23 | 2429 | 1420 | 1009 | 1.08 | 41.54% | 2509.72 | 23 | 2605 | 1420 | 1185 | 1.24 | 45.49% | 2889.4
24 | 2469 | 1420 | 1049 | 1.12 | 42.49% | 2594.88 | 24 | 2429 | 1420 | 1009 | 1.08 | 41.54% | 2509.72 | 24 | 2605 | 1420 | 1185 | 1.24 | 45.49% | 2889.4
2021-10-01 | [6 empty] | 2021-11-01 | [6 empty] | 2021-12-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs |  | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs |  | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs
1 | [6 empty] | 1 | [6 empty] | 1
2 | [6 empty] | 2 | [6 empty] | 2
3 | [6 empty] | 3 | [6 empty] | 3
4 | [6 empty] | 4 | [6 empty] | 4
5 | [6 empty] | 5 | [6 empty] | 5
6 | [6 empty] | 6 | [6 empty] | 6
7 | [6 empty] | 7 | [6 empty] | 7
8 | [6 empty] | 8 | [6 empty] | 8
9 | [6 empty] | 9 | [6 empty] | 9
10 | [6 empty] | 10 | [6 empty] | 10
11 | [6 empty] | 11 | [6 empty] | 11
12 | [6 empty] | 12 | [6 empty] | 12
13 | [6 empty] | 13 | [6 empty] | 13
14 | [6 empty] | 14 | [6 empty] | 14
15 | [6 empty] | 15 | [6 empty] | 15
16 | [6 empty] | 16 | [6 empty] | 16
17 | [6 empty] | 17 | [6 empty] | 17
18 | [6 empty] | 18 | [6 empty] | 18
19 | [6 empty] | 19 | [6 empty] | 19
20 | [6 empty] | 20 | [6 empty] | 20
21 | [6 empty] | 21 | [6 empty] | 21
22 | [6 empty] | 22 | [6 empty] | 22
23 | [6 empty] | 23 | [6 empty] | 23
24 | [6 empty] | 24 | [6 empty] | 24

## Charts
Month | Date | Group | HE | Type | 2020 RRS Value | 2021 RRS Value | 2021 Upd RRS Value | Delta | Delta-2 | Delta-3 | 2020 Total Equivalent PFRs | 2021 Total Equivalent PFRs | Month | Jun |  |  | Responsive Reserve Requirement Comparison for June
Jan | 2018-01-01 | a. HE1-2 & HE23-24 | 1 | RRS | 2998 | 2959 | 3053 | 39 | 94 | 55 | 4329.26 | 4112.75 | Type | RRS
Jan | 2018-01-01 | a. HE1-2 & HE23-24 | 2 | RRS | 2998 | 2959 | 3053 | 39 | 94 | 55 | 4329.26 | 4112.75
Jan | 2018-01-01 | b. HE3-6 | 3 | RRS | 2959 | 2959 | 3053 | 0 | 94 | 94 | 4114.4 | 4112.75 | Row Labels | 2020 | 2021 (Curr IFRO) | 2021 (Upd IFRO)
Jan | 2018-01-01 | b. HE3-6 | 4 | RRS | 2959 | 2959 | 3053 | 0 | 94 | 94 | 4114.4 | 4112.75 | a. HE1-2 & HE23-24 | 2553 | 2598 | 2658
Jan | 2018-01-01 | b. HE3-6 | 5 | RRS | 2959 | 2959 | 3053 | 0 | 94 | 94 | 4114.4 | 4112.75 | b. HE3-6 | 2598 | 2707 | 2783
Jan | 2018-01-01 | b. HE3-6 | 6 | RRS | 2959 | 2959 | 3053 | 0 | 94 | 94 | 4114.4 | 4112.75 | c. HE7-10 | 2523 | 2553 | 2605
Jan | 2018-01-01 | c. HE7-10 | 7 | RRS | 2797 | 2868 | 2959 | 71 | 91 | 162 | 3521.68 | 3744.18 | d. HE11-14 | 2372 | 2409 | 2429
Jan | 2018-01-01 | c. HE7-10 | 8 | RRS | 2797 | 2868 | 2959 | 71 | 91 | 162 | 3521.68 | 3744.18 | e. HE15-18 | 2341 | 2372 | 2383
Jan | 2018-01-01 | c. HE7-10 | 9 | RRS | 2797 | 2868 | 2959 | 71 | 91 | 162 | 3521.68 | 3744.18 | f. HE19-22 | 2372 | 2409 | 2429
Jan | 2018-01-01 | c. HE7-10 | 10 | RRS | 2797 | 2868 | 2959 | 71 | 91 | 162 | 3521.68 | 3744.18
Jan | 2018-01-01 | d. HE11-14 | 11 | RRS | 2868 | 2797 | 2880 | 71 | 83 | 12 | 3744.18 | 3521.68
Jan | 2018-01-01 | d. HE11-14 | 12 | RRS | 2868 | 2797 | 2880 | 71 | 83 | 12 | 3744.18 | 3521.68
Jan | 2018-01-01 | d. HE11-14 | 13 | RRS | 2868 | 2797 | 2880 | 71 | 83 | 12 | 3744.18 | 3521.68
Jan | 2018-01-01 | d. HE11-14 | 14 | RRS | 2868 | 2797 | 2880 | 71 | 83 | 12 | 3744.18 | 3521.68
Jan | 2018-01-01 | e. HE15-18 | 15 | RRS | 2868 | 2797 | 2880 | 71 | 83 | 12 | 3744.18 | 3521.68
Jan | 2018-01-01 | e. HE15-18 | 16 | RRS | 2868 | 2797 | 2880 | 71 | 83 | 12 | 3744.18 | 3521.68
Jan | 2018-01-01 | e. HE15-18 | 17 | RRS | 2868 | 2797 | 2880 | 71 | 83 | 12 | 3744.18 | 3521.68
Jan | 2018-01-01 | e. HE15-18 | 18 | RRS | 2868 | 2797 | 2880 | 71 | 83 | 12 | 3744.18 | 3521.68
Jan | 2018-01-01 | f. HE19-22 | 19 | RRS | 2868 | 2868 | 2959 | 0 | 91 | 91 | 3744.18 | 3744.18
Jan | 2018-01-01 | f. HE19-22 | 20 | RRS | 2868 | 2868 | 2959 | 0 | 91 | 91 | 3744.18 | 3744.18
Jan | 2018-01-01 | f. HE19-22 | 21 | RRS | 2868 | 2868 | 2959 | 0 | 91 | 91 | 3744.18 | 3744.18
Jan | 2018-01-01 | f. HE19-22 | 22 | RRS | 2868 | 2868 | 2959 | 0 | 91 | 91 | 3744.18 | 3744.18
Jan | 2018-01-01 | a. HE1-2 & HE23-24 | 23 | RRS | 2998 | 2959 | 3053 | 39 | 94 | 55 | 4329.26 | 4112.75
Jan | 2018-01-01 | a. HE1-2 & HE23-24 | 24 | RRS | 2998 | 2959 | 3053 | 39 | 94 | 55 | 4329.26 | 4112.75
Feb | 2018-02-01 | a. HE1-2 & HE23-24 | 1 | RRS | 2998 | 3086 | 3170 | 88 | 84 | 172 | 4329.26 | 4623.16
Feb | 2018-02-01 | a. HE1-2 & HE23-24 | 2 | RRS | 2998 | 3086 | 3170 | 88 | 84 | 172 | 4329.26 | 4623.16
Feb | 2018-02-01 | b. HE3-6 | 3 | RRS | 2998 | 2998 | 3092 | 0 | 94 | 94 | 4329.26 | 4329.26
Feb | 2018-02-01 | b. HE3-6 | 4 | RRS | 2998 | 2998 | 3092 | 0 | 94 | 94 | 4329.26 | 4329.26
Feb | 2018-02-01 | b. HE3-6 | 5 | RRS | 2998 | 2998 | 3092 | 0 | 94 | 94 | 4329.26 | 4329.26 | Type | RRS |  |  | Hourly Average Responsive Reserve Requirement Comparison
Feb | 2018-02-01 | b. HE3-6 | 6 | RRS | 2998 | 2998 | 3092 | 0 | 94 | 94 | 4329.26 | 4329.26
Feb | 2018-02-01 | c. HE7-10 | 7 | RRS | 2868 | 2868 | 2959 | 0 | 91 | 91 | 3744.18 | 3744.18 | Row Labels | 2020 Hourly Avg | 2021 (Curr IFRO) Hourly Avg | 2021 (Upd IFRO) Hourly Avg
Feb | 2018-02-01 | c. HE7-10 | 8 | RRS | 2868 | 2868 | 2959 | 0 | 91 | 91 | 3744.18 | 3744.18 | Jan | 2893 | 2874.6667 | 2964 | -18.3333 | 89.3333 | 71
Feb | 2018-02-01 | c. HE7-10 | 9 | RRS | 2868 | 2868 | 2959 | 0 | 91 | 91 | 3744.18 | 3744.18 | Feb | 2911.3333 | 2932.6667 | 3023.5 | 21.3333 | 90.8333 | 112.1667
Feb | 2018-02-01 | c. HE7-10 | 10 | RRS | 2868 | 2868 | 2959 | 0 | 91 | 91 | 3744.18 | 3744.18 | Mar | 2969.1667 | 2932.6667 | 3023.5 | -36.5 | 90.8333 | 54.3333
Feb | 2018-02-01 | d. HE11-14 | 11 | RRS | 2868 | 2868 | 2959 | 0 | 91 | 91 | 3744.18 | 3744.18 | Apr | 2975.6667 | 2969.1667 | 3059.3333 | -6.5 | 90.1667 | 83.6667
Feb | 2018-02-01 | d. HE11-14 | 12 | RRS | 2868 | 2868 | 2959 | 0 | 91 | 91 | 3744.18 | 3744.18 | May | 2666.8333 | 2720.3333 | 2793.6667 | 53.5 | 73.3333 | 126.8333
Feb | 2018-02-01 | d. HE11-14 | 13 | RRS | 2868 | 2868 | 2959 | 0 | 91 | 91 | 3744.18 | 3744.18 | Jun | 2459.8333 | 2508 | 2547.8333 | 48.1667 | 39.8333 | 88
Feb | 2018-02-01 | d. HE11-14 | 14 | RRS | 2868 | 2868 | 2959 | 0 | 91 | 91 | 3744.18 | 3744.18 | Jul | 2372.5 | 2383.8333 | 2400.6667 | 11.3333 | 16.8333 | 28.1667
Feb | 2018-02-01 | e. HE15-18 | 15 | RRS | 2868 | 2868 | 2959 | 0 | 91 | 91 | 3744.18 | 3744.18 | Aug | 2353.5 | 2353.5 | 2363.5 | 0 | 10 | 10
Feb | 2018-02-01 | e. HE15-18 | 16 | RRS | 2868 | 2868 | 2959 | 0 | 91 | 91 | 3744.18 | 3744.18 | Sep | 2469.8333 | 2500.5 | 2540.5 | 30.6667 | 40 | 70.6667
Feb | 2018-02-01 | e. HE15-18 | 17 | RRS | 2868 | 2868 | 2959 | 0 | 91 | 91 | 3744.18 | 3744.18 | Oct | 2799 | 0 | 0 | -2799 | 0 | -2799
Feb | 2018-02-01 | e. HE15-18 | 18 | RRS | 2868 | 2868 | 2959 | 0 | 91 | 91 | 3744.18 | 3744.18 | Nov | 2932.9565 | 0 | 0 | -2932.9565 | 0 | -2932.9565
Feb | 2018-02-01 | f. HE19-22 | 19 | RRS | 2868 | 2908 | 3002 | 40 | 94 | 134 | 3744.18 | 3920.1 | Dec | 2889.36 | 0 | 0 | -2889.36 | 0 | -2889.36
Feb | 2018-02-01 | f. HE19-22 | 20 | RRS | 2868 | 2908 | 3002 | 40 | 94 | 134 | 3744.18 | 3920.1
Feb | 2018-02-01 | f. HE19-22 | 21 | RRS | 2868 | 2908 | 3002 | 40 | 94 | 134 | 3744.18 | 3920.1
Feb | 2018-02-01 | f. HE19-22 | 22 | RRS | 2868 | 2908 | 3002 | 40 | 94 | 134 | 3744.18 | 3920.1
Feb | 2018-02-01 | a. HE1-2 & HE23-24 | 23 | RRS | 2998 | 3086 | 3170 | 88 | 84 | 172 | 4329.26 | 4623.16 | Type | RRS
Feb | 2018-02-01 | a. HE1-2 & HE23-24 | 24 | RRS | 2998 | 3086 | 3170 | 88 | 84 | 172 | 4329.26 | 4623.16
Mar | 2018-03-01 | a. HE1-2 & HE23-24 | 1 | RRS | 3086 | 2998 | 3092 | 88 | 94 | 6 | 4623.16 | 4329.26 | Month | Group | Max of Delta | Max of Delta-2 | Max of Delta-3
Mar | 2018-03-01 | a. HE1-2 & HE23-24 | 2 | RRS | 3086 | 2998 | 3092 | 88 | 94 | 6 | 4623.16 | 4329.26 | Jan | a. HE1-2 & HE23-24 | 39 | 94 | 55
Mar | 2018-03-01 | b. HE3-6 | 3 | RRS | 3086 | 3086 | 3170 | 0 | 84 | 84 | 4623.16 | 4623.16 | Jan | b. HE3-6 | 0 | 94 | 94
Mar | 2018-03-01 | b. HE3-6 | 4 | RRS | 3086 | 3086 | 3170 | 0 | 84 | 84 | 4623.16 | 4623.16 | Jan | c. HE7-10 | 71 | 91 | 162
Mar | 2018-03-01 | b. HE3-6 | 5 | RRS | 3086 | 3086 | 3170 | 0 | 84 | 84 | 4623.16 | 4623.16 | Jan | d. HE11-14 | 71 | 83 | 12
Mar | 2018-03-01 | b. HE3-6 | 6 | RRS | 3086 | 3086 | 3170 | 0 | 84 | 84 | 4623.16 | 4623.16 | Jan | e. HE15-18 | 71 | 83 | 12
Mar | 2018-03-01 | c. HE7-10 | 7 | RRS | 2959 | 2908 | 3002 | 51 | 94 | 43 | 4112.75 | 3920.1 | Jan | f. HE19-22 | 0 | 91 | 91
Mar | 2018-03-01 | c. HE7-10 | 8 | RRS | 2959 | 2908 | 3002 | 51 | 94 | 43 | 4112.75 | 3920.1 | Jan Total |  | 71 | 94 | 162
Mar | 2018-03-01 | c. HE7-10 | 9 | RRS | 2959 | 2908 | 3002 | 51 | 94 | 43 | 4112.75 | 3920.1 | Feb | a. HE1-2 & HE23-24 | 88 | 84 | 172
Mar | 2018-03-01 | c. HE7-10 | 10 | RRS | 2959 | 2908 | 3002 | 51 | 94 | 43 | 4112.75 | 3920.1 | Feb | b. HE3-6 | 0 | 94 | 94
Mar | 2018-03-01 | d. HE11-14 | 11 | RRS | 2908 | 2868 | 2959 | 40 | 91 | 51 | 3920.1 | 3744.18 | Feb | c. HE7-10 | 0 | 91 | 91
Mar | 2018-03-01 | d. HE11-14 | 12 | RRS | 2908 | 2868 | 2959 | 40 | 91 | 51 | 3920.1 | 3744.18 | Feb | d. HE11-14 | 0 | 91 | 91
Mar | 2018-03-01 | d. HE11-14 | 13 | RRS | 2908 | 2868 | 2959 | 40 | 91 | 51 | 3920.1 | 3744.18 | Feb | e. HE15-18 | 0 | 91 | 91
Mar | 2018-03-01 | d. HE11-14 | 14 | RRS | 2908 | 2868 | 2959 | 40 | 91 | 51 | 3920.1 | 3744.18 | Feb | f. HE19-22 | 40 | 94 | 134
Mar | 2018-03-01 | e. HE15-18 | 15 | RRS | 2868 | 2868 | 2959 | 0 | 91 | 91 | 3744.18 | 3744.18 | Feb Total |  | 88 | 94 | 172
Mar | 2018-03-01 | e. HE15-18 | 16 | RRS | 2868 | 2868 | 2959 | 0 | 91 | 91 | 3744.18 | 3744.18 | Mar | a. HE1-2 & HE23-24 | 88 | 94 | 6
Mar | 2018-03-01 | e. HE15-18 | 17 | RRS | 2868 | 2868 | 2959 | 0 | 91 | 91 | 3744.18 | 3744.18 | Mar | b. HE3-6 | 0 | 84 | 84
Mar | 2018-03-01 | e. HE15-18 | 18 | RRS | 2868 | 2868 | 2959 | 0 | 91 | 91 | 3744.18 | 3744.18 | Mar | c. HE7-10 | 51 | 94 | 43
Mar | 2018-03-01 | f. HE19-22 | 19 | RRS | 2908 | 2868 | 2959 | 40 | 91 | 51 | 3920.1 | 3744.18 | Mar | d. HE11-14 | 40 | 91 | 51
Mar | 2018-03-01 | f. HE19-22 | 20 | RRS | 2908 | 2868 | 2959 | 40 | 91 | 51 | 3920.1 | 3744.18 | Mar | e. HE15-18 | 0 | 91 | 91
Mar | 2018-03-01 | f. HE19-22 | 21 | RRS | 2908 | 2868 | 2959 | 40 | 91 | 51 | 3920.1 | 3744.18 | Mar | f. HE19-22 | 40 | 91 | 51
Mar | 2018-03-01 | f. HE19-22 | 22 | RRS | 2908 | 2868 | 2959 | 40 | 91 | 51 | 3920.1 | 3744.18 | Mar Total |  | 88 | 94 | 91
Mar | 2018-03-01 | a. HE1-2 & HE23-24 | 23 | RRS | 3086 | 2998 | 3092 | 88 | 94 | 6 | 4623.16 | 4329.26 | Apr | a. HE1-2 & HE23-24 | 0 | 84 | 84
Mar | 2018-03-01 | a. HE1-2 & HE23-24 | 24 | RRS | 3086 | 2998 | 3092 | 88 | 94 | 6 | 4623.16 | 4329.26 | Apr | b. HE3-6 | 0 | 84 | 84
Apr | 2018-04-01 | a. HE1-2 & HE23-24 | 1 | RRS | 3086 | 3086 | 3170 | 0 | 84 | 84 | 4623.16 | 4623.16 | Apr | c. HE7-10 | 39 | 94 | 55
Apr | 2018-04-01 | a. HE1-2 & HE23-24 | 2 | RRS | 3086 | 3086 | 3170 | 0 | 84 | 84 | 4623.16 | 4623.16 | Apr | d. HE11-14 | 0 | 94 | 94
Apr | 2018-04-01 | b. HE3-6 | 3 | RRS | 3086 | 3086 | 3170 | 0 | 84 | 84 | 4623.16 | 4623.16 | Apr | e. HE15-18 | 0 | 91 | 91
Apr | 2018-04-01 | b. HE3-6 | 4 | RRS | 3086 | 3086 | 3170 | 0 | 84 | 84 | 4623.16 | 4623.16 | Apr | f. HE19-22 | 0 | 94 | 94
Apr | 2018-04-01 | b. HE3-6 | 5 | RRS | 3086 | 3086 | 3170 | 0 | 84 | 84 | 4623.16 | 4623.16 | Apr Total |  | 39 | 94 | 94
Apr | 2018-04-01 | b. HE3-6 | 6 | RRS | 3086 | 3086 | 3170 | 0 | 84 | 84 | 4623.16 | 4623.16 | May | a. HE1-2 & HE23-24 | 71 | 91 | 162
Apr | 2018-04-01 | c. HE7-10 | 7 | RRS | 2998 | 2959 | 3053 | 39 | 94 | 55 | 4329.26 | 4112.75 | May | b. HE3-6 | 40 | 94 | 134
Apr | 2018-04-01 | c. HE7-10 | 8 | RRS | 2998 | 2959 | 3053 | 39 | 94 | 55 | 4329.26 | 4112.75 | May | c. HE7-10 | 90 | 83 | 173
Apr | 2018-04-01 | c. HE7-10 | 9 | RRS | 2998 | 2959 | 3053 | 39 | 94 | 55 | 4329.26 | 4112.75 | May | d. HE11-14 | 45 | 60 | 105
Apr | 2018-04-01 | c. HE7-10 | 10 | RRS | 2998 | 2959 | 3053 | 39 | 94 | 55 | 4329.26 | 4112.75 | May | e. HE15-18 | 30 | 52 | 82
Apr | 2018-04-01 | d. HE11-14 | 11 | RRS | 2908 | 2908 | 3002 | 0 | 94 | 94 | 3920.1 | 3920.1 | May | f. HE19-22 | 45 | 60 | 105
Apr | 2018-04-01 | d. HE11-14 | 12 | RRS | 2908 | 2908 | 3002 | 0 | 94 | 94 | 3920.1 | 3920.1 | May Total |  | 90 | 94 | 173
Apr | 2018-04-01 | d. HE11-14 | 13 | RRS | 2908 | 2908 | 3002 | 0 | 94 | 94 | 3920.1 | 3920.1 | Jun | a. HE1-2 & HE23-24 | 45 | 60 | 105
Apr | 2018-04-01 | d. HE11-14 | 14 | RRS | 2908 | 2908 | 3002 | 0 | 94 | 94 | 3920.1 | 3920.1 | Jun | b. HE3-6 | 109 | 76 | 185
Apr | 2018-04-01 | e. HE15-18 | 15 | RRS | 2868 | 2868 | 2959 | 0 | 91 | 91 | 3744.18 | 3744.18 | Jun | c. HE7-10 | 30 | 52 | 82
Apr | 2018-04-01 | e. HE15-18 | 16 | RRS | 2868 | 2868 | 2959 | 0 | 91 | 91 | 3744.18 | 3744.18 | Jun | d. HE11-14 | 37 | 20 | 57
Apr | 2018-04-01 | e. HE15-18 | 17 | RRS | 2868 | 2868 | 2959 | 0 | 91 | 91 | 3744.18 | 3744.18 | Jun | e. HE15-18 | 31 | 11 | 42
Apr | 2018-04-01 | e. HE15-18 | 18 | RRS | 2868 | 2868 | 2959 | 0 | 91 | 91 | 3744.18 | 3744.18 | Jun | f. HE19-22 | 37 | 20 | 57
Apr | 2018-04-01 | f. HE19-22 | 19 | RRS | 2908 | 2908 | 3002 | 0 | 94 | 94 | 3920.1 | 3920.1 | Jun Total |  | 109 | 76 | 185
Apr | 2018-04-01 | f. HE19-22 | 20 | RRS | 2908 | 2908 | 3002 | 0 | 94 | 94 | 3920.1 | 3920.1 | Jul | a. HE1-2 & HE23-24 | 0 | 29 | 29
Apr | 2018-04-01 | f. HE19-22 | 21 | RRS | 2908 | 2908 | 3002 | 0 | 94 | 94 | 3920.1 | 3920.1 | Jul | b. HE3-6 | 37 | 43 | 80
Apr | 2018-04-01 | f. HE19-22 | 22 | RRS | 2908 | 2908 | 3002 | 0 | 94 | 94 | 3920.1 | 3920.1 | Jul | c. HE7-10 | 31 | 29 | 60
Apr | 2018-04-01 | a. HE1-2 & HE23-24 | 23 | RRS | 3086 | 3086 | 3170 | 0 | 84 | 84 | 4623.16 | 4623.16 | Jul | d. HE11-14 | 0 | 0 | 0
Apr | 2018-04-01 | a. HE1-2 & HE23-24 | 24 | RRS | 3086 | 3086 | 3170 | 0 | 84 | 84 | 4623.16 | 4623.16 | Jul | e. HE15-18 | 0 | 0 | 0
May | 2018-05-01 | a. HE1-2 & HE23-24 | 1 | RRS | 2797 | 2868 | 2959 | 71 | 91 | 162 | 3521.68 | 3744.18 | Jul | f. HE19-22 | 0 | 0 | 0
May | 2018-05-01 | a. HE1-2 & HE23-24 | 2 | RRS | 2797 | 2868 | 2959 | 71 | 91 | 162 | 3521.68 | 3744.18 | Jul Total |  | 37 | 43 | 80
May | 2018-05-01 | b. HE3-6 | 3 | RRS | 2868 | 2908 | 3002 | 40 | 94 | 134 | 3744.18 | 3920.1 | Aug | a. HE1-2 & HE23-24 | 0 | 20 | 20
May | 2018-05-01 | b. HE3-6 | 4 | RRS | 2868 | 2908 | 3002 | 40 | 94 | 134 | 3744.18 | 3920.1 | Aug | b. HE3-6 | 0 | 29 | 29
May | 2018-05-01 | b. HE3-6 | 5 | RRS | 2868 | 2908 | 3002 | 40 | 94 | 134 | 3744.18 | 3920.1 | Aug | c. HE7-10 | 0 | 11 | 11
May | 2018-05-01 | b. HE3-6 | 6 | RRS | 2868 | 2908 | 3002 | 40 | 94 | 134 | 3744.18 | 3920.1 | Aug | d. HE11-14 | 0 | 0 | 0
May | 2018-05-01 | c. HE7-10 | 7 | RRS | 2707 | 2797 | 2880 | 90 | 83 | 173 | 3314.23 | 3521.68 | Aug | e. HE15-18 | 0 | 0 | 0
May | 2018-05-01 | c. HE7-10 | 8 | RRS | 2707 | 2797 | 2880 | 90 | 83 | 173 | 3314.23 | 3521.68 | Aug | f. HE19-22 | 0 | 0 | 0
May | 2018-05-01 | c. HE7-10 | 9 | RRS | 2707 | 2797 | 2880 | 90 | 83 | 173 | 3314.23 | 3521.68 | Aug Total |  | 0 | 29 | 29
May | 2018-05-01 | c. HE7-10 | 10 | RRS | 2707 | 2797 | 2880 | 90 | 83 | 173 | 3314.23 | 3521.68 | Sep | a. HE1-2 & HE23-24 | 0 | 52 | 52
May | 2018-05-01 | d. HE11-14 | 11 | RRS | 2553 | 2598 | 2658 | 45 | 60 | 105 | 2889.72 | 3003.44 | Sep | b. HE3-6 | 92 | 67 | 159
May | 2018-05-01 | d. HE11-14 | 12 | RRS | 2553 | 2598 | 2658 | 45 | 60 | 105 | 2889.72 | 3003.44 | Sep | c. HE7-10 | 30 | 52 | 82
May | 2018-05-01 | d. HE11-14 | 13 | RRS | 2553 | 2598 | 2658 | 45 | 60 | 105 | 2889.72 | 3003.44 | Sep | d. HE11-14 | 31 | 29 | 60
May | 2018-05-01 | d. HE11-14 | 14 | RRS | 2553 | 2598 | 2658 | 45 | 60 | 105 | 2889.72 | 3003.44 | Sep | e. HE15-18 | 0 | 11 | 11
May | 2018-05-01 | e. HE15-18 | 15 | RRS | 2523 | 2553 | 2605 | 30 | 52 | 82 | 2783.87 | 2889.72 | Sep | f. HE19-22 | 31 | 29 | 60
May | 2018-05-01 | e. HE15-18 | 16 | RRS | 2523 | 2553 | 2605 | 30 | 52 | 82 | 2783.87 | 2889.72 | Sep Total |  | 92 | 67 | 159
May | 2018-05-01 | e. HE15-18 | 17 | RRS | 2523 | 2553 | 2605 | 30 | 52 | 82 | 2783.87 | 2889.72 | Oct | a. HE1-2 & HE23-24 | 2908 | 0 | -2908
May | 2018-05-01 | e. HE15-18 | 18 | RRS | 2523 | 2553 | 2605 | 30 | 52 | 82 | 2783.87 | 2889.72 | Oct | b. HE3-6 | 2959 | 0 | -2959
May | 2018-05-01 | f. HE19-22 | 19 | RRS | 2553 | 2598 | 2658 | 45 | 60 | 105 | 2889.72 | 3003.44 | Oct | c. HE7-10 | 2868 | 0 | -2868
May | 2018-05-01 | f. HE19-22 | 20 | RRS | 2553 | 2598 | 2658 | 45 | 60 | 105 | 2889.72 | 3003.44 | Oct | d. HE11-14 | 2707 | 0 | -2707
May | 2018-05-01 | f. HE19-22 | 21 | RRS | 2553 | 2598 | 2658 | 45 | 60 | 105 | 2889.72 | 3003.44 | Oct | e. HE15-18 | 2645 | 0 | -2645
May | 2018-05-01 | f. HE19-22 | 22 | RRS | 2553 | 2598 | 2658 | 45 | 60 | 105 | 2889.72 | 3003.44 | Oct | f. HE19-22 | 2707 | 0 | -2707
May | 2018-05-01 | a. HE1-2 & HE23-24 | 23 | RRS | 2797 | 2868 | 2959 | 71 | 91 | 162 | 3521.68 | 3744.18 | Oct Total |  | 2959 | 0 | -2645
May | 2018-05-01 | a. HE1-2 & HE23-24 | 24 | RRS | 2797 | 2868 | 2959 | 71 | 91 | 162 | 3521.68 | 3744.18 | Nov | a. HE1-2 & HE23-24 | 3086 | 0 | -3086
Jun | 2018-06-01 | a. HE1-2 & HE23-24 | 1 | RRS | 2553 | 2598 | 2658 | 45 | 60 | 105 | 2889.72 | 3003.44 | Nov | b. HE3-6 | 2998 | 0 | -2998
Jun | 2018-06-01 | a. HE1-2 & HE23-24 | 2 | RRS | 2553 | 2598 | 2658 | 45 | 60 | 105 | 2889.72 | 3003.44 | Nov | c. HE7-10 | 2908 | 0 | -2908
Jun | 2018-06-01 | b. HE3-6 | 3 | RRS | 2598 | 2707 | 2783 | 109 | 76 | 185 | 3003.44 | 3314.23 | Nov | d. HE11-14 | 2868 | 0 | -2868
Jun | 2018-06-01 | b. HE3-6 | 4 | RRS | 2598 | 2707 | 2783 | 109 | 76 | 185 | 3003.44 | 3314.23 | Nov | e. HE15-18 | 2868 | 0 | -2868
Jun | 2018-06-01 | b. HE3-6 | 5 | RRS | 2598 | 2707 | 2783 | 109 | 76 | 185 | 3003.44 | 3314.23 | Nov | f. HE19-22 | 2908 | 0 | -2908
Jun | 2018-06-01 | b. HE3-6 | 6 | RRS | 2598 | 2707 | 2783 | 109 | 76 | 185 | 3003.44 | 3314.23 | Nov Total |  | 3086 | 0 | -2868
Jun | 2018-06-01 | c. HE7-10 | 7 | RRS | 2523 | 2553 | 2605 | 30 | 52 | 82 | 2783.87 | 2889.72 | Dec | a. HE1-2 & HE23-24 | 3086 | 0 | -2998
Jun | 2018-06-01 | c. HE7-10 | 8 | RRS | 2523 | 2553 | 2605 | 30 | 52 | 82 | 2783.87 | 2889.72 | Dec | b. HE3-6 | 2959 | 0 | -2959
Jun | 2018-06-01 | c. HE7-10 | 9 | RRS | 2523 | 2553 | 2605 | 30 | 52 | 82 | 2783.87 | 2889.72 | Dec | c. HE7-10 | 2868 | 0 | -2868
Jun | 2018-06-01 | c. HE7-10 | 10 | RRS | 2523 | 2553 | 2605 | 30 | 52 | 82 | 2783.87 | 2889.72 | Dec | d. HE11-14 | 2797 | 0 | -2797
Jun | 2018-06-01 | d. HE11-14 | 11 | RRS | 2372 | 2409 | 2429 | 37 | 20 | 57 | 2420.88 | 2509.72 | Dec | e. HE15-18 | 2797 | 0 | -2797
Jun | 2018-06-01 | d. HE11-14 | 12 | RRS | 2372 | 2409 | 2429 | 37 | 20 | 57 | 2420.88 | 2509.72 | Dec | f. HE19-22 | 2868 | 0 | -2868
Jun | 2018-06-01 | d. HE11-14 | 13 | RRS | 2372 | 2409 | 2429 | 37 | 20 | 57 | 2420.88 | 2509.72 | Dec Total |  | 3086 | 0 | -2797
Jun | 2018-06-01 | d. HE11-14 | 14 | RRS | 2372 | 2409 | 2429 | 37 | 20 | 57 | 2420.88 | 2509.72 | Grand Total |  | 3086 | 94 | 185
Jun | 2018-06-01 | e. HE15-18 | 15 | RRS | 2341 | 2372 | 2383 | 31 | 11 | 42 | 2352.91 | 2420.88
Jun | 2018-06-01 | e. HE15-18 | 16 | RRS | 2341 | 2372 | 2383 | 31 | 11 | 42 | 2352.91 | 2420.88
Jun | 2018-06-01 | e. HE15-18 | 17 | RRS | 2341 | 2372 | 2383 | 31 | 11 | 42 | 2352.91 | 2420.88
Jun | 2018-06-01 | e. HE15-18 | 18 | RRS | 2341 | 2372 | 2383 | 31 | 11 | 42 | 2352.91 | 2420.88
Jun | 2018-06-01 | f. HE19-22 | 19 | RRS | 2372 | 2409 | 2429 | 37 | 20 | 57 | 2420.88 | 2509.72
Jun | 2018-06-01 | f. HE19-22 | 20 | RRS | 2372 | 2409 | 2429 | 37 | 20 | 57 | 2420.88 | 2509.72
Jun | 2018-06-01 | f. HE19-22 | 21 | RRS | 2372 | 2409 | 2429 | 37 | 20 | 57 | 2420.88 | 2509.72
Jun | 2018-06-01 | f. HE19-22 | 22 | RRS | 2372 | 2409 | 2429 | 37 | 20 | 57 | 2420.88 | 2509.72
Jun | 2018-06-01 | a. HE1-2 & HE23-24 | 23 | RRS | 2553 | 2598 | 2658 | 45 | 60 | 105 | 2889.72 | 3003.44
Jun | 2018-06-01 | a. HE1-2 & HE23-24 | 24 | RRS | 2553 | 2598 | 2658 | 45 | 60 | 105 | 2889.72 | 3003.44
Jul | 2018-07-01 | a. HE1-2 & HE23-24 | 1 | RRS | 2440 | 2440 | 2469 | 0 | 29 | 29 | 2594.8 | 2594.8
Jul | 2018-07-01 | a. HE1-2 & HE23-24 | 2 | RRS | 2440 | 2440 | 2469 | 0 | 29 | 29 | 2594.8 | 2594.8
Jul | 2018-07-01 | b. HE3-6 | 3 | RRS | 2486 | 2523 | 2566 | 37 | 43 | 80 | 2686.4 | 2783.87
Jul | 2018-07-01 | b. HE3-6 | 4 | RRS | 2486 | 2523 | 2566 | 37 | 43 | 80 | 2686.4 | 2783.87
Jul | 2018-07-01 | b. HE3-6 | 5 | RRS | 2486 | 2523 | 2566 | 37 | 43 | 80 | 2686.4 | 2783.87
Jul | 2018-07-01 | b. HE3-6 | 6 | RRS | 2486 | 2523 | 2566 | 37 | 43 | 80 | 2686.4 | 2783.87
Jul | 2018-07-01 | c. HE7-10 | 7 | RRS | 2409 | 2440 | 2469 | 31 | 29 | 60 | 2509.72 | 2594.8
Jul | 2018-07-01 | c. HE7-10 | 8 | RRS | 2409 | 2440 | 2469 | 31 | 29 | 60 | 2509.72 | 2594.8
Jul | 2018-07-01 | c. HE7-10 | 9 | RRS | 2409 | 2440 | 2469 | 31 | 29 | 60 | 2509.72 | 2594.8
Jul | 2018-07-01 | c. HE7-10 | 10 | RRS | 2409 | 2440 | 2469 | 31 | 29 | 60 | 2509.72 | 2594.8
Jul | 2018-07-01 | d. HE11-14 | 11 | RRS | 2300 | 2300 | 2300 | 0 | 0 | 0 | 2300 | 2300
Jul | 2018-07-01 | d. HE11-14 | 12 | RRS | 2300 | 2300 | 2300 | 0 | 0 | 0 | 2300 | 2300
Jul | 2018-07-01 | d. HE11-14 | 13 | RRS | 2300 | 2300 | 2300 | 0 | 0 | 0 | 2300 | 2300
Jul | 2018-07-01 | d. HE11-14 | 14 | RRS | 2300 | 2300 | 2300 | 0 | 0 | 0 | 2300 | 2300
Jul | 2018-07-01 | e. HE15-18 | 15 | RRS | 2300 | 2300 | 2300 | 0 | 0 | 0 | 2300 | 2300
Jul | 2018-07-01 | e. HE15-18 | 16 | RRS | 2300 | 2300 | 2300 | 0 | 0 | 0 | 2300 | 2300
Jul | 2018-07-01 | e. HE15-18 | 17 | RRS | 2300 | 2300 | 2300 | 0 | 0 | 0 | 2300 | 2300
Jul | 2018-07-01 | e. HE15-18 | 18 | RRS | 2300 | 2300 | 2300 | 0 | 0 | 0 | 2300 | 2300
Jul | 2018-07-01 | f. HE19-22 | 19 | RRS | 2300 | 2300 | 2300 | 0 | 0 | 0 | 2300 | 2300
Jul | 2018-07-01 | f. HE19-22 | 20 | RRS | 2300 | 2300 | 2300 | 0 | 0 | 0 | 2300 | 2300
Jul | 2018-07-01 | f. HE19-22 | 21 | RRS | 2300 | 2300 | 2300 | 0 | 0 | 0 | 2300 | 2300
Jul | 2018-07-01 | f. HE19-22 | 22 | RRS | 2300 | 2300 | 2300 | 0 | 0 | 0 | 2300 | 2300
Jul | 2018-07-01 | a. HE1-2 & HE23-24 | 23 | RRS | 2440 | 2440 | 2469 | 0 | 29 | 29 | 2594.8 | 2594.8
Jul | 2018-07-01 | a. HE1-2 & HE23-24 | 24 | RRS | 2440 | 2440 | 2469 | 0 | 29 | 29 | 2594.8 | 2594.8
Aug | 2018-08-01 | a. HE1-2 & HE23-24 | 1 | RRS | 2409 | 2409 | 2429 | 0 | 20 | 20 | 2509.72 | 2509.72
Aug | 2018-08-01 | a. HE1-2 & HE23-24 | 2 | RRS | 2409 | 2409 | 2429 | 0 | 20 | 20 | 2509.72 | 2509.72
Aug | 2018-08-01 | b. HE3-6 | 3 | RRS | 2440 | 2440 | 2469 | 0 | 29 | 29 | 2594.8 | 2594.8
Aug | 2018-08-01 | b. HE3-6 | 4 | RRS | 2440 | 2440 | 2469 | 0 | 29 | 29 | 2594.8 | 2594.8
Aug | 2018-08-01 | b. HE3-6 | 5 | RRS | 2440 | 2440 | 2469 | 0 | 29 | 29 | 2594.8 | 2594.8
Aug | 2018-08-01 | b. HE3-6 | 6 | RRS | 2440 | 2440 | 2469 | 0 | 29 | 29 | 2594.8 | 2594.8
Aug | 2018-08-01 | c. HE7-10 | 7 | RRS | 2372 | 2372 | 2383 | 0 | 11 | 11 | 2420.88 | 2420.88
Aug | 2018-08-01 | c. HE7-10 | 8 | RRS | 2372 | 2372 | 2383 | 0 | 11 | 11 | 2420.88 | 2420.88
Aug | 2018-08-01 | c. HE7-10 | 9 | RRS | 2372 | 2372 | 2383 | 0 | 11 | 11 | 2420.88 | 2420.88
Aug | 2018-08-01 | c. HE7-10 | 10 | RRS | 2372 | 2372 | 2383 | 0 | 11 | 11 | 2420.88 | 2420.88
Aug | 2018-08-01 | d. HE11-14 | 11 | RRS | 2300 | 2300 | 2300 | 0 | 0 | 0 | 2300 | 2300
Aug | 2018-08-01 | d. HE11-14 | 12 | RRS | 2300 | 2300 | 2300 | 0 | 0 | 0 | 2300 | 2300
Aug | 2018-08-01 | d. HE11-14 | 13 | RRS | 2300 | 2300 | 2300 | 0 | 0 | 0 | 2300 | 2300
Aug | 2018-08-01 | d. HE11-14 | 14 | RRS | 2300 | 2300 | 2300 | 0 | 0 | 0 | 2300 | 2300
Aug | 2018-08-01 | e. HE15-18 | 15 | RRS | 2300 | 2300 | 2300 | 0 | 0 | 0 | 2300 | 2300
Aug | 2018-08-01 | e. HE15-18 | 16 | RRS | 2300 | 2300 | 2300 | 0 | 0 | 0 | 2300 | 2300
Aug | 2018-08-01 | e. HE15-18 | 17 | RRS | 2300 | 2300 | 2300 | 0 | 0 | 0 | 2300 | 2300
Aug | 2018-08-01 | e. HE15-18 | 18 | RRS | 2300 | 2300 | 2300 | 0 | 0 | 0 | 2300 | 2300
Aug | 2018-08-01 | f. HE19-22 | 19 | RRS | 2300 | 2300 | 2300 | 0 | 0 | 0 | 2300 | 2300
Aug | 2018-08-01 | f. HE19-22 | 20 | RRS | 2300 | 2300 | 2300 | 0 | 0 | 0 | 2300 | 2300
Aug | 2018-08-01 | f. HE19-22 | 21 | RRS | 2300 | 2300 | 2300 | 0 | 0 | 0 | 2300 | 2300
Aug | 2018-08-01 | f. HE19-22 | 22 | RRS | 2300 | 2300 | 2300 | 0 | 0 | 0 | 2300 | 2300
Aug | 2018-08-01 | a. HE1-2 & HE23-24 | 23 | RRS | 2409 | 2409 | 2429 | 0 | 20 | 20 | 2509.72 | 2509.72
Aug | 2018-08-01 | a. HE1-2 & HE23-24 | 24 | RRS | 2409 | 2409 | 2429 | 0 | 20 | 20 | 2509.72 | 2509.72
Sep | 2018-09-01 | a. HE1-2 & HE23-24 | 1 | RRS | 2553 | 2553 | 2605 | 0 | 52 | 52 | 2889.72 | 2889.72
Sep | 2018-09-01 | a. HE1-2 & HE23-24 | 2 | RRS | 2553 | 2553 | 2605 | 0 | 52 | 52 | 2889.72 | 2889.72
Sep | 2018-09-01 | b. HE3-6 | 3 | RRS | 2553 | 2645 | 2712 | 92 | 67 | 159 | 2889.72 | 3138.35
Sep | 2018-09-01 | b. HE3-6 | 4 | RRS | 2553 | 2645 | 2712 | 92 | 67 | 159 | 2889.72 | 3138.35
Sep | 2018-09-01 | b. HE3-6 | 5 | RRS | 2553 | 2645 | 2712 | 92 | 67 | 159 | 2889.72 | 3138.35
Sep | 2018-09-01 | b. HE3-6 | 6 | RRS | 2553 | 2645 | 2712 | 92 | 67 | 159 | 2889.72 | 3138.35
Sep | 2018-09-01 | c. HE7-10 | 7 | RRS | 2523 | 2553 | 2605 | 30 | 52 | 82 | 2783.87 | 2889.72
Sep | 2018-09-01 | c. HE7-10 | 8 | RRS | 2523 | 2553 | 2605 | 30 | 52 | 82 | 2783.87 | 2889.72
Sep | 2018-09-01 | c. HE7-10 | 9 | RRS | 2523 | 2553 | 2605 | 30 | 52 | 82 | 2783.87 | 2889.72
Sep | 2018-09-01 | c. HE7-10 | 10 | RRS | 2523 | 2553 | 2605 | 30 | 52 | 82 | 2783.87 | 2889.72
Sep | 2018-09-01 | d. HE11-14 | 11 | RRS | 2409 | 2440 | 2469 | 31 | 29 | 60 | 2509.72 | 2594.8
Sep | 2018-09-01 | d. HE11-14 | 12 | RRS | 2409 | 2440 | 2469 | 31 | 29 | 60 | 2509.72 | 2594.8
Sep | 2018-09-01 | d. HE11-14 | 13 | RRS | 2409 | 2440 | 2469 | 31 | 29 | 60 | 2509.72 | 2594.8
Sep | 2018-09-01 | d. HE11-14 | 14 | RRS | 2409 | 2440 | 2469 | 31 | 29 | 60 | 2509.72 | 2594.8
Sep | 2018-09-01 | e. HE15-18 | 15 | RRS | 2372 | 2372 | 2383 | 0 | 11 | 11 | 2420.88 | 2420.88
Sep | 2018-09-01 | e. HE15-18 | 16 | RRS | 2372 | 2372 | 2383 | 0 | 11 | 11 | 2420.88 | 2420.88
Sep | 2018-09-01 | e. HE15-18 | 17 | RRS | 2372 | 2372 | 2383 | 0 | 11 | 11 | 2420.88 | 2420.88
Sep | 2018-09-01 | e. HE15-18 | 18 | RRS | 2372 | 2372 | 2383 | 0 | 11 | 11 | 2420.88 | 2420.88
Sep | 2018-09-01 | f. HE19-22 | 19 | RRS | 2409 | 2440 | 2469 | 31 | 29 | 60 | 2509.72 | 2594.8
Sep | 2018-09-01 | f. HE19-22 | 20 | RRS | 2409 | 2440 | 2469 | 31 | 29 | 60 | 2509.72 | 2594.8
Sep | 2018-09-01 | f. HE19-22 | 21 | RRS | 2409 | 2440 | 2469 | 31 | 29 | 60 | 2509.72 | 2594.8
Sep | 2018-09-01 | f. HE19-22 | 22 | RRS | 2409 | 2440 | 2469 | 31 | 29 | 60 | 2509.72 | 2594.8
Sep | 2018-09-01 | a. HE1-2 & HE23-24 | 23 | RRS | 2553 | 2553 | 2605 | 0 | 52 | 52 | 2889.72 | 2889.72
Sep | 2018-09-01 | a. HE1-2 & HE23-24 | 24 | RRS | 2553 | 2553 | 2605 | 0 | 52 | 52 | 2889.72 | 2889.72
Oct | 2018-10-01 | a. HE1-2 & HE23-24 | 1 | RRS | 2908 | 0 | 0 | 2908 | 0 | -2908 | 3920.1 | 0
Oct | 2018-10-01 | a. HE1-2 & HE23-24 | 2 | RRS | 2908 | 0 | 0 | 2908 | 0 | -2908 | 3920.1 | 0
Oct | 2018-10-01 | b. HE3-6 | 3 | RRS | 2959 | 0 | 0 | 2959 | 0 | -2959 | 4112.75 | 0
Oct | 2018-10-01 | b. HE3-6 | 4 | RRS | 2959 | 0 | 0 | 2959 | 0 | -2959 | 4112.75 | 0
Oct | 2018-10-01 | b. HE3-6 | 5 | RRS | 2959 | 0 | 0 | 2959 | 0 | -2959 | 4112.75 | 0
Oct | 2018-10-01 | b. HE3-6 | 6 | RRS | 2959 | 0 | 0 | 2959 | 0 | -2959 | 4112.75 | 0
Oct | 2018-10-01 | c. HE7-10 | 7 | RRS | 2868 | 0 | 0 | 2868 | 0 | -2868 | 3744.18 | 0
Oct | 2018-10-01 | c. HE7-10 | 8 | RRS | 2868 | 0 | 0 | 2868 | 0 | -2868 | 3744.18 | 0
Oct | 2018-10-01 | c. HE7-10 | 9 | RRS | 2868 | 0 | 0 | 2868 | 0 | -2868 | 3744.18 | 0
Oct | 2018-10-01 | c. HE7-10 | 10 | RRS | 2868 | 0 | 0 | 2868 | 0 | -2868 | 3744.18 | 0
Oct | 2018-10-01 | d. HE11-14 | 11 | RRS | 2707 | 0 | 0 | 2707 | 0 | -2707 | 3314.23 | 0
Oct | 2018-10-01 | d. HE11-14 | 12 | RRS | 2707 | 0 | 0 | 2707 | 0 | -2707 | 3314.23 | 0
Oct | 2018-10-01 | d. HE11-14 | 13 | RRS | 2707 | 0 | 0 | 2707 | 0 | -2707 | 3314.23 | 0
Oct | 2018-10-01 | d. HE11-14 | 14 | RRS | 2707 | 0 | 0 | 2707 | 0 | -2707 | 3314.23 | 0
Oct | 2018-10-01 | e. HE15-18 | 15 | RRS | 2645 | 0 | 0 | 2645 | 0 | -2645 | 3138.35 | 0
Oct | 2018-10-01 | e. HE15-18 | 16 | RRS | 2645 | 0 | 0 | 2645 | 0 | -2645 | 3138.35 | 0
Oct | 2018-10-01 | e. HE15-18 | 17 | RRS | 2645 | 0 | 0 | 2645 | 0 | -2645 | 3138.35 | 0
Oct | 2018-10-01 | e. HE15-18 | 18 | RRS | 2645 | 0 | 0 | 2645 | 0 | -2645 | 3138.35 | 0
Oct | 2018-10-01 | f. HE19-22 | 19 | RRS | 2707 | 0 | 0 | 2707 | 0 | -2707 | 3314.23 | 0
Oct | 2018-10-01 | f. HE19-22 | 20 | RRS | 2707 | 0 | 0 | 2707 | 0 | -2707 | 3314.23 | 0
Oct | 2018-10-01 | f. HE19-22 | 21 | RRS | 2707 | 0 | 0 | 2707 | 0 | -2707 | 3314.23 | 0
Oct | 2018-10-01 | f. HE19-22 | 22 | RRS | 2707 | 0 | 0 | 2707 | 0 | -2707 | 3314.23 | 0
Oct | 2018-10-01 | a. HE1-2 & HE23-24 | 23 | RRS | 2908 | 0 | 0 | 2908 | 0 | -2908 | 3920.1 | 0
Oct | 2018-10-01 | a. HE1-2 & HE23-24 | 24 | RRS | 2908 | 0 | 0 | 2908 | 0 | -2908 | 3920.1 | 0
Nov | 2018-11-01 | a. HE1-2 & HE23-24 | 1 | RRS | 3086 | 0 | 0 | 3086 | 0 | -3086 | 4623.16 | 0
Nov | 2018-11-01 | a. HE1-2 & HE23-24 | 2 | RRS | 3086 | 0 | 0 | 3086 | 0 | -3086 | 4623.16 | 0
Nov | 2018-11-01 | b. HE3-6 | 3 | RRS | 2998 | 0 | 0 | 2998 | 0 | -2998 | 4329.26 | 0
Nov | 2018-11-01 | b. HE3-6 | 4 | RRS | 2998 | 0 | 0 | 2998 | 0 | -2998 | 4329.26 | 0
Nov | 2018-11-01 | b. HE3-6 | 5 | RRS | 2998 | 0 | 0 | 2998 | 0 | -2998 | 4329.26 | 0
Nov | 2018-11-01 | b. HE3-6 | 6 | RRS | 2998 | 0 | 0 | 2998 | 0 | -2998 | 4329.26 | 0
Nov | 2018-11-01 | c. HE7-10 | 7 | RRS | 2908 | 0 | 0 | 2908 | 0 | -2908 | 3920.1 | 0
Nov | 2018-11-01 | c. HE7-10 | 8 | RRS | 2908 | 0 | 0 | 2908 | 0 | -2908 | 3920.1 | 0
Nov | 2018-11-01 | c. HE7-10 | 9 | RRS | 2908 | 0 | 0 | 2908 | 0 | -2908 | 3920.1 | 0
Nov | 2018-11-01 | c. HE7-10 | 10 | RRS | 2908 | 0 | 0 | 2908 | 0 | -2908 | 3920.1 | 0
Nov | 2018-11-01 | d. HE11-14 | 11 | RRS | 2868 | 0 | 0 | 2868 | 0 | -2868 | 3744.18 | 0
Nov | 2018-11-01 | d. HE11-14 | 12 | RRS | 2868 | 0 | 0 | 2868 | 0 | -2868 | 3744.18 | 0
Nov | 2018-11-01 | d. HE11-14 | 13 | RRS | 2868 | 0 | 0 | 2868 | 0 | -2868 | 3744.18 | 0
Nov | 2018-11-01 | d. HE11-14 | 14 | RRS | 2868 | 0 | 0 | 2868 | 0 | -2868 | 3744.18 | 0
Nov | 2018-11-01 | e. HE15-18 | 15 | RRS | 2868 | 0 | 0 | 2868 | 0 | -2868 | 3744.18 | 0
Nov | 2018-11-01 | e. HE15-18 | 16 | RRS | 2868 | 0 | 0 | 2868 | 0 | -2868 | 3744.18 | 0
Nov | 2018-11-01 | e. HE15-18 | 17 | RRS | 2868 | 0 | 0 | 2868 | 0 | -2868 | 3744.18 | 0
Nov | 2018-11-01 | e. HE15-18 | 18 | RRS | 2868 | 0 | 0 | 2868 | 0 | -2868 | 3744.18 | 0
Nov | 2018-11-01 | f. HE19-22 | 19 | RRS | 2908 | 0 | 0 | 2908 | 0 | -2908 | 3920.1 | 0
Nov | 2018-11-01 | f. HE19-22 | 20 | RRS | 2908 | 0 | 0 | 2908 | 0 | -2908 | 3920.1 | 0
Nov | 2018-11-01 | f. HE19-22 | 21 | RRS | 2908 | 0 | 0 | 2908 | 0 | -2908 | 3920.1 | 0
Nov | 2018-11-01 | f. HE19-22 | 22 | RRS | 2908 | 0 | 0 | 2908 | 0 | -2908 | 3920.1 | 0
Nov | 2018-11-01 | a. HE1-2 & HE23-24 | 23 | RRS | 3086 | 0 | 0 | 3086 | 0 | -3086 | 4623.16 | 0
Dec | 2018-12-01 | a. HE1-2 & HE23-24 | 24 | RRS | 3086 | 0 | 0 | 3086 | 0 | -3086 | 4623.16 | 0
Dec | 2018-12-01 | a. HE1-2 & HE23-24 | 1 | RRS | 2998 | 0 | 0 | 2998 | 0 | -2998 | 4329.26 | 0
Dec | 2018-12-01 | a. HE1-2 & HE23-24 | 2 | RRS | 2998 | 0 | 0 | 2998 | 0 | -2998 | 4329.26 | 0
Dec | 2018-12-01 | b. HE3-6 | 3 | RRS | 2959 | 0 | 0 | 2959 | 0 | -2959 | 4112.75 | 0
Dec | 2018-12-01 | b. HE3-6 | 4 | RRS | 2959 | 0 | 0 | 2959 | 0 | -2959 | 4112.75 | 0
Dec | 2018-12-01 | b. HE3-6 | 5 | RRS | 2959 | 0 | 0 | 2959 | 0 | -2959 | 4112.75 | 0
Dec | 2018-12-01 | b. HE3-6 | 6 | RRS | 2959 | 0 | 0 | 2959 | 0 | -2959 | 4112.75 | 0
Dec | 2018-12-01 | c. HE7-10 | 7 | RRS | 2868 | 0 | 0 | 2868 | 0 | -2868 | 3744.18 | 0
Dec | 2018-12-01 | c. HE7-10 | 8 | RRS | 2868 | 0 | 0 | 2868 | 0 | -2868 | 3744.18 | 0
Dec | 2018-12-01 | c. HE7-10 | 9 | RRS | 2868 | 0 | 0 | 2868 | 0 | -2868 | 3744.18 | 0
Dec | 2018-12-01 | c. HE7-10 | 10 | RRS | 2868 | 0 | 0 | 2868 | 0 | -2868 | 3744.18 | 0
Dec | 2018-12-01 | d. HE11-14 | 11 | RRS | 2797 | 0 | 0 | 2797 | 0 | -2797 | 3521.68 | 0
Dec | 2018-12-01 | d. HE11-14 | 12 | RRS | 2797 | 0 | 0 | 2797 | 0 | -2797 | 3521.68 | 0
Dec | 2018-12-01 | d. HE11-14 | 13 | RRS | 2797 | 0 | 0 | 2797 | 0 | -2797 | 3521.68 | 0
Dec | 2018-12-01 | d. HE11-14 | 14 | RRS | 2797 | 0 | 0 | 2797 | 0 | -2797 | 3521.68 | 0
Dec | 2018-12-01 | e. HE15-18 | 15 | RRS | 2797 | 0 | 0 | 2797 | 0 | -2797 | 3521.68 | 0
Dec | 2018-12-01 | e. HE15-18 | 16 | RRS | 2797 | 0 | 0 | 2797 | 0 | -2797 | 3521.68 | 0
Dec | 2018-12-01 | e. HE15-18 | 17 | RRS | 2797 | 0 | 0 | 2797 | 0 | -2797 | 3521.68 | 0
Dec | 2018-12-01 | e. HE15-18 | 18 | RRS | 2797 | 0 | 0 | 2797 | 0 | -2797 | 3521.68 | 0
Dec | 2018-12-01 | f. HE19-22 | 19 | RRS | 2868 | 0 | 0 | 2868 | 0 | -2868 | 3744.18 | 0
Dec | 2018-12-01 | f. HE19-22 | 20 | RRS | 2868 | 0 | 0 | 2868 | 0 | -2868 | 3744.18 | 0
Dec | 2018-12-01 | f. HE19-22 | 21 | RRS | 2868 | 0 | 0 | 2868 | 0 | -2868 | 3744.18 | 0
Dec | 2018-12-01 | f. HE19-22 | 22 | RRS | 2868 | 0 | 0 | 2868 | 0 | -2868 | 3744.18 | 0
Dec | 2018-12-01 | a. HE1-2 & HE23-24 | 23 | RRS | 2998 | 0 | 0 | 2998 | 0 | -2998 | 4329.26 | 0
Dec | 2018-12-01 | a. HE1-2 & HE23-24 | 24 | RRS | 2998 | 0 | 0 | 2998 | 0 | -2998 | 4329.26 | 0