## Slide 1
PDCWG Report to ROS
Chair: Chad Mulholland, NRG
Vice Chair: Jimmy Jackson, CPS
ROS
November 5th, 2020

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
  BAL-001-TRE-2 FMEs & IMFR
    1 FME in the month of August
    1 FME in the month of September
  Frequency Control Report

## Slide 3: Meeting Minutes
PDCWG Meeting 10/14/2020
  Southern Cross DC Tie – Directives 3 and 9
  Draft Revision: ODBRR25 Procedure for Calculating RRS Limits for Units
  Follow up – ERCOT 2020/2021 Ancillary Service Methodology & Analysis
  NPRR 1040 – Compliance Metrics for Ancillary Service Supply Responsibility
  ERCOT Reports and FME Discussion

## Slide 4: Frequency Measurable Events Performance

## Slide 5: Frequency Measurable Events
There was 1 FME in August and 1 FME in September
  8/22/2020 23:46:53
    Loss of 664 MW
    Interconnection Frequency Response: 1383 MW/0.1 Hz
    10 of 58 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    10 of 58 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.
  9/19/2020 16:02:03
    Loss of 493 MW
    Interconnection Frequency Response: 978 MW/0.1 Hz
    5 of 33 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    6 of 33 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 6: Interconnection Minimum Frequency Response (IMFR) Performance
IMFR Performance currently 1120.41 MW/0.1Hz
Frequency Response Obligation (FRO): 425 MW/0.1 Hz

## Slide 7: Frequency Control Report
September 2020

## Slide 8: CPS1 Performance

## Slide 9: RMS1 Performance of ERCOT Frequency

## Slide 10: Frequency Profile Analysis

## Slide 11: Time Error Corrections

## Slide 12: ERCOT Total Energy
Notes: 32,735,862 MWh

## Slide 13: ERCOT Total Energy from Wind Generation
Notes: 5,026,960 MWh

## Slide 14: ERCOT % Energy from Wind Generation
Notes: 15.36%

## Slide 15: ERCOT Total Energy from Solar Generation
Notes: 782,376 MWh

## Slide 16: ERCOT % Energy from Solar Generation
Notes: 2.39%

## Slide 17
Questions?