## Summary
Release Date: November 5, 2020
PRELIMINARY
Seasonal Assessment of Resource Adequacy for the ERCOT Region (SARA)
Spring 2021
SUMMARY
The ERCOT region is expected to have sufficient installed generating capacity to serve forecasted peak demands in the upcoming spring season, March – May 2021.
The peak demand forecast for spring 2021 was developed using Moody’s economic data obtained in April 2020. Based on expected spring peak weather conditions, the preliminary spring SARA anticipates a seasonal peak demand of 64,548 MW.
This is this first spring assessment that includes a low wind output scenario, and even under this particular scenario, ERCOT anticipates there will be sufficient generation to meet the forecasted demand.
Based on ERCOT’s preliminary assessment, an additional 4,262 MW of planned resource capacity comprised of gas-fired units, wind and utility-scale solar is expected to be available to meet the spring peak demand.
The report also includes a forecast of 12,124 MW of unit outages based on historical outage data from the past three spring seasons (starting with 2018), and assumes the high likelihood that the spring peak demand will occur in May.
The final spring SARA report will be released in early March 2021.

## Scenarios
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Spring 2020 - Preliminary
Release Date: November 5, 2020
Forecasted Capacity and Demand
|  | Operational Resources (thermal and hydro), MW | 65564.7353 | Based on current Seasonal Maximum Sustainable Limits reported through the unit registration process
|  | Switchable Capacity Total, MW | 3691 | Installed capacity of units that can interconnect with other Regions and are available to ERCOT
|  | Less Switchable Capacity Unavailable to ERCOT, MW | -558 | Based on survey responses of Switchable Resource owners
|  | Available Mothballed Capacity, MW | 0 | Based on seasonal Mothball units plus Probability of Return responses of Mothball Resource owners
|  | Capacity from Private Use Networks, MW | 2799 | Average grid injection during the top 20 spring peak load hours over the last three years, plus the forecasted net change in generation capacity available to the ERCOT grid pursuant to Nodal Protocol Section 10.3.2.4.
|  | Coastal Wind, Peak Average Capacity Contribution, MW | 2202.624 | Based on 64% of installed capacity for coastal wind resources (spring season) per ERCOT Nodal Protocols Section 3.2.6.2.2
|  | Panhandle Wind, Peak Average Capacity Contribution, MW | 1543.045 | Based on 35% of installed capacity for panhandle wind resources (spring season) per ERCOT Nodal Protocols Section 3.2.6.2.2
|  | Other Wind, Peak Average Capacity Contribution, MW | 5818.114 | Based on 34% of installed capacity for other wind resources (spring season) per ERCOT Nodal Protocols Section 3.2.6.2.2
|  | Solar Utility-Scale, Peak Average Capacity Contribution, MW | 2493.985 | Based on 65% of rated capacity for solar resources (spring season) per Nodal Protocols Section 3.2.6.2.2
|  | Storage, Peak Average Capacity Contribution, MW | 0 | Based on 0% of rated capacity (spring season); resources assumed to provide regulation reserves rather than sustained capacity available to meet peak loads
|  | RMR Capacity to be under Contract | 0
|  | Capacity Pending Retirement, MW | 0 | Announced retired capacity that is undergoing ERCOT grid reliability reviews pursuant to Nodal Protocol Section 3.14.1.2
|  | Non-Synchronous Ties, Capacity Contribution, MW | 837.53 | Based on import flows during most recent Energy Emergency Alert (EEA) intervals for the spring season (Used as a proxy for the spring season due to lack of EEA intervals.)
|  | Planned Thermal Resources with Signed IA, Air Permits and Water Rights, MW | 306 | Based on in-service dates provided by developers
|  | Planned Coastal Wind with Signed IA, Peak Average Capacity Contribution, MW | 809.152 | Based on in-service dates provided by developers and 64% spring capacity contribution for coastal wind resources
|  | Planned Panhandle Wind with Signed IA, Peak Average Capacity Contribution, MW | 0 | Based on in-service dates provided by developers and 35% spring capacity contribution for panhandle wind resources
|  | Planned Other Wind with Signed IA, Peak Average Capacity Contribution, MW | 1633.598 | Based on in-service dates provided by developers and 34% spring capacity contribution for other wind resources
|  | Planned Solar Utility-Scale, Peak Average Capacity Contribution, MW | 1513.395 | Based on in-service dates provided by developers and 65% spring capacity contribution for solar resources
|  | Planned Storage, Peak Average Capacity Contribution, MW | 0 | Based on in-service dates provided by developers and 0% spring capacity contribution for storage resources
| [a] Total Resources, MW |  | 88654.1783
| [b] Peak Demand, MW |  | 64548 | Based on average weather conditions at the time of the May peak demand from 2004 – 2018, and updated to reflect a revised economic growth forecast prepared in April 2020
| [c] Reserve Capacity [a - b], MW |  | 24106.1783
Range of Potential Risks
|  |  | Forecasted Season Peak Load (May) | Forecasted April Peak Load and Typical Generation Outages During Peak Maintenance Season (March-April) | Forecasted Season Peak Load / Extreme Low Wind Output | Extreme April Peak Load and Typical Generation Outages During Peak Maintenance Season (March-April)
|  | Seasonal Load Adjustment | 0 | -9726 | 0 | -4111 | Based on a revised economic growth forecast prepared in April 2020; the April peak forecast is 54,822 MW, and the extreme April peak forecast is 60,437 MW; adjustments reflect April peak forecast for average and 90th percentile weather conditions, respectively
|  | Typical May Maintenance Outages, Thermal | 6386.8333 | 6386.8333 | 6386.8333 | 6386.8333 | Based on historical average of planned maintenance outages for May weekdays (starting in 2018)
|  | Typical May Forced Outages, Thermal | 5736.704 | 5736.704 | 5736.704 | 5736.704 | Based on historical average of forced outages for May weekdays (starting in 2018)
|  | Incremental Unit Outages to Reflect April Peak Maintenance Season, Thermal | 0 | 9021.9217 | 0 | 9021.9217 | Incremental outages based on historical average of forced and planned maintenance outages for April weekdays, hours ending 3 pm - 8 pm (starting in 2018)
|  | Low Wind Output Adjustment | 0 | 0 | 9480.533 | 0 | Based on the 5th percentile of hourly wind capacity factors (output as a percentage of installed capacity) associated with the 100 highest Net Load hours (Load minus wind output) for the 2017-2020 spring Peak Load seasons; this low wind output level is 2,526 MW
| [d] Total Uses of Reserve Capacity |  | 12123.5373 | 11419.459 | 21604.0703 | 17034.459
| [e] Capacity Available for Operating Reserves, Normal Operating Conditions (c-d), MW |  | 11982.641 | 12686.7194 | 2502.108 | 7071.7194 | See the Background tab for additional details
Less than 2,300 MW indicates risk of EEA1

## SpringCapacities
Unit Capacities - Spring
| UNIT NAME | GENERATION INTERCONNECTION PROJECT CODE | UNIT CODE | COUNTY | FUEL | CDR ZONE | START YEAR | CAPACITY (MW)
Operational Resources (Thermal)
4 | COMANCHE PEAK U1 |  | CPSES_UNIT1 | SOMERVELL | NUCLEAR | NORTH | 1990 | 1227
5 | COMANCHE PEAK U2 |  | CPSES_UNIT2 | SOMERVELL | NUCLEAR | NORTH | 1993 | 1214
6 | SOUTH TEXAS U1 | 20INR0287 | STP_STP_G1 | MATAGORDA | NUCLEAR | COASTAL | 1988 | 1323.2
7 | SOUTH TEXAS U2 |  | STP_STP_G2 | MATAGORDA | NUCLEAR | COASTAL | 1989 | 1310
8 | COLETO CREEK |  | COLETO_COLETOG1 | GOLIAD | COAL | SOUTH | 1980 | 655
9 | FAYETTE POWER U1 |  | FPPYD1_FPP_G1 | FAYETTE | COAL | SOUTH | 1979 | 608
10 | FAYETTE POWER U2 |  | FPPYD1_FPP_G2 | FAYETTE | COAL | SOUTH | 1980 | 608
11 | FAYETTE POWER U3 |  | FPPYD2_FPP_G3 | FAYETTE | COAL | SOUTH | 1988 | 448
12 | J K SPRUCE U1 |  | CALAVERS_JKS1 | BEXAR | COAL | SOUTH | 1992 | 560
13 | J K SPRUCE U2 |  | CALAVERS_JKS2 | BEXAR | COAL | SOUTH | 2010 | 785
14 | LIMESTONE U1 |  | LEG_LEG_G1 | LIMESTONE | COAL | NORTH | 1985 | 824
15 | LIMESTONE U2 |  | LEG_LEG_G2 | LIMESTONE | COAL | NORTH | 1986 | 836
16 | MARTIN LAKE U1 |  | MLSES_UNIT1 | RUSK | COAL | NORTH | 1977 | 815
17 | MARTIN LAKE U2 |  | MLSES_UNIT2 | RUSK | COAL | NORTH | 1978 | 820
18 | MARTIN LAKE U3 |  | MLSES_UNIT3 | RUSK | COAL | NORTH | 1979 | 820
19 | OAK GROVE SES U1 |  | OGSES_UNIT1A | ROBERTSON | COAL | NORTH | 2010 | 855
20 | OAK GROVE SES U2 |  | OGSES_UNIT2 | ROBERTSON | COAL | NORTH | 2011 | 855
21 | SAN MIGUEL U1 |  | SANMIGL_G1 | ATASCOSA | COAL | SOUTH | 1982 | 391
22 | SANDY CREEK U1 |  | SCES_UNIT1 | MCLENNAN | COAL | NORTH | 2013 | 932.6
23 | TWIN OAKS U1 |  | TNP_ONE_TNP_O_1 | ROBERTSON | COAL | NORTH | 1990 | 155
24 | TWIN OAKS U2 |  | TNP_ONE_TNP_O_2 | ROBERTSON | COAL | NORTH | 1991 | 155
25 | W A PARISH U5 |  | WAP_WAP_G5 | FORT BEND | COAL | HOUSTON | 1977 | 664
26 | W A PARISH U6 |  | WAP_WAP_G6 | FORT BEND | COAL | HOUSTON | 1978 | 663
27 | W A PARISH U7 |  | WAP_WAP_G7 | FORT BEND | COAL | HOUSTON | 1980 | 577
28 | W A PARISH U8 |  | WAP_WAP_G8 | FORT BEND | COAL | HOUSTON | 1982 | 610
29 | ARTHUR VON ROSENBERG 1 CTG 1 |  | BRAUNIG_AVR1_CT1 | BEXAR | GAS-CC | SOUTH | 2000 | 164
30 | ARTHUR VON ROSENBERG 1 CTG 2 |  | BRAUNIG_AVR1_CT2 | BEXAR | GAS-CC | SOUTH | 2000 | 164
31 | ARTHUR VON ROSENBERG 1 STG |  | BRAUNIG_AVR1_ST | BEXAR | GAS-CC | SOUTH | 2000 | 190
32 | ATKINS CTG 7 |  | ATKINS_ATKINSG7 | BRAZOS | GAS-GT | NORTH | 1973 | 19
33 | BARNEY M DAVIS CTG 3 | 20INR0312 | B_DAVIS_B_DAVIG3 | NUECES | GAS-CC | COASTAL | 2010 | 161
34 | BARNEY M DAVIS CTG 4 | 20INR0312 | B_DAVIS_B_DAVIG4 | NUECES | GAS-CC | COASTAL | 2010 | 161
35 | BARNEY M DAVIS STG 1 | 20INR0312 | B_DAVIS_B_DAVIG1 | NUECES | GAS-ST | COASTAL | 1974 | 330
36 | BARNEY M DAVIS STG 2 | 20INR0312 | B_DAVIS_B_DAVIG2 | NUECES | GAS-CC | COASTAL | 1976 | 322
37 | BASTROP ENERGY CENTER CTG 1 |  | BASTEN_GTG1100 | BASTROP | GAS-CC | SOUTH | 2002 | 157
38 | BASTROP ENERGY CENTER CTG 2 |  | BASTEN_GTG2100 | BASTROP | GAS-CC | SOUTH | 2002 | 157
39 | BASTROP ENERGY CENTER STG |  | BASTEN_ST0100 | BASTROP | GAS-CC | SOUTH | 2002 | 236
40 | BOSQUE ENERGY CENTER CTG 1 |  | BOSQUESW_BSQSU_1 | BOSQUE | GAS-CC | NORTH | 2000 | 161.8
41 | BOSQUE ENERGY CENTER CTG 2 |  | BOSQUESW_BSQSU_2 | BOSQUE | GAS-CC | NORTH | 2000 | 161.8
42 | BOSQUE ENERGY CENTER CTG 3 |  | BOSQUESW_BSQSU_3 | BOSQUE | GAS-CC | NORTH | 2001 | 160.6
43 | BOSQUE ENERGY CENTER STG 4 |  | BOSQUESW_BSQSU_4 | BOSQUE | GAS-CC | NORTH | 2001 | 83.6
44 | BOSQUE ENERGY CENTER STG 5 |  | BOSQUESW_BSQSU_5 | BOSQUE | GAS-CC | NORTH | 2009 | 222.4
45 | BRAZOS VALLEY CTG 1 |  | BVE_UNIT1 | FORT BEND | GAS-CC | HOUSTON | 2003 | 169
46 | BRAZOS VALLEY CTG 2 |  | BVE_UNIT2 | FORT BEND | GAS-CC | HOUSTON | 2003 | 169
47 | BRAZOS VALLEY STG 3 |  | BVE_UNIT3 | FORT BEND | GAS-CC | HOUSTON | 2003 | 270
48 | CALENERGY-FALCON SEABOARD CTG 1 |  | FLCNS_UNIT1 | HOWARD | GAS-CC | WEST | 1987 | 77
49 | CALENERGY-FALCON SEABOARD CTG 2 |  | FLCNS_UNIT2 | HOWARD | GAS-CC | WEST | 1987 | 77
50 | CALENERGY-FALCON SEABOARD STG 3 |  | FLCNS_UNIT3 | HOWARD | GAS-CC | WEST | 1988 | 71
51 | CALHOUN (PORT COMFORT) CTG 1 |  | CALHOUN_UNIT1 | CALHOUN | GAS-GT | COASTAL | 2017 | 46.7
52 | CALHOUN (PORT COMFORT) CTG 2 |  | CALHOUN_UNIT2 | CALHOUN | GAS-GT | COASTAL | 2017 | 46.7
53 | CASTLEMAN CHAMON CTG 1 |  | CHAMON_CTG_0101 | HARRIS | GAS-GT | HOUSTON | 2017 | 46.7
54 | CASTLEMAN CHAMON CTG 2 |  | CHAMON_CTG_0301 | HARRIS | GAS-GT | HOUSTON | 2017 | 46.7
55 | CEDAR BAYOU 4 CTG 1 |  | CBY4_CT41 | CHAMBERS | GAS-CC | HOUSTON | 2009 | 168
56 | CEDAR BAYOU 4 CTG 2 |  | CBY4_CT42 | CHAMBERS | GAS-CC | HOUSTON | 2009 | 168
57 | CEDAR BAYOU 4 STG |  | CBY4_ST04 | CHAMBERS | GAS-CC | HOUSTON | 2009 | 182
58 | CEDAR BAYOU STG 1 |  | CBY_CBY_G1 | CHAMBERS | GAS-ST | HOUSTON | 1970 | 745
59 | CEDAR BAYOU STG 2 |  | CBY_CBY_G2 | CHAMBERS | GAS-ST | HOUSTON | 1972 | 749
60 | COLORADO BEND ENERGY CENTER CTG 1 |  | CBEC_GT1 | WHARTON | GAS-CC | SOUTH | 2007 | 83.9
61 | COLORADO BEND ENERGY CENTER CTG 2 |  | CBEC_GT2 | WHARTON | GAS-CC | SOUTH | 2007 | 76.9
62 | COLORADO BEND ENERGY CENTER CTG 3 |  | CBEC_GT3 | WHARTON | GAS-CC | SOUTH | 2008 | 82.9
63 | COLORADO BEND ENERGY CENTER CTG 4 |  | CBEC_GT4 | WHARTON | GAS-CC | SOUTH | 2008 | 77.9
64 | COLORADO BEND ENERGY CENTER STG 1 |  | CBEC_STG1 | WHARTON | GAS-CC | SOUTH | 2007 | 103
65 | COLORADO BEND ENERGY CENTER STG 2 |  | CBEC_STG2 | WHARTON | GAS-CC | SOUTH | 2008 | 107
66 | COLORADO BEND II CTG 7 | 18INR0077 | CBECII_CT7 | WHARTON | GAS-CC | SOUTH | 2017 | 332.1
67 | COLORADO BEND II CTG 8 | 18INR0077 | CBECII_CT8 | WHARTON | GAS-CC | SOUTH | 2017 | 337.8
68 | COLORADO BEND II STG 9 | 18INR0077 | CBECII_STG9 | WHARTON | GAS-CC | SOUTH | 2017 | 482.3
69 | CVC CHANNELVIEW CTG 1 |  | CVC_CVC_G1 | HARRIS | GAS-CC | HOUSTON | 2008 | 181
70 | CVC CHANNELVIEW CTG 2 |  | CVC_CVC_G2 | HARRIS | GAS-CC | HOUSTON | 2008 | 178
71 | CVC CHANNELVIEW CTG 3 |  | CVC_CVC_G3 | HARRIS | GAS-CC | HOUSTON | 2008 | 178
72 | CVC CHANNELVIEW STG 5 |  | CVC_CVC_G5 | HARRIS | GAS-CC | HOUSTON | 2008 | 144
73 | DANSBY CTG 2 |  | DANSBY_DANSBYG2 | BRAZOS | GAS-GT | NORTH | 2004 | 46.5
74 | DANSBY CTG 3 |  | DANSBY_DANSBYG3 | BRAZOS | GAS-GT | NORTH | 2010 | 48.5
75 | DANSBY STG 1 |  | DANSBY_DANSBYG1 | BRAZOS | GAS-ST | NORTH | 1978 | 108.5
76 | DECKER CREEK CTG 1 |  | DECKER_DPGT_1 | TRAVIS | GAS-GT | SOUTH | 1989 | 50
77 | DECKER CREEK CTG 2 |  | DECKER_DPGT_2 | TRAVIS | GAS-GT | SOUTH | 1989 | 50
78 | DECKER CREEK CTG 3 |  | DECKER_DPGT_3 | TRAVIS | GAS-GT | SOUTH | 1989 | 50
79 | DECKER CREEK CTG 4 |  | DECKER_DPGT_4 | TRAVIS | GAS-GT | SOUTH | 1989 | 50
80 | DECKER CREEK STG 2 |  | DECKER_DPG2 | TRAVIS | GAS-ST | SOUTH | 1978 | 428
81 | DECORDOVA CTG 1 |  | DCSES_CT10 | HOOD | GAS-GT | NORTH | 1990 | 71
82 | DECORDOVA CTG 2 |  | DCSES_CT20 | HOOD | GAS-GT | NORTH | 1990 | 70
83 | DECORDOVA CTG 3 |  | DCSES_CT30 | HOOD | GAS-GT | NORTH | 1990 | 70
84 | DECORDOVA CTG 4 |  | DCSES_CT40 | HOOD | GAS-GT | NORTH | 1990 | 71
85 | DEER PARK ENERGY CENTER CTG 1 |  | DDPEC_GT1 | HARRIS | GAS-CC | HOUSTON | 2002 | 190
86 | DEER PARK ENERGY CENTER CTG 2 |  | DDPEC_GT2 | HARRIS | GAS-CC | HOUSTON | 2002 | 202
87 | DEER PARK ENERGY CENTER CTG 3 |  | DDPEC_GT3 | HARRIS | GAS-CC | HOUSTON | 2002 | 190
88 | DEER PARK ENERGY CENTER CTG 4 |  | DDPEC_GT4 | HARRIS | GAS-CC | HOUSTON | 2002 | 202
89 | DEER PARK ENERGY CENTER CTG 6 |  | DDPEC_GT6 | HARRIS | GAS-CC | HOUSTON | 2014 | 174
90 | DEER PARK ENERGY CENTER STG 1 |  | DDPEC_ST1 | HARRIS | GAS-CC | HOUSTON | 2002 | 290
91 | DENTON ENERGY CENTER IC A |  | DEC_AGR_A | DENTON | GAS-IC | NORTH | 2018 | 56.5
92 | DENTON ENERGY CENTER IC B |  | DEC_AGR_B | DENTON | GAS-IC | NORTH | 2018 | 56.5
93 | DENTON ENERGY CENTER IC C |  | DEC_AGR_C | DENTON | GAS-IC | NORTH | 2018 | 56.5
94 | DENTON ENERGY CENTER IC D |  | DEC_AGR_D | DENTON | GAS-IC | NORTH | 2018 | 56.5
95 | ECTOR COUNTY ENERGY CTG 1 |  | ECEC_G1 | ECTOR | GAS-GT | WEST | 2015 | 153.6
96 | ECTOR COUNTY ENERGY CTG 2 |  | ECEC_G2 | ECTOR | GAS-GT | WEST | 2015 | 153.6
97 | ELK STATION IC 3 |  | AEEC_ELK_3 | HALE | GAS-IC | PANHANDLE | 2016 | 195
98 | ENNIS POWER STATION CTG 2 |  | ETCCS_CT1 | ELLIS | GAS-CC | NORTH | 2002 | 209
99 | ENNIS POWER STATION STG 1 |  | ETCCS_UNIT1 | ELLIS | GAS-CC | NORTH | 2002 | 116
100 | EXTEX LAPORTE GEN STN CTG 1 |  | AZ_AZ_G1 | HARRIS | GAS-GT | HOUSTON | 2009 | 36
101 | EXTEX LAPORTE GEN STN CTG 2 |  | AZ_AZ_G2 | HARRIS | GAS-GT | HOUSTON | 2009 | 36
102 | EXTEX LAPORTE GEN STN CTG 3 |  | AZ_AZ_G3 | HARRIS | GAS-GT | HOUSTON | 2009 | 36
103 | EXTEX LAPORTE GEN STN CTG 4 |  | AZ_AZ_G4 | HARRIS | GAS-GT | HOUSTON | 2009 | 36
104 | FERGUSON REPLACEMENT CTG 1 |  | FERGCC_FERGGT1 | LLANO | GAS-CC | SOUTH | 2014 | 176
105 | FERGUSON REPLACEMENT CTG 2 |  | FERGCC_FERGGT2 | LLANO | GAS-CC | SOUTH | 2014 | 176
106 | FERGUSON REPLACEMENT STG 1 |  | FERGCC_FERGST1 | LLANO | GAS-CC | SOUTH | 2014 | 189
107 | FORNEY ENERGY CENTER CTG 11 |  | FRNYPP_GT11 | KAUFMAN | GAS-CC | NORTH | 2003 | 167
108 | FORNEY ENERGY CENTER CTG 12 |  | FRNYPP_GT12 | KAUFMAN | GAS-CC | NORTH | 2003 | 159
109 | FORNEY ENERGY CENTER CTG 13 |  | FRNYPP_GT13 | KAUFMAN | GAS-CC | NORTH | 2003 | 159
110 | FORNEY ENERGY CENTER CTG 21 |  | FRNYPP_GT21 | KAUFMAN | GAS-CC | NORTH | 2003 | 167
111 | FORNEY ENERGY CENTER CTG 22 |  | FRNYPP_GT22 | KAUFMAN | GAS-CC | NORTH | 2003 | 159
112 | FORNEY ENERGY CENTER CTG 23 |  | FRNYPP_GT23 | KAUFMAN | GAS-CC | NORTH | 2003 | 159
113 | FORNEY ENERGY CENTER STG 10 |  | FRNYPP_ST10 | KAUFMAN | GAS-CC | NORTH | 2003 | 408
114 | FORNEY ENERGY CENTER STG 20 |  | FRNYPP_ST20 | KAUFMAN | GAS-CC | NORTH | 2003 | 408
115 | FREESTONE ENERGY CENTER CTG 1 |  | FREC_GT1 | FREESTONE | GAS-CC | NORTH | 2002 | 156.2
116 | FREESTONE ENERGY CENTER CTG 2 |  | FREC_GT2 | FREESTONE | GAS-CC | NORTH | 2002 | 156.2
117 | FREESTONE ENERGY CENTER CTG 4 |  | FREC_GT4 | FREESTONE | GAS-CC | NORTH | 2002 | 156.5
118 | FREESTONE ENERGY CENTER CTG 5 |  | FREC_GT5 | FREESTONE | GAS-CC | NORTH | 2002 | 156.5
119 | FREESTONE ENERGY CENTER STG 3 |  | FREC_ST3 | FREESTONE | GAS-CC | NORTH | 2002 | 178
120 | FREESTONE ENERGY CENTER STG 6 |  | FREC_ST6 | FREESTONE | GAS-CC | NORTH | 2002 | 177.1
121 | FRIENDSWOOD G (FEGC) CTG 1 |  | FEGC_UNIT1 | HARRIS | GAS-GT | HOUSTON | 2018 | 119
122 | GRAHAM STG 1 |  | GRSES_UNIT1 | YOUNG | GAS-ST | WEST | 1960 | 234
123 | GRAHAM STG 2 |  | GRSES_UNIT2 | YOUNG | GAS-ST | WEST | 1969 | 390
124 | GREENS BAYOU CTG 73 |  | GBY_GBYGT73 | HARRIS | GAS-GT | HOUSTON | 1976 | 57
125 | GREENS BAYOU CTG 74 |  | GBY_GBYGT74 | HARRIS | GAS-GT | HOUSTON | 1976 | 57
126 | GREENS BAYOU CTG 81 |  | GBY_GBYGT81 | HARRIS | GAS-GT | HOUSTON | 1976 | 57
127 | GREENS BAYOU CTG 82 |  | GBY_GBYGT82 | HARRIS | GAS-GT | HOUSTON | 1976 | 50
128 | GREENS BAYOU CTG 83 |  | GBY_GBYGT83 | HARRIS | GAS-GT | HOUSTON | 1976 | 57
129 | GREENS BAYOU CTG 84 |  | GBY_GBYGT84 | HARRIS | GAS-GT | HOUSTON | 1976 | 57
130 | GREENVILLE IC ENGINE PLANT IC 1 |  | STEAM_ENGINE_1 | HUNT | GAS-IC | NORTH | 2010 | 8.2
131 | GREENVILLE IC ENGINE PLANT IC 2 |  | STEAM_ENGINE_2 | HUNT | GAS-IC | NORTH | 2010 | 8.2
132 | GREENVILLE IC ENGINE PLANT IC 3 |  | STEAM_ENGINE_3 | HUNT | GAS-IC | NORTH | 2010 | 8.2
133 | GUADALUPE ENERGY CENTER CTG 1 |  | GUADG_GAS1 | GUADALUPE | GAS-CC | SOUTH | 2000 | 158
134 | GUADALUPE ENERGY CENTER CTG 2 |  | GUADG_GAS2 | GUADALUPE | GAS-CC | SOUTH | 2000 | 158
135 | GUADALUPE ENERGY CENTER CTG 3 |  | GUADG_GAS3 | GUADALUPE | GAS-CC | SOUTH | 2000 | 158
136 | GUADALUPE ENERGY CENTER CTG 4 |  | GUADG_GAS4 | GUADALUPE | GAS-CC | SOUTH | 2000 | 158
137 | GUADALUPE ENERGY CENTER STG 5 |  | GUADG_STM5 | GUADALUPE | GAS-CC | SOUTH | 2000 | 200
138 | GUADALUPE ENERGY CENTER STG 6 |  | GUADG_STM6 | GUADALUPE | GAS-CC | SOUTH | 2000 | 200
139 | HANDLEY STG 3 |  | HLSES_UNIT3 | TARRANT | GAS-ST | NORTH | 1963 | 395
140 | HANDLEY STG 4 |  | HLSES_UNIT4 | TARRANT | GAS-ST | NORTH | 1976 | 435
141 | HANDLEY STG 5 |  | HLSES_UNIT5 | TARRANT | GAS-ST | NORTH | 1977 | 435
142 | HAYS ENERGY FACILITY CSG 1 |  | HAYSEN_HAYSENG1 | HAYS | GAS-CC | SOUTH | 2002 | 213
143 | HAYS ENERGY FACILITY CSG 2 | 21INR0527 | HAYSEN_HAYSENG2 | HAYS | GAS-CC | SOUTH | 2002 | 214
144 | HAYS ENERGY FACILITY CSG 3 | 21INR0527 | HAYSEN_HAYSENG3 | HAYS | GAS-CC | SOUTH | 2002 | 213
145 | HAYS ENERGY FACILITY CSG 4 |  | HAYSEN_HAYSENG4 | HAYS | GAS-CC | SOUTH | 2002 | 216
146 | HIDALGO ENERGY CENTER CTG 1 |  | DUKE_DUKE_GT1 | HIDALGO | GAS-CC | SOUTH | 2000 | 143
147 | HIDALGO ENERGY CENTER CTG 2 |  | DUKE_DUKE_GT2 | HIDALGO | GAS-CC | SOUTH | 2000 | 143
148 | HIDALGO ENERGY CENTER STG 1 |  | DUKE_DUKE_ST1 | HIDALGO | GAS-CC | SOUTH | 2000 | 172
149 | JACK COUNTY GEN FACILITY CTG 1 |  | JACKCNTY_CT1 | JACK | GAS-CC | NORTH | 2006 | 150
150 | JACK COUNTY GEN FACILITY CTG 2 |  | JACKCNTY_CT2 | JACK | GAS-CC | NORTH | 2006 | 150
151 | JACK COUNTY GEN FACILITY CTG 3 |  | JCKCNTY2_CT3 | JACK | GAS-CC | NORTH | 2011 | 150
152 | JACK COUNTY GEN FACILITY CTG 4 |  | JCKCNTY2_CT4 | JACK | GAS-CC | NORTH | 2011 | 150
153 | JACK COUNTY GEN FACILITY STG 1 |  | JACKCNTY_STG | JACK | GAS-CC | NORTH | 2006 | 285
154 | JACK COUNTY GEN FACILITY STG 2 |  | JCKCNTY2_ST2 | JACK | GAS-CC | NORTH | 2011 | 285
155 | JOHNSON COUNTY GEN FACILITY CTG 1 |  | TEN_CT1 | JOHNSON | GAS-CC | NORTH | 1997 | 163
156 | JOHNSON COUNTY GEN FACILITY STG 1 |  | TEN_STG | JOHNSON | GAS-CC | NORTH | 1997 | 106
157 | LAKE HUBBARD STG 1 |  | LHSES_UNIT1 | DALLAS | GAS-ST | NORTH | 1970 | 392
158 | LAKE HUBBARD STG 2 |  | LHSES_UNIT2A | DALLAS | GAS-ST | NORTH | 1973 | 523
159 | LAMAR ENERGY CENTER CTG 11 |  | LPCCS_CT11 | LAMAR | GAS-CC | NORTH | 2000 | 161
160 | LAMAR ENERGY CENTER CTG 12 |  | LPCCS_CT12 | LAMAR | GAS-CC | NORTH | 2000 | 153
161 | LAMAR ENERGY CENTER CTG 21 |  | LPCCS_CT21 | LAMAR | GAS-CC | NORTH | 2000 | 153
162 | LAMAR ENERGY CENTER CTG 22 |  | LPCCS_CT22 | LAMAR | GAS-CC | NORTH | 2000 | 161
163 | LAMAR ENERGY CENTER STG 1 |  | LPCCS_UNIT1 | LAMAR | GAS-CC | NORTH | 2000 | 204
164 | LAMAR ENERGY CENTER STG 2 |  | LPCCS_UNIT2 | LAMAR | GAS-CC | NORTH | 2000 | 204
165 | LAREDO CTG 4 |  | LARDVFTN_G4 | WEBB | GAS-GT | SOUTH | 2008 | 92.9
166 | LAREDO CTG 5 |  | LARDVFTN_G5 | WEBB | GAS-GT | SOUTH | 2008 | 90.1
167 | LEON CREEK PEAKER CTG 1 |  | LEON_CRK_LCPCT1 | BEXAR | GAS-GT | SOUTH | 2004 | 46
168 | LEON CREEK PEAKER CTG 2 |  | LEON_CRK_LCPCT2 | BEXAR | GAS-GT | SOUTH | 2004 | 46
169 | LEON CREEK PEAKER CTG 3 |  | LEON_CRK_LCPCT3 | BEXAR | GAS-GT | SOUTH | 2004 | 46
170 | LEON CREEK PEAKER CTG 4 |  | LEON_CRK_LCPCT4 | BEXAR | GAS-GT | SOUTH | 2004 | 46
171 | LOST PINES POWER CTG 1 |  | LOSTPI_LOSTPGT1 | BASTROP | GAS-CC | SOUTH | 2001 | 183
172 | LOST PINES POWER CTG 2 |  | LOSTPI_LOSTPGT2 | BASTROP | GAS-CC | SOUTH | 2001 | 175
173 | LOST PINES POWER STG 1 |  | LOSTPI_LOSTPST1 | BASTROP | GAS-CC | SOUTH | 2001 | 192
174 | MAGIC VALLEY STATION CTG 1 |  | NEDIN_NEDIN_G1 | HIDALGO | GAS-CC | SOUTH | 2001 | 213.6
175 | MAGIC VALLEY STATION CTG 2 |  | NEDIN_NEDIN_G2 | HIDALGO | GAS-CC | SOUTH | 2001 | 213.6
176 | MAGIC VALLEY STATION STG 3 |  | NEDIN_NEDIN_G3 | HIDALGO | GAS-CC | SOUTH | 2001 | 255.5
177 | MIDLOTHIAN ENERGY FACILITY CTG 1 |  | MDANP_CT1 | ELLIS | GAS-CC | NORTH | 2001 | 232
178 | MIDLOTHIAN ENERGY FACILITY CTG 2 |  | MDANP_CT2 | ELLIS | GAS-CC | NORTH | 2001 | 230
179 | MIDLOTHIAN ENERGY FACILITY CTG 3 |  | MDANP_CT3 | ELLIS | GAS-CC | NORTH | 2001 | 229
180 | MIDLOTHIAN ENERGY FACILITY CTG 4 |  | MDANP_CT4 | ELLIS | GAS-CC | NORTH | 2001 | 232
181 | MIDLOTHIAN ENERGY FACILITY CTG 5 |  | MDANP_CT5 | ELLIS | GAS-CC | NORTH | 2002 | 244
182 | MIDLOTHIAN ENERGY FACILITY CTG 6 |  | MDANP_CT6 | ELLIS | GAS-CC | NORTH | 2002 | 246
183 | MORGAN CREEK CTG 1 |  | MGSES_CT1 | MITCHELL | GAS-GT | WEST | 1988 | 67
184 | MORGAN CREEK CTG 2 |  | MGSES_CT2 | MITCHELL | GAS-GT | WEST | 1988 | 66
185 | MORGAN CREEK CTG 3 |  | MGSES_CT3 | MITCHELL | GAS-GT | WEST | 1988 | 66
186 | MORGAN CREEK CTG 4 |  | MGSES_CT4 | MITCHELL | GAS-GT | WEST | 1988 | 67
187 | MORGAN CREEK CTG 5 |  | MGSES_CT5 | MITCHELL | GAS-GT | WEST | 1988 | 68
188 | MORGAN CREEK CTG 6 |  | MGSES_CT6 | MITCHELL | GAS-GT | WEST | 1988 | 68
189 | MOUNTAIN CREEK STG 6 |  | MCSES_UNIT6 | DALLAS | GAS-ST | NORTH | 1956 | 122
190 | MOUNTAIN CREEK STG 7 |  | MCSES_UNIT7 | DALLAS | GAS-ST | NORTH | 1958 | 118
191 | MOUNTAIN CREEK STG 8 |  | MCSES_UNIT8 | DALLAS | GAS-ST | NORTH | 1967 | 568
192 | NUECES BAY REPOWER CTG 8 |  | NUECES_B_NUECESG8 | NUECES | GAS-CC | COASTAL | 2010 | 161
193 | NUECES BAY REPOWER CTG 9 |  | NUECES_B_NUECESG9 | NUECES | GAS-CC | COASTAL | 2010 | 161
194 | NUECES BAY REPOWER STG 7 |  | NUECES_B_NUECESG7 | NUECES | GAS-CC | COASTAL | 1972 | 322
195 | O W SOMMERS STG 1 |  | CALAVERS_OWS1 | BEXAR | GAS-ST | SOUTH | 1972 | 420
196 | O W SOMMERS STG 2 |  | CALAVERS_OWS2 | BEXAR | GAS-ST | SOUTH | 1974 | 410
197 | ODESSA-ECTOR POWER CTG 11 |  | OECCS_CT11 | ECTOR | GAS-CC | WEST | 2001 | 164.6
198 | ODESSA-ECTOR POWER CTG 12 |  | OECCS_CT12 | ECTOR | GAS-CC | WEST | 2001 | 156.1
199 | ODESSA-ECTOR POWER CTG 21 | 20INR0282 | OECCS_CT21 | ECTOR | GAS-CC | WEST | 2001 | 164.6
200 | ODESSA-ECTOR POWER CTG 22 | 20INR0282 | OECCS_CT22 | ECTOR | GAS-CC | WEST | 2001 | 156.1
201 | ODESSA-ECTOR POWER STG 1 |  | OECCS_UNIT1 | ECTOR | GAS-CC | WEST | 2001 | 206.4
202 | ODESSA-ECTOR POWER STG 2 | 20INR0282 | OECCS_UNIT2 | ECTOR | GAS-CC | WEST | 2001 | 206.4
203 | PANDA SHERMAN POWER CTG 1 |  | PANDA_S_SHER1CT1 | GRAYSON | GAS-CC | NORTH | 2014 | 218.5
204 | PANDA SHERMAN POWER CTG 2 |  | PANDA_S_SHER1CT2 | GRAYSON | GAS-CC | NORTH | 2014 | 218.5
205 | PANDA SHERMAN POWER STG 1 |  | PANDA_S_SHER1ST1 | GRAYSON | GAS-CC | NORTH | 2014 | 353.1
206 | PANDA TEMPLE I POWER CTG 1 |  | PANDA_T1_TMPL1CT1 | BELL | GAS-CC | NORTH | 2014 | 218.5
207 | PANDA TEMPLE I POWER CTG 2 |  | PANDA_T1_TMPL1CT2 | BELL | GAS-CC | NORTH | 2014 | 218.5
208 | PANDA TEMPLE I POWER STG 1 |  | PANDA_T1_TMPL1ST1 | BELL | GAS-CC | NORTH | 2014 | 353.1
209 | PANDA TEMPLE II POWER CTG 1 |  | PANDA_T2_TMPL2CT1 | BELL | GAS-CC | NORTH | 2015 | 218.5
210 | PANDA TEMPLE II POWER CTG 2 |  | PANDA_T2_TMPL2CT2 | BELL | GAS-CC | NORTH | 2015 | 218.5
211 | PANDA TEMPLE II POWER STG 1 |  | PANDA_T2_TMPL2ST1 | BELL | GAS-CC | NORTH | 2015 | 353.1
212 | PARIS ENERGY CENTER CTG 1 |  | TNSKA_GT1 | LAMAR | GAS-CC | NORTH | 1989 | 86
213 | PARIS ENERGY CENTER CTG 2 |  | TNSKA_GT2 | LAMAR | GAS-CC | NORTH | 1989 | 86
214 | PARIS ENERGY CENTER STG 1 |  | TNSKA_STG | LAMAR | GAS-CC | NORTH | 1990 | 87
215 | PASADENA COGEN FACILITY CTG 2 |  | PSG_PSG_GT2 | HARRIS | GAS-CC | HOUSTON | 2000 | 170
216 | PASADENA COGEN FACILITY CTG 3 |  | PSG_PSG_GT3 | HARRIS | GAS-CC | HOUSTON | 2000 | 170
217 | PASADENA COGEN FACILITY STG 2 |  | PSG_PSG_ST2 | HARRIS | GAS-CC | HOUSTON | 2000 | 168
218 | PEARSALL ENGINE PLANT IC A |  | PEARSAL2_AGR_A | FRIO | GAS-IC | SOUTH | 2012 | 50.6
219 | PEARSALL ENGINE PLANT IC B |  | PEARSAL2_AGR_B | FRIO | GAS-IC | SOUTH | 2012 | 50.6
220 | PEARSALL ENGINE PLANT IC C |  | PEARSAL2_AGR_C | FRIO | GAS-IC | SOUTH | 2012 | 50.6
221 | PEARSALL ENGINE PLANT IC D |  | PEARSAL2_AGR_D | FRIO | GAS-IC | SOUTH | 2012 | 50.6
222 | PERMIAN BASIN CTG 1 |  | PB2SES_CT1 | WARD | GAS-GT | WEST | 1988 | 64
223 | PERMIAN BASIN CTG 2 |  | PB2SES_CT2 | WARD | GAS-GT | WEST | 1988 | 64
224 | PERMIAN BASIN CTG 3 |  | PB2SES_CT3 | WARD | GAS-GT | WEST | 1988 | 64
225 | PERMIAN BASIN CTG 4 |  | PB2SES_CT4 | WARD | GAS-GT | WEST | 1990 | 64
226 | PERMIAN BASIN CTG 5 |  | PB2SES_CT5 | WARD | GAS-GT | WEST | 1990 | 65
227 | PHR PEAKERS (BAC) CTG 1 |  | BAC_CTG1 | GALVESTON | GAS-GT | HOUSTON | 2018 | 61
228 | PHR PEAKERS (BAC) CTG 2 |  | BAC_CTG2 | GALVESTON | GAS-GT | HOUSTON | 2018 | 62
229 | PHR PEAKERS (BAC) CTG 3 |  | BAC_CTG3 | GALVESTON | GAS-GT | HOUSTON | 2018 | 52
230 | PHR PEAKERS (BAC) CTG 4 |  | BAC_CTG4 | GALVESTON | GAS-GT | HOUSTON | 2018 | 56
231 | PHR PEAKERS (BAC) CTG 5 |  | BAC_CTG5 | GALVESTON | GAS-GT | HOUSTON | 2018 | 56
232 | PHR PEAKERS (BAC) CTG 6 |  | BAC_CTG6 | GALVESTON | GAS-GT | HOUSTON | 2018 | 54
233 | POWERLANE PLANT STG 1 |  | STEAM1A_STEAM_1 | HUNT | GAS-ST | NORTH | 1966 | 17.5
234 | POWERLANE PLANT STG 2 |  | STEAM_STEAM_2 | HUNT | GAS-ST | NORTH | 1967 | 23.5
235 | POWERLANE PLANT STG 3 |  | STEAM_STEAM_3 | HUNT | GAS-ST | NORTH | 1978 | 39.5
236 | QUAIL RUN ENERGY CTG 1 |  | QALSW_GT1 | ECTOR | GAS-CC | WEST | 2007 | 80
237 | QUAIL RUN ENERGY CTG 2 |  | QALSW_GT2 | ECTOR | GAS-CC | WEST | 2007 | 80
238 | QUAIL RUN ENERGY CTG 3 |  | QALSW_GT3 | ECTOR | GAS-CC | WEST | 2008 | 80
239 | QUAIL RUN ENERGY CTG 4 |  | QALSW_GT4 | ECTOR | GAS-CC | WEST | 2008 | 80
240 | QUAIL RUN ENERGY STG 1 |  | QALSW_STG1 | ECTOR | GAS-CC | WEST | 2007 | 98
241 | QUAIL RUN ENERGY STG 2 |  | QALSW_STG2 | ECTOR | GAS-CC | WEST | 2008 | 98
242 | R W MILLER CTG 4 |  | MIL_MILLERG4 | PALO PINTO | GAS-GT | NORTH | 1994 | 104
243 | R W MILLER CTG 5 |  | MIL_MILLERG5 | PALO PINTO | GAS-GT | NORTH | 1994 | 104
244 | R W MILLER STG 1 |  | MIL_MILLERG1 | PALO PINTO | GAS-ST | NORTH | 1968 | 75
245 | R W MILLER STG 2 |  | MIL_MILLERG2 | PALO PINTO | GAS-ST | NORTH | 1972 | 120
246 | R W MILLER STG 3 |  | MIL_MILLERG3 | PALO PINTO | GAS-ST | NORTH | 1975 | 208
247 | RAY OLINGER CTG 4 |  | OLINGR_OLING_4 | COLLIN | GAS-GT | NORTH | 2001 | 75
248 | RAY OLINGER STG 1 |  | OLINGR_OLING_1 | COLLIN | GAS-ST | NORTH | 1967 | 78
249 | RAY OLINGER STG 2 |  | OLINGR_OLING_2 | COLLIN | GAS-ST | NORTH | 1971 | 107
250 | RAY OLINGER STG 3 |  | OLINGR_OLING_3 | COLLIN | GAS-ST | NORTH | 1975 | 146
251 | REDGATE IC A |  | REDGATE_AGR_A | HIDALGO | GAS-IC | SOUTH | 2016 | 56.3
252 | REDGATE IC B |  | REDGATE_AGR_B | HIDALGO | GAS-IC | SOUTH | 2016 | 56.3
253 | REDGATE IC C |  | REDGATE_AGR_C | HIDALGO | GAS-IC | SOUTH | 2016 | 56.3
254 | REDGATE IC D |  | REDGATE_AGR_D | HIDALGO | GAS-IC | SOUTH | 2016 | 56.3
255 | RIO NOGALES POWER CTG 1 |  | RIONOG_CT1 | GUADALUPE | GAS-CC | SOUTH | 2002 | 173
256 | RIO NOGALES POWER CTG 2 | 21INR0328 | RIONOG_CT2 | GUADALUPE | GAS-CC | SOUTH | 2002 | 160
257 | RIO NOGALES POWER CTG 3 |  | RIONOG_CT3 | GUADALUPE | GAS-CC | SOUTH | 2002 | 173
258 | RIO NOGALES POWER STG 4 |  | RIONOG_ST1 | GUADALUPE | GAS-CC | SOUTH | 2002 | 310
259 | SAM RAYBURN POWER CTG 7 |  | RAYBURN_RAYBURG7 | VICTORIA | GAS-CC | SOUTH | 2003 | 50
260 | SAM RAYBURN POWER CTG 8 |  | RAYBURN_RAYBURG8 | VICTORIA | GAS-CC | SOUTH | 2003 | 51
261 | SAM RAYBURN POWER CTG 9 |  | RAYBURN_RAYBURG9 | VICTORIA | GAS-CC | SOUTH | 2003 | 50
262 | SAM RAYBURN POWER STG 10 |  | RAYBURN_RAYBURG10 | VICTORIA | GAS-CC | SOUTH | 2003 | 40
263 | SAN JACINTO SES CTG 1 |  | SJS_SJS_G1 | HARRIS | GAS-GT | HOUSTON | 1995 | 83
264 | SAN JACINTO SES CTG 2 |  | SJS_SJS_G2 | HARRIS | GAS-GT | HOUSTON | 1995 | 83
265 | SANDHILL ENERGY CENTER CTG 1 |  | SANDHSYD_SH1 | TRAVIS | GAS-GT | SOUTH | 2001 | 47
266 | SANDHILL ENERGY CENTER CTG 2 |  | SANDHSYD_SH2 | TRAVIS | GAS-GT | SOUTH | 2001 | 47
267 | SANDHILL ENERGY CENTER CTG 3 |  | SANDHSYD_SH3 | TRAVIS | GAS-GT | SOUTH | 2001 | 47
268 | SANDHILL ENERGY CENTER CTG 4 |  | SANDHSYD_SH4 | TRAVIS | GAS-GT | SOUTH | 2001 | 47
269 | SANDHILL ENERGY CENTER CTG 5A |  | SANDHSYD_SH_5A | TRAVIS | GAS-CC | SOUTH | 2004 | 151
270 | SANDHILL ENERGY CENTER CTG 6 |  | SANDHSYD_SH6 | TRAVIS | GAS-GT | SOUTH | 2010 | 47
271 | SANDHILL ENERGY CENTER CTG 7 |  | SANDHSYD_SH7 | TRAVIS | GAS-GT | SOUTH | 2010 | 47
272 | SANDHILL ENERGY CENTER STG 5C |  | SANDHSYD_SH_5C | TRAVIS | GAS-CC | SOUTH | 2004 | 148
273 | SILAS RAY CTG 10 |  | SILASRAY_SILAS_10 | CAMERON | GAS-GT | COASTAL | 2004 | 46
274 | SILAS RAY POWER CTG 9 |  | SILASRAY_SILAS_9 | CAMERON | GAS-CC | COASTAL | 1996 | 40
275 | SILAS RAY POWER STG 6 |  | SILASRAY_SILAS_6 | CAMERON | GAS-CC | COASTAL | 1962 | 20
276 | SIM GIDEON STG 1 |  | GIDEON_GIDEONG1 | BASTROP | GAS-ST | SOUTH | 1965 | 130
277 | SIM GIDEON STG 2 |  | GIDEON_GIDEONG2 | BASTROP | GAS-ST | SOUTH | 1968 | 133
278 | SIM GIDEON STG 3 |  | GIDEON_GIDEONG3 | BASTROP | GAS-ST | SOUTH | 1972 | 336
279 | SKY GLOBAL POWER ONE IC A |  | SKY1_SKY1A | COLORADO | GAS-IC | SOUTH | 2016 | 26.7
280 | SKY GLOBAL POWER ONE IC B |  | SKY1_SKY1B | COLORADO | GAS-IC | SOUTH | 2016 | 26.7
281 | STRYKER CREEK STG 1 |  | SCSES_UNIT1A | CHEROKEE | GAS-ST | NORTH | 1958 | 167
282 | STRYKER CREEK STG 2 |  | SCSES_UNIT2 | CHEROKEE | GAS-ST | NORTH | 1965 | 502
283 | T H WHARTON CTG 1 |  | THW_THWGT_1 | HARRIS | GAS-GT | HOUSTON | 1967 | 14
284 | T H WHARTON POWER CTG 31 |  | THW_THWGT31 | HARRIS | GAS-CC | HOUSTON | 1972 | 56
285 | T H WHARTON POWER CTG 32 |  | THW_THWGT32 | HARRIS | GAS-CC | HOUSTON | 1972 | 56
286 | T H WHARTON POWER CTG 33 |  | THW_THWGT33 | HARRIS | GAS-CC | HOUSTON | 1972 | 56
287 | T H WHARTON POWER CTG 34 |  | THW_THWGT34 | HARRIS | GAS-CC | HOUSTON | 1972 | 56
288 | T H WHARTON POWER CTG 41 |  | THW_THWGT41 | HARRIS | GAS-CC | HOUSTON | 1972 | 56
289 | T H WHARTON POWER CTG 42 |  | THW_THWGT42 | HARRIS | GAS-CC | HOUSTON | 1972 | 56
290 | T H WHARTON POWER CTG 43 |  | THW_THWGT43 | HARRIS | GAS-CC | HOUSTON | 1974 | 56
291 | T H WHARTON POWER CTG 44 |  | THW_THWGT44 | HARRIS | GAS-CC | HOUSTON | 1974 | 56
292 | T H WHARTON POWER CTG 51 |  | THW_THWGT51 | HARRIS | GAS-GT | HOUSTON | 1975 | 57
293 | T H WHARTON POWER CTG 52 |  | THW_THWGT52 | HARRIS | GAS-GT | HOUSTON | 1975 | 57
294 | T H WHARTON POWER CTG 53 |  | THW_THWGT53 | HARRIS | GAS-GT | HOUSTON | 1975 | 57
295 | T H WHARTON POWER CTG 54 |  | THW_THWGT54 | HARRIS | GAS-GT | HOUSTON | 1975 | 57
296 | T H WHARTON POWER CTG 55 |  | THW_THWGT55 | HARRIS | GAS-GT | HOUSTON | 1975 | 57
297 | T H WHARTON POWER CTG 56 |  | THW_THWGT56 | HARRIS | GAS-GT | HOUSTON | 1975 | 57
298 | T H WHARTON POWER STG 3 |  | THW_THWST_3 | HARRIS | GAS-CC | HOUSTON | 1974 | 109
299 | T H WHARTON POWER STG 4 |  | THW_THWST_4 | HARRIS | GAS-CC | HOUSTON | 1974 | 109
300 | TEXAS CITY POWER CTG A |  | TXCTY_CTA | GALVESTON | GAS-CC | HOUSTON | 2000 | 100.6
301 | TEXAS CITY POWER CTG B |  | TXCTY_CTB | GALVESTON | GAS-CC | HOUSTON | 2000 | 100.6
302 | TEXAS CITY POWER CTG C |  | TXCTY_CTC | GALVESTON | GAS-CC | HOUSTON | 2000 | 100.6
303 | TEXAS CITY POWER STG |  | TXCTY_ST | GALVESTON | GAS-CC | HOUSTON | 2000 | 131.5
304 | TEXAS GULF SULPHUR CTG 1 |  | TGF_TGFGT_1 | WHARTON | GAS-GT | SOUTH | 1985 | 70
305 | TRINIDAD STG 6 |  | TRSES_UNIT6 | HENDERSON | GAS-ST | NORTH | 1965 | 235
306 | V H BRAUNIG CTG 5 |  | BRAUNIG_VHB6CT5 | BEXAR | GAS-GT | SOUTH | 2009 | 48
307 | V H BRAUNIG CTG 6 |  | BRAUNIG_VHB6CT6 | BEXAR | GAS-GT | SOUTH | 2009 | 48
308 | V H BRAUNIG CTG 7 |  | BRAUNIG_VHB6CT7 | BEXAR | GAS-GT | SOUTH | 2009 | 48
309 | V H BRAUNIG CTG 8 |  | BRAUNIG_VHB6CT8 | BEXAR | GAS-GT | SOUTH | 2009 | 47
310 | V H BRAUNIG STG 1 |  | BRAUNIG_VHB1 | BEXAR | GAS-ST | SOUTH | 1966 | 217
311 | V H BRAUNIG STG 2 |  | BRAUNIG_VHB2 | BEXAR | GAS-ST | SOUTH | 1968 | 230
312 | V H BRAUNIG STG 3 |  | BRAUNIG_VHB3 | BEXAR | GAS-ST | SOUTH | 1970 | 412
313 | VICTORIA CITY (CITYVICT) CTG 1 |  | CITYVICT_CTG01 | VICTORIA | GAS-GT | SOUTH | 2020 | 46.7
314 | VICTORIA CITY (CITYVICT) CTG 2 |  | CITYVICT_CTG02 | VICTORIA | GAS-GT | SOUTH | 2020 | 46.7
315 | VICTORIA PORT (VICTPORT) CTG 1 |  | VICTPORT_CTG01 | VICTORIA | GAS-GT | SOUTH | 2019 | 46.7
316 | VICTORIA PORT (VICTPORT) CTG 2 |  | VICTPORT_CTG02 | VICTORIA | GAS-GT | SOUTH | 2019 | 46.7
317 | VICTORIA POWER CTG 6 |  | VICTORIA_VICTORG6 | VICTORIA | GAS-CC | SOUTH | 2009 | 171
318 | VICTORIA POWER STG 5 |  | VICTORIA_VICTORG5 | VICTORIA | GAS-CC | SOUTH | 1963 | 132
319 | W A PARISH CTG 1 |  | WAP_WAPGT_1 | FORT BEND | GAS-GT | HOUSTON | 1967 | 13
320 | W A PARISH STG 1 |  | WAP_WAP_G1 | FORT BEND | GAS-ST | HOUSTON | 1958 | 169
321 | W A PARISH STG 2 |  | WAP_WAP_G2 | FORT BEND | GAS-ST | HOUSTON | 1958 | 169
322 | W A PARISH STG 3 |  | WAP_WAP_G3 | FORT BEND | GAS-ST | HOUSTON | 1961 | 246
323 | W A PARISH STG 4 |  | WAP_WAP_G4 | FORT BEND | GAS-ST | HOUSTON | 1968 | 536
324 | WICHITA FALLS CTG 1 |  | WFCOGEN_UNIT1 | WICHITA | GAS-CC | WEST | 1987 | 20
325 | WICHITA FALLS CTG 2 |  | WFCOGEN_UNIT2 | WICHITA | GAS-CC | WEST | 1987 | 20
326 | WICHITA FALLS CTG 3 |  | WFCOGEN_UNIT3 | WICHITA | GAS-CC | WEST | 1987 | 20
327 | WICHITA FALLS STG 4 |  | WFCOGEN_UNIT4 | WICHITA | GAS-CC | WEST | 1987 | 17
328 | WINCHESTER POWER PARK CTG 1 |  | WIPOPA_WPP_G1 | FAYETTE | GAS-GT | SOUTH | 2009 | 44
329 | WINCHESTER POWER PARK CTG 2 |  | WIPOPA_WPP_G2 | FAYETTE | GAS-GT | SOUTH | 2009 | 44
330 | WINCHESTER POWER PARK CTG 3 |  | WIPOPA_WPP_G3 | FAYETTE | GAS-GT | SOUTH | 2009 | 44
331 | WINCHESTER POWER PARK CTG 4 |  | WIPOPA_WPP_G4 | FAYETTE | GAS-GT | SOUTH | 2009 | 44
332 | WISE-TRACTEBEL POWER CTG 1 | 20INR0286 | WCPP_CT1 | WISE | GAS-CC | NORTH | 2004 | 244.4
333 | WISE-TRACTEBEL POWER CTG 2 | 20INR0286 | WCPP_CT2 | WISE | GAS-CC | NORTH | 2004 | 244.4
334 | WISE-TRACTEBEL POWER STG 1 | 20INR0286 | WCPP_ST1 | WISE | GAS-CC | NORTH | 2004 | 298
335 | WOLF HOLLOW 2 CTG 4 | 18INR0076 | WHCCS2_CT4 | HOOD | GAS-CC | NORTH | 2017 | 330.6
336 | WOLF HOLLOW 2 CTG 5 | 18INR0076 | WHCCS2_CT5 | HOOD | GAS-CC | NORTH | 2017 | 331.1
337 | WOLF HOLLOW 2 STG 6 | 18INR0076 | WHCCS2_STG6 | HOOD | GAS-CC | NORTH | 2017 | 468.9
338 | WOLF HOLLOW POWER CTG 1 |  | WHCCS_CT1 | HOOD | GAS-CC | NORTH | 2002 | 240.4
339 | WOLF HOLLOW POWER CTG 2 |  | WHCCS_CT2 | HOOD | GAS-CC | NORTH | 2002 | 234.4
340 | WOLF HOLLOW POWER STG |  | WHCCS_STG | HOOD | GAS-CC | NORTH | 2002 | 270
341 | BIOENERGY AUSTIN WALZEM RD LFG |  | DG_WALZE_4UNITS | BEXAR | BIOMASS | SOUTH | 2002 | 9.8
342 | BIOENERGY TEXAS COVEL GARDENS LFG |  | DG_MEDIN_1UNIT | BEXAR | BIOMASS | SOUTH | 2005 | 9.6
343 | FARMERS BRANCH LANDFILL GAS TO ENERGY |  | DG_HBR_2UNITS | DENTON | BIOMASS | NORTH | 2011 | 3.2
344 | GRAND PRAIRIE LFG |  | DG_TRIRA_1UNIT | DALLAS | BIOMASS | NORTH | 2015 | 4
345 | NELSON GARDENS LFG |  | DG_78252_4UNITS | BEXAR | BIOMASS | SOUTH | 2013 | 4.2
346 | SKYLINE LFG |  | DG_FERIS_4 UNITS | DALLAS | BIOMASS | NORTH | 2007 | 6.4
347 | WM RENEWABLE-AUSTIN LFG |  | DG_SPRIN_4UNITS | TRAVIS | BIOMASS | SOUTH | 2007 | 6.4
348 | WM RENEWABLE-BIOENERGY PARTNERS LFG |  | DG_BIOE_2UNITS | DENTON | BIOMASS | NORTH | 1988 | 6.2
349 | WM RENEWABLE-DFW GAS RECOVERY LFG |  | DG_BIO2_4UNITS | DENTON | BIOMASS | NORTH | 2009 | 6.4
350 | WM RENEWABLE-MESQUITE CREEK LFG |  | DG_FREIH_2UNITS | COMAL | BIOMASS | SOUTH | 2011 | 3.2
351 | WM RENEWABLE-WESTSIDE LFG |  | DG_WSTHL_3UNITS | PARKER | BIOMASS | NORTH | 2010 | 4.8
352 | Operational Capacity Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 65113.6
353
354 | Operational Resources (Hydro)
355 | AMISTAD HYDRO 1 |  | AMISTAD_AMISTAG1 | VAL VERDE | HYDRO | WEST | 1983 | 37.9
356 | AMISTAD HYDRO 2 |  | AMISTAD_AMISTAG2 | VAL VERDE | HYDRO | WEST | 1983 | 37.9
357 | AUSTIN HYDRO 1 |  | AUSTPL_AUSTING1 | TRAVIS | HYDRO | SOUTH | 1940 | 8
358 | AUSTIN HYDRO 2 |  | AUSTPL_AUSTING2 | TRAVIS | HYDRO | SOUTH | 1940 | 9
359 | BUCHANAN HYDRO 1 |  | BUCHAN_BUCHANG1 | LLANO | HYDRO | SOUTH | 1938 | 16
360 | BUCHANAN HYDRO 2 |  | BUCHAN_BUCHANG2 | LLANO | HYDRO | SOUTH | 1938 | 16
361 | BUCHANAN HYDRO 3 |  | BUCHAN_BUCHANG3 | LLANO | HYDRO | SOUTH | 1950 | 17
362 | DENISON DAM 1 |  | DNDAM_DENISOG1 | GRAYSON | HYDRO | NORTH | 1944 | 40
363 | DENISON DAM 2 |  | DNDAM_DENISOG2 | GRAYSON | HYDRO | NORTH | 1948 | 40
364 | EAGLE PASS HYDRO |  | EAGLE_HY_EAGLE_HY1 | MAVERICK | HYDRO | SOUTH | 2005 | 9.6
365 | FALCON HYDRO 1 |  | FALCON_FALCONG1 | STARR | HYDRO | SOUTH | 1954 | 12
366 | FALCON HYDRO 2 |  | FALCON_FALCONG2 | STARR | HYDRO | SOUTH | 1954 | 12
367 | FALCON HYDRO 3 |  | FALCON_FALCONG3 | STARR | HYDRO | SOUTH | 1954 | 12
368 | GRANITE SHOALS HYDRO 1 |  | WIRTZ_WIRTZ_G1 | BURNET | HYDRO | SOUTH | 1951 | 29
369 | GRANITE SHOALS HYDRO 2 |  | WIRTZ_WIRTZ_G2 | BURNET | HYDRO | SOUTH | 1951 | 29
370 | GUADALUPE BLANCO RIVER AUTH-CANYON |  | CANYHY_CANYHYG1 | COMAL | HYDRO | SOUTH | 1989 | 6
371 | INKS HYDRO 1 |  | INKSDA_INKS_G1 | LLANO | HYDRO | SOUTH | 1938 | 14
372 | MARBLE FALLS HYDRO 1 |  | MARBFA_MARBFAG1 | BURNET | HYDRO | SOUTH | 1951 | 21
373 | MARBLE FALLS HYDRO 2 |  | MARBFA_MARBFAG2 | BURNET | HYDRO | SOUTH | 1951 | 20
374 | MARSHALL FORD HYDRO 1 |  | MARSFO_MARSFOG1 | TRAVIS | HYDRO | SOUTH | 1941 | 34
375 | MARSHALL FORD HYDRO 2 |  | MARSFO_MARSFOG2 | TRAVIS | HYDRO | SOUTH | 1941 | 36
376 | MARSHALL FORD HYDRO 3 |  | MARSFO_MARSFOG3 | TRAVIS | HYDRO | SOUTH | 1941 | 36
377 | WHITNEY DAM HYDRO |  | WND_WHITNEY1 | BOSQUE | HYDRO | NORTH | 1953 | 22
378 | WHITNEY DAM HYDRO 2 |  | WND_WHITNEY2 | BOSQUE | HYDRO | NORTH | 1953 | 22
379 | Operational Capacity Total (Hydro) | [6 empty] | 536.4
380 | Hydro Capacity Contribution (Top 20 Hours) |  | HYDRO_CAP_CONT |  |  |  |  | 439.9
381
382 | Operational Hydro Resources, Settlement Only Distributed Generators (SODGs)
383 | ARLINGTON OUTLET HYDROELECTRIC FACILITY |  | DG_OAKHL_1UNIT | TARRANT | HYDRO | NORTH | 2014 | 1.4
384 | GUADALUPE BLANCO RIVER AUTH-LAKEWOOD TAP |  | DG_LKWDT_2UNITS | GONZALES | HYDRO | SOUTH | 1931 | 4.8
385 | GUADALUPE BLANCO RIVER AUTH-MCQUEENEY |  | DG_MCQUE_5UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 7.7
386 | GUADALUPE BLANCO RIVER AUTH-SCHUMANSVILLE |  | DG_SCHUM_2UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 3.6
387 | LEWISVILLE HYDRO-CITY OF GARLAND |  | DG_LWSVL_1UNIT | DENTON | HYDRO | NORTH | 1991 | 2.2
388 | Operational Hydro Resources Total, Settlement Only Distributed Generators (SODGs) | [6 empty] | 19.7
389 | Hydro SODG Capacity Contribution (Highest 20 Peak Load Hours) |  | DG_HYDRO_CAP_CONT |  |  |  |  | 16.1559
390
391 | Operational Capacity Unavailable due to Extended Outage or Derate |  | OPERATION_UNAVAIL |  |  |  |  | -4.9206
392 | Operational Capacity Total (Including Hydro) |  | OPERATION_TOTAL |  |  |  |  | 65564.7353
393
394 | Operational Resources (Switchable)
395 | ANTELOPE IC 1 |  | AEEC_ANTLP_1 | HALE | GAS-IC | PANHANDLE | 2016 | 56
396 | ANTELOPE IC 2 |  | AEEC_ANTLP_2 | HALE | GAS-IC | PANHANDLE | 2016 | 56
397 | ANTELOPE IC 3 |  | AEEC_ANTLP_3 | HALE | GAS-IC | PANHANDLE | 2016 | 56
398 | ELK STATION CTG 1 |  | AEEC_ELK_1 | HALE | GAS-GT | PANHANDLE | 2016 | 195
399 | ELK STATION CTG 2 |  | AEEC_ELK_2 | HALE | GAS-GT | PANHANDLE | 2016 | 195
400 | TENASKA FRONTIER STATION CTG 1 |  | FTR_FTR_G1 | GRIMES | GAS-CC | NORTH | 2000 | 180
401 | TENASKA FRONTIER STATION CTG 2 |  | FTR_FTR_G2 | GRIMES | GAS-CC | NORTH | 2000 | 180
402 | TENASKA FRONTIER STATION CTG 3 |  | FTR_FTR_G3 | GRIMES | GAS-CC | NORTH | 2000 | 180
403 | TENASKA FRONTIER STATION STG 4 |  | FTR_FTR_G4 | GRIMES | GAS-CC | NORTH | 2000 | 400
404 | TENASKA GATEWAY STATION CTG 1 |  | TGCCS_CT1 | RUSK | GAS-CC | NORTH | 2001 | 162
405 | TENASKA GATEWAY STATION CTG 2 |  | TGCCS_CT2 | RUSK | GAS-CC | NORTH | 2001 | 179
406 | TENASKA GATEWAY STATION CTG 3 |  | TGCCS_CT3 | RUSK | GAS-CC | NORTH | 2001 | 178
407 | TENASKA GATEWAY STATION STG 4 |  | TGCCS_UNIT4 | RUSK | GAS-CC | NORTH | 2001 | 389
408 | TENASKA KIAMICHI STATION 1CT101 |  | KMCHI_1CT101 | FANNIN | GAS-CC | NORTH | 2003 | 162
409 | TENASKA KIAMICHI STATION 1CT201 |  | KMCHI_1CT201 | FANNIN | GAS-CC | NORTH | 2003 | 158
410 | TENASKA KIAMICHI STATION 1ST |  | KMCHI_1ST | FANNIN | GAS-CC | NORTH | 2003 | 322
411 | TENASKA KIAMICHI STATION 2CT101 |  | KMCHI_2CT101 | FANNIN | GAS-CC | NORTH | 2003 | 159
412 | TENASKA KIAMICHI STATION 2CT201 |  | KMCHI_2CT201 | FANNIN | GAS-CC | NORTH | 2003 | 161
413 | TENASKA KIAMICHI STATION 2ST |  | KMCHI_2ST | FANNIN | GAS-CC | NORTH | 2003 | 323
414 | Switchable Capacity Total | [6 empty] | 3691
415
416 | Switchable Capacity Unavailable to ERCOT
417 | ANTELOPE IC 1 |  | AEEC_ANTLP_1_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | -56
418 | ANTELOPE IC 2 |  | AEEC_ANTLP_2_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | -56
419 | ANTELOPE IC 3 |  | AEEC_ANTLP_3_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | -56
420 | ELK STATION CTG 1 |  | AEEC_ELK_1_UNAVAIL | HALE | GAS-GT | PANHANDLE | 2017 | -195
421 | ELK STATION CTG 2 |  | AEEC_ELK_2_UNAVAIL | HALE | GAS-GT | PANHANDLE | 2017 | -195
422 | Switchable Capacity Unavailable to ERCOT |  | SWITCH_UNAVAIL |  |  |  |  | -558
423
424 | Available Mothball Capacity based on Owner's Return Probability |  | MOTH_AVAIL |  |  |  |  | 0
425
426 | Private-Use Network Capacity Contribution (Top 20 Hours) |  | PUN_CAP_CONT |  | GAS |  |  | 2758
427 | Private-Use Network Forecast Adjustment (per Protocol 10.3.2.4) |  | PUN_CAP_ADJUST |  | GAS |  |  | 41
428
429 | Operational Resources (Wind)
430 | BAFFIN WIND UNIT1 |  | BAFFIN_UNIT1 | KENEDY | WIND-C | COASTAL | 2016 | 100
431 | BAFFIN WIND UNIT2 |  | BAFFIN_UNIT2 | KENEDY | WIND-C | COASTAL | 2016 | 102
432 | BRUENNING'S BREEZE A |  | BBREEZE_UNIT1 | WILLACY | WIND-C | COASTAL | 2017 | 120
433 | BRUENNING'S BREEZE B |  | BBREEZE_UNIT2 | WILLACY | WIND-C | COASTAL | 2017 | 108
434 | CAMERON COUNTY WIND |  | CAMWIND_UNIT1 | CAMERON | WIND-C | COASTAL | 2016 | 165
435 | CHAPMAN RANCH WIND IA (SANTA CRUZ) |  | SANTACRU_UNIT1 | NUECES | WIND-C | COASTAL | 2017 | 150.6
436 | CHAPMAN RANCH WIND IB (SANTA CRUZ) |  | SANTACRU_UNIT2 | NUECES | WIND-C | COASTAL | 2017 | 98.4
437 | GULF WIND I |  | TGW_T1 | KENEDY | WIND-C | COASTAL | 2009 | 141.6
438 | GULF WIND II |  | TGW_T2 | KENEDY | WIND-C | COASTAL | 2009 | 141.6
439 | KARANKAWA WIND 1A |  | KARAKAW1_UNIT1 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 103.3
440 | KARANKAWA WIND 1B |  | KARAKAW1_UNIT2 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 103.3
441 | KARANKAWA WIND 2 |  | KARAKAW2_UNIT3 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 100.4
442 | LOS VIENTOS WIND I |  | LV1_LV1A | WILLACY | WIND-C | COASTAL | 2013 | 200.1
443 | LOS VIENTOS WIND II |  | LV2_LV2 | WILLACY | WIND-C | COASTAL | 2013 | 201.6
444 | MAGIC VALLEY WIND (REDFISH) 1A |  | REDFISH_MV1A | WILLACY | WIND-C | COASTAL | 2012 | 99.8
445 | MAGIC VALLEY WIND (REDFISH) 1B |  | REDFISH_MV1B | WILLACY | WIND-C | COASTAL | 2012 | 103.5
446 | MIDWAY WIND |  | MIDWIND_UNIT1 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 162.8
447 | PAPALOTE CREEK WIND |  | PAP1_PAP1 | SAN PATRICIO | WIND-C | COASTAL | 2009 | 179.9
448 | PAPALOTE CREEK WIND II |  | COTTON_PAP2 | SAN PATRICIO | WIND-C | COASTAL | 2010 | 200.1
449 | PENASCAL WIND 1 |  | PENA_UNIT1 | KENEDY | WIND-C | COASTAL | 2009 | 160.8
450 | PENASCAL WIND 2 |  | PENA_UNIT2 | KENEDY | WIND-C | COASTAL | 2009 | 141.6
451 | PENASCAL WIND 3 |  | PENA3_UNIT3 | KENEDY | WIND-C | COASTAL | 2011 | 100.8
452 | PEYTON CREEK WIND |  | PEY_UNIT1 | MATAGORDA | WIND-C | COASTAL | 2020 | 151.2
453 | SAN ROMAN WIND |  | SANROMAN_WIND_1 | CAMERON | WIND-C | COASTAL | 2017 | 95.2
454 | STELLA WIND |  | STELLA_UNIT1 | KENEDY | WIND-C | COASTAL | 2018 | 201
455 | HARBOR WIND |  | DG_NUECE_6UNITS | NUECES | WIND-C | COASTAL | 2012 | 9
456 | BRISCOE WIND |  | BRISCOE_WIND | BRISCOE | WIND-P | PANHANDLE | 2015 | 149.8
457 | CANADIAN BREAKS WIND |  | CN_BRKS_UNIT_1 | OLDHAM | WIND-P | PANHANDLE | 2019 | 210.1
458 | COTTON PLAINS WIND |  | COTPLNS_COTTONPL | FLOYD | WIND-P | PANHANDLE | 2017 | 50.4
459 | DOUG COLBECK'S CORNER (CONWAY) B |  | GRANDVW1_COLB | CARSON | WIND-P | PANHANDLE | 2016 | 100.2
460 | DOUG COLBECK'S CORNER (CONWAY) A |  | GRANDVW1_COLA | CARSON | WIND-P | PANHANDLE | 2016 | 100.2
461 | FALVEZ ASTRA WIND |  | ASTRA_UNIT1 | RANDALL | WIND-P | PANHANDLE | 2017 | 163.2
462 | GRANDVIEW WIND 1 (CONWAY) GV1A |  | GRANDVW1_GV1A | CARSON | WIND-P | PANHANDLE | 2014 | 107.4
463 | GRANDVIEW WIND 1 (CONWAY) GV1B |  | GRANDVW1_GV1B | CARSON | WIND-P | PANHANDLE | 2014 | 103.8
464 | HEREFORD WIND G |  | HRFDWIND_WIND_G | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 99.9
465 | HEREFORD WIND V |  | HRFDWIND_WIND_V | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 100
466 | JUMBO ROAD WIND 1 |  | HRFDWIND_JRDWIND1 | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 146.2
467 | JUMBO ROAD WIND 2 |  | HRFDWIND_JRDWIND2 | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 153.6
468 | LONGHORN WIND NORTH U1 |  | LHORN_N_UNIT1 | FLOYD | WIND-P | PANHANDLE | 2015 | 100
469 | LONGHORN WIND NORTH U2 |  | LHORN_N_UNIT2 | FLOYD | WIND-P | PANHANDLE | 2015 | 100
470 | MARIAH DEL NORTE 1 |  | MARIAH_NORTE1 | PARMER | WIND-P | PANHANDLE | 2017 | 115.2
471 | MARIAH DEL NORTE 2 |  | MARIAH_NORTE2 | PARMER | WIND-P | PANHANDLE | 2017 | 115.2
472 | MCADOO WIND |  | MWEC_G1 | DICKENS | WIND-P | PANHANDLE | 2008 | 150
473 | MIAMI WIND G1 |  | MIAM1_G1 | GRAY | WIND-P | PANHANDLE | 2014 | 144.3
474 | MIAMI WIND G2 |  | MIAM1_G2 | GRAY | WIND-P | PANHANDLE | 2014 | 144.3
475 | OLD SETTLER WIND |  | COTPLNS_OLDSETLR | FLOYD | WIND-P | PANHANDLE | 2017 | 151.2
476 | PANHANDLE WIND 1 U1 |  | PH1_UNIT1 | CARSON | WIND-P | PANHANDLE | 2014 | 109.2
477 | PANHANDLE WIND 1 U2 |  | PH1_UNIT2 | CARSON | WIND-P | PANHANDLE | 2014 | 109.2
478 | PANHANDLE WIND 2 U1 |  | PH2_UNIT1 | CARSON | WIND-P | PANHANDLE | 2014 | 94.2
479 | PANHANDLE WIND 2 U2 |  | PH2_UNIT2 | CARSON | WIND-P | PANHANDLE | 2014 | 96.6
480 | ROUTE 66 WIND |  | ROUTE_66_WIND1 | CARSON | WIND-P | PANHANDLE | 2015 | 150
481 | SALT FORK 1 WIND U1 |  | SALTFORK_UNIT1 | DONLEY | WIND-P | PANHANDLE | 2017 | 64
482 | SALT FORK 1 WIND U2 |  | SALTFORK_UNIT2 | DONLEY | WIND-P | PANHANDLE | 2017 | 110
483 | SOUTH PLAINS WIND 1 U1 |  | SPLAIN1_WIND1 | FLOYD | WIND-P | PANHANDLE | 2015 | 102
484 | SOUTH PLAINS WIND 1 U2 |  | SPLAIN1_WIND2 | FLOYD | WIND-P | PANHANDLE | 2015 | 98
485 | SOUTH PLAINS WIND 2 U1 |  | SPLAIN2_WIND21 | FLOYD | WIND-P | PANHANDLE | 2016 | 148.5
486 | SOUTH PLAINS WIND 2 U2 |  | SPLAIN2_WIND22 | FLOYD | WIND-P | PANHANDLE | 2016 | 151.8
487 | SPINNING SPUR WIND TWO A |  | SSPURTWO_WIND_1 | OLDHAM | WIND-P | PANHANDLE | 2014 | 161
488 | SPINNING SPUR WIND TWO B |  | SSPURTWO_SS3WIND2 | OLDHAM | WIND-P | PANHANDLE | 2015 | 98
489 | SPINNING SPUR WIND TWO C |  | SSPURTWO_SS3WIND1 | OLDHAM | WIND-P | PANHANDLE | 2015 | 96
490 | WAKE WIND 1 |  | WAKEWE_G1 | DICKENS | WIND-P | PANHANDLE | 2016 | 114.9
491 | WAKE WIND 2 |  | WAKEWE_G2 | DICKENS | WIND-P | PANHANDLE | 2016 | 142.3
492 | WHIRLWIND ENERGY |  | WEC_WECG1 | FLOYD | WIND-P | PANHANDLE | 2007 | 57
493 | WOLF FLATS WIND (WIND MGT) |  | DG_TURL_UNIT1 | HALL | WIND-P | PANHANDLE | 2007 | 1
494 | ANACACHO WIND |  | ANACACHO_ANA | KINNEY | WIND-O | SOUTH | 2012 | 99.8
495 | BARTON CHAPEL WIND |  | BRTSW_BCW1 | JACK | WIND-O | NORTH | 2007 | 120
496 | BLUE SUMMIT WIND 1 A | 18INR0072 | BLSUMMIT_BLSMT1_5 | WILBARGER | WIND-O | WEST | 2013 | 8.8
497 | BLUE SUMMIT WIND 1 B | 18INR0072 | BLSUMMIT_BLSMT1_6 | WILBARGER | WIND-O | WEST | 2013 | 124.3
498 | BLUE SUMMIT WIND 2 A |  | BLSUMMIT_UNIT2_25 | WILBARGER | WIND-O | WEST | 2020 | 89.7
499 | BLUE SUMMIT WIND 2 B |  | BLSUMMIT_UNIT2_17 | WILBARGER | WIND-O | WEST | 2020 | 6.7
500 | BLUE SUMMIT WIND 3 A |  | BLSUMIT3_UNIT_17 | WILBARGER | WIND-O | WEST | 2020 | 13.4
501 | BLUE SUMMIT WIND 3 B |  | BLSUMIT3_UNIT_25 | WILBARGER | WIND-O | WEST | 2020 | 182.4
502 | BOBCAT BLUFF WIND |  | BCATWIND_WIND_1 | ARCHER | WIND-O | WEST | 2020 | 162
503 | BUCKTHORN WIND 1 A |  | BUCKTHRN_UNIT1 | ERATH | WIND-O | NORTH | 2017 | 44.9
504 | BUCKTHORN WIND 1 B |  | BUCKTHRN_UNIT2 | ERATH | WIND-O | NORTH | 2017 | 55.7
505 | BUFFALO GAP WIND 1 |  | BUFF_GAP_UNIT1 | TAYLOR | WIND-O | WEST | 2006 | 120.6
506 | BUFFALO GAP WIND 2_1 |  | BUFF_GAP_UNIT2_1 | TAYLOR | WIND-O | WEST | 2007 | 115.5
507 | BUFFALO GAP WIND 2_2 |  | BUFF_GAP_UNIT2_2 | TAYLOR | WIND-O | WEST | 2007 | 117
508 | BUFFALO GAP WIND 3 |  | BUFF_GAP_UNIT3 | TAYLOR | WIND-O | WEST | 2008 | 170.2
509 | BULL CREEK WIND U1 |  | BULLCRK_WND1 | BORDEN | WIND-O | WEST | 2009 | 88
510 | BULL CREEK WIND U2 |  | BULLCRK_WND2 | BORDEN | WIND-O | WEST | 2009 | 90
511 | CABEZON WIND (RIO BRAVO I WIND) 1 A |  | CABEZON_WIND1 | STARR | WIND-O | SOUTH | 2019 | 115.2
512 | CABEZON WIND (RIO BRAVO I WIND) 1 B |  | CABEZON_WIND2 | STARR | WIND-O | SOUTH | 2019 | 122.4
513 | CALLAHAN WIND |  | CALLAHAN_WND1 | CALLAHAN | WIND-O | WEST | 2004 | 114
514 | CAMP SPRINGS WIND 1 |  | CSEC_CSECG1 | SCURRY | WIND-O | WEST | 2007 | 130.5
515 | CAMP SPRINGS WIND 2 |  | CSEC_CSECG2 | SCURRY | WIND-O | WEST | 2007 | 120
516 | CAPRICORN RIDGE WIND 1 | 17INR0054 | CAPRIDGE_CR1 | STERLING | WIND-O | WEST | 2007 | 231.7
517 | CAPRICORN RIDGE WIND 2 | 17INR0054 | CAPRIDGE_CR2 | STERLING | WIND-O | WEST | 2007 | 149.5
518 | CAPRICORN RIDGE WIND 3 | 17INR0054 | CAPRIDGE_CR3 | STERLING | WIND-O | WEST | 2008 | 200.9
519 | CAPRICORN RIDGE WIND 4 | 17INR0061 | CAPRIDG4_CR4 | COKE | WIND-O | WEST | 2008 | 121.5
520 | CEDRO HILL WIND 1 |  | CEDROHIL_CHW1 | WEBB | WIND-O | SOUTH | 2010 | 75
521 | CEDRO HILL WIND 2 |  | CEDROHIL_CHW2 | WEBB | WIND-O | SOUTH | 2010 | 75
522 | CHAMPION WIND |  | CHAMPION_UNIT1 | NOLAN | WIND-O | WEST | 2008 | 126.5
523 | DERMOTT WIND 1_1 |  | DERMOTT_UNIT1 | SCURRY | WIND-O | WEST | 2017 | 126.5
524 | DERMOTT WIND 1_2 |  | DERMOTT_UNIT2 | SCURRY | WIND-O | WEST | 2017 | 126.5
525 | DESERT SKY WIND 1 | 17INR0070 | INDNENR_INDNENR | PECOS | WIND-O | WEST | 2002 | 85.1
526 | DESERT SKY WIND 2 | 17INR0070 | INDNENR_INDNENR_2 | PECOS | WIND-O | WEST | 2002 | 85.1
527 | ELBOW CREEK WIND |  | ELB_ELBCREEK | HOWARD | WIND-O | WEST | 2008 | 118.7
528 | ELECTRA WIND 1 |  | DIGBY_UNIT1 | WILBARGER | WIND-O | WEST | 2017 | 98.9
529 | ELECTRA WIND 2 |  | DIGBY_UNIT2 | WILBARGER | WIND-O | WEST | 2017 | 131.1
530 | FLAT TOP WIND I |  | FTWIND_UNIT_1 | MILLS | WIND-O | NORTH | 2018 | 200
531 | FLUVANNA RENEWABLE 1 A |  | FLUVANNA_UNIT1 | SCURRY | WIND-O | WEST | 2017 | 79.8
532 | FLUVANNA RENEWABLE 1 B |  | FLUVANNA_UNIT2 | SCURRY | WIND-O | WEST | 2017 | 75.6
533 | FOARD CITY WIND 1 A |  | FOARDCTY_UNIT1 | FOARD | WIND-O | WEST | 2019 | 186.5
534 | FOARD CITY WIND 1 B |  | FOARDCTY_UNIT2 | FOARD | WIND-O | WEST | 2019 | 163.8
535 | FOREST CREEK WIND |  | MCDLD_FCW1 | GLASSCOCK | WIND-O | WEST | 2007 | 124.2
536 | GOAT WIND |  | GOAT_GOATWIND | STERLING | WIND-O | WEST | 2008 | 80
537 | GOAT WIND 2 |  | GOAT_GOATWIN2 | STERLING | WIND-O | WEST | 2010 | 69.6
538 | GOLDTHWAITE WIND 1 |  | GWEC_GWEC_G1 | MILLS | WIND-O | NORTH | 2014 | 148.6
539 | GOPHER CREEK WIND 1 |  | GOPHER_UNIT1 | BORDEN | WIND-O | WEST | 2020 | 82
540 | GOPHER CREEK WIND 2 |  | GOPHER_UNIT2 | BORDEN | WIND-O | WEST | 2020 | 76
541 | GREEN MOUNTAIN WIND (BRAZOS) U1 |  | BRAZ_WND_WND1 | SCURRY | WIND-O | WEST | 2003 | 99
542 | GREEN MOUNTAIN WIND (BRAZOS) U2 |  | BRAZ_WND_WND2 | SCURRY | WIND-O | WEST | 2003 | 61
543 | GREEN PASTURES WIND I |  | GPASTURE_WIND_I | BAYLOR | WIND-O | WEST | 2015 | 150
544 | VERTIGO WIND (FORMERLY GREEN PASTURES WIND 2) |  | VERTIGO_WIND_I | BAYLOR | WIND-O | WEST | 2015 | 150
545 | GUNSIGHT MOUNTAIN WIND |  | GUNMTN_G1 | HOWARD | WIND-O | WEST | 2016 | 119.9
546 | HACKBERRY WIND |  | HWF_HWFG1 | SHACKELFORD | WIND-O | WEST | 2008 | 163.5
547 | HICKMAN (SANTA RITA WIND) 1 |  | HICKMAN_G1 | REAGAN | WIND-O | WEST | 2018 | 152.5
548 | HICKMAN (SANTA RITA WIND) 2 |  | HICKMAN_G2 | REAGAN | WIND-O | WEST | 2018 | 147.5
549 | HIDALGO & STARR WIND 11 |  | MIRASOLE_MIR11 | HIDALGO | WIND-O | SOUTH | 2016 | 52
550 | HIDALGO & STARR WIND 12 |  | MIRASOLE_MIR12 | HIDALGO | WIND-O | SOUTH | 2016 | 98
551 | HIDALGO & STARR WIND 21 |  | MIRASOLE_MIR21 | HIDALGO | WIND-O | SOUTH | 2016 | 100
552 | HORSE CREEK WIND 1 |  | HORSECRK_UNIT1 | HASKELL | WIND-O | WEST | 2017 | 131.1
553 | HORSE CREEK WIND 2 |  | HORSECRK_UNIT2 | HASKELL | WIND-O | WEST | 2017 | 98.9
554 | HORSE HOLLOW WIND 1 | 17INR0052 | H_HOLLOW_WND1 | TAYLOR | WIND-O | WEST | 2005 | 230
555 | HORSE HOLLOW WIND 2 | 17INR0052 | HHOLLOW2_WIND1 | TAYLOR | WIND-O | WEST | 2006 | 184
556 | HORSE HOLLOW WIND 3 | 17INR0052 | HHOLLOW3_WND_1 | TAYLOR | WIND-O | WEST | 2006 | 241.4
557 | HORSE HOLLOW WIND 4 | 17INR0052 | HHOLLOW4_WND1 | TAYLOR | WIND-O | WEST | 2006 | 115
558 | INADALE WIND 1 |  | INDL_INADALE1 | NOLAN | WIND-O | WEST | 2008 | 95
559 | INADALE WIND 2 |  | INDL_INADALE2 | NOLAN | WIND-O | WEST | 2008 | 102
560 | INDIAN MESA WIND |  | INDNNWP_INDNNWP2 | PECOS | WIND-O | WEST | 2001 | 91.8
561 | JAVELINA I WIND 18 |  | BORDAS_JAVEL18 | WEBB | WIND-O | SOUTH | 2015 | 19.7
562 | JAVELINA I WIND 20 |  | BORDAS_JAVEL20 | WEBB | WIND-O | SOUTH | 2015 | 230
563 | JAVELINA II WIND 1 |  | BORDAS2_JAVEL2_A | WEBB | WIND-O | SOUTH | 2017 | 96
564 | JAVELINA II WIND 2 |  | BORDAS2_JAVEL2_B | WEBB | WIND-O | SOUTH | 2017 | 74
565 | JAVELINA II WIND 3 |  | BORDAS2_JAVEL2_C | WEBB | WIND-O | SOUTH | 2017 | 30
566 | KEECHI WIND |  | KEECHI_U1 | JACK | WIND-O | NORTH | 2015 | 110
567 | KING MOUNTAIN WIND (NE) |  | KING_NE_KINGNE | UPTON | WIND-O | WEST | 2001 | 79.7
568 | KING MOUNTAIN WIND (NW) |  | KING_NW_KINGNW | UPTON | WIND-O | WEST | 2001 | 79.7
569 | KING MOUNTAIN WIND (SE) |  | KING_SE_KINGSE | UPTON | WIND-O | WEST | 2001 | 40.5
570 | KING MOUNTAIN WIND (SW) |  | KING_SW_KINGSW | UPTON | WIND-O | WEST | 2001 | 79.7
571 | LANGFORD WIND POWER |  | LGD_LANGFORD | TOM GREEN | WIND-O | WEST | 2009 | 160
572 | LOCKETT WIND FARM |  | LOCKETT_UNIT1 | WILBARGER | WIND-O | WEST | 2019 | 183.7
573 | LOGANS GAP WIND I U1 |  | LGW_UNIT1 | COMANCHE | WIND-O | NORTH | 2015 | 106.3
574 | LOGANS GAP WIND I U2 |  | LGW_UNIT2 | COMANCHE | WIND-O | NORTH | 2015 | 103.8
575 | LONE STAR WIND 1 (MESQUITE) |  | LNCRK_G83 | SHACKELFORD | WIND-O | WEST | 2006 | 194
576 | LONE STAR WIND 2 (POST OAK) U1 |  | LNCRK2_G871 | SHACKELFORD | WIND-O | WEST | 2007 | 98
577 | LONE STAR WIND 2 (POST OAK) U2 |  | LNCRK2_G872 | SHACKELFORD | WIND-O | WEST | 2007 | 100
578 | LORAINE WINDPARK I |  | LONEWOLF_G1 | MITCHELL | WIND-O | WEST | 2010 | 49.5
579 | LORAINE WINDPARK II |  | LONEWOLF_G2 | MITCHELL | WIND-O | WEST | 2010 | 51
580 | LORAINE WINDPARK III |  | LONEWOLF_G3 | MITCHELL | WIND-O | WEST | 2011 | 25.5
581 | LORAINE WINDPARK IV |  | LONEWOLF_G4 | MITCHELL | WIND-O | WEST | 2011 | 24
582 | LOS VIENTOS III WIND |  | LV3_UNIT_1 | STARR | WIND-O | SOUTH | 2015 | 200
583 | LOS VIENTOS IV WIND |  | LV4_UNIT_1 | STARR | WIND-O | SOUTH | 2016 | 200
584 | LOS VIENTOS V WIND |  | LV5_UNIT_1 | STARR | WIND-O | SOUTH | 2016 | 110
585 | MESQUITE CREEK WIND 1 |  | MESQCRK_WND1 | DAWSON | WIND-O | WEST | 2015 | 105.6
586 | MESQUITE CREEK WIND 2 |  | MESQCRK_WND2 | DAWSON | WIND-O | WEST | 2015 | 105.6
587 | NIELS BOHR WIND A (BEARKAT WIND A) |  | NBOHR_UNIT1 | GLASSCOCK | WIND-O | WEST | 2018 | 196.6
588 | NOTREES WIND 1 |  | NWF_NWF1 | WINKLER | WIND-O | WEST | 2009 | 92.6
589 | NOTREES WIND 2 |  | NWF_NWF2 | WINKLER | WIND-O | WEST | 2009 | 60
590 | OCOTILLO WIND |  | OWF_OWF | HOWARD | WIND-O | WEST | 2008 | 58.8
591 | PANTHER CREEK WIND 1 |  | PC_NORTH_PANTHER1 | HOWARD | WIND-O | WEST | 2008 | 142.5
592 | PANTHER CREEK WIND 2 |  | PC_SOUTH_PANTHER2 | HOWARD | WIND-O | WEST | 2019 | 115.5
593 | PANTHER CREEK WIND 3 | 21INR0449 | PC_SOUTH_PANTHER3 | HOWARD | WIND-O | WEST | 2009 | 199.5
594 | PECOS WIND 1 (WOODWARD) |  | WOODWRD1_WOODWRD1 | PECOS | WIND-O | WEST | 2001 | 90
595 | PECOS WIND 2 (WOODWARD) |  | WOODWRD2_WOODWRD2 | PECOS | WIND-O | WEST | 2001 | 86
596 | PYRON WIND 1 |  | PYR_PYRON1 | NOLAN | WIND-O | WEST | 2008 | 121.5
597 | PYRON WIND 2 |  | PYR_PYRON2 | NOLAN | WIND-O | WEST | 2008 | 127.5
598 | RANCHERO WIND |  | RANCHERO_UNIT1 | CROCKETT | WIND-O | WEST | 2020 | 150
599 | RANCHERO WIND |  | RANCHERO_UNIT2 | CROCKETT | WIND-O | WEST | 2020 | 150
600 | RATTLESNAKE I WIND ENERGY CENTER G1 |  | RSNAKE_G1 | GLASSCOCK | WIND-O | WEST | 2015 | 104.3
601 | RATTLESNAKE I WIND ENERGY CENTER G2 |  | RSNAKE_G2 | GLASSCOCK | WIND-O | WEST | 2015 | 103
602 | RED CANYON WIND |  | RDCANYON_RDCNY1 | BORDEN | WIND-O | WEST | 2006 | 89.6
603 | ROCK SPRINGS VAL VERDE WIND (FERMI) 1 |  | FERMI_WIND1 | VAL VERDE | WIND-O | WEST | 2017 | 121.9
604 | ROCK SPRINGS VAL VERDE WIND (FERMI) 2 |  | FERMI_WIND2 | VAL VERDE | WIND-O | WEST | 2017 | 27.4
605 | ROSCOE WIND |  | TKWSW1_ROSCOE | NOLAN | WIND-O | WEST | 2008 | 114
606 | ROSCOE WIND 2A |  | TKWSW1_ROSCOE2A | NOLAN | WIND-O | WEST | 2008 | 95
607 | RTS WIND |  | RTS_U1 | MCCULLOCH | WIND-O | SOUTH | 2018 | 160
608 | SAND BLUFF WIND | 20INR0296 | MCDLD_SBW1 | GLASSCOCK | WIND-O | WEST | 2008 | 90
609 | SENDERO WIND ENERGY |  | EXGNSND_WIND_1 | JIM HOGG | WIND-O | SOUTH | 2015 | 76
610 | SEYMOUR HILLS WIND (S_HILLS WIND) |  | S_HILLS_UNIT1 | BAYLOR | WIND-O | WEST | 2019 | 30.2
611 | SENATE WIND |  | SENATEWD_UNIT1 | JACK | WIND-O | NORTH | 2012 | 150
612 | SHANNON WIND |  | SHANNONW_UNIT_1 | CLAY | WIND-O | WEST | 2015 | 204.1
613 | SHERBINO 1 WIND | 19INR0120 | KEO_KEO_SM1 | PECOS | WIND-O | WEST | 2008 | 150
614 | SHERBINO 2 WIND | 19INR0120 | KEO_SHRBINO2 | PECOS | WIND-O | WEST | 2020 | 132
615 | SILVER STAR WIND | 18INR0064 | FLTCK_SSI | ERATH | WIND-O | NORTH | 2008 | 52.8
616 | SNYDER WIND | 20INR0257 | ENAS_ENA1 | SCURRY | WIND-O | WEST | 2007 | 63
617 | SOUTH TRENT WIND |  | STWF_T1 | NOLAN | WIND-O | WEST | 2008 | 98.2
618 | STANTON WIND ENERGY |  | SWEC_G1 | MARTIN | WIND-O | WEST | 2008 | 120
619 | STEPHENS RANCH WIND 1 |  | SRWE1_UNIT1 | BORDEN | WIND-O | WEST | 2014 | 211.2
620 | STEPHENS RANCH WIND 2 |  | SRWE1_SRWE2 | BORDEN | WIND-O | WEST | 2015 | 164.7
621 | SWEETWATER WIND 1 | 18INR0073 | SWEETWND_WND1 | NOLAN | WIND-O | WEST | 2003 | 42.5
622 | SWEETWATER WIND 2A | 17INR0068 | SWEETWN2_WND24 | NOLAN | WIND-O | WEST | 2006 | 16.8
623 | SWEETWATER WIND 2B | 17INR0068 | SWEETWN2_WND2 | NOLAN | WIND-O | WEST | 2004 | 110.8
624 | SWEETWATER WIND 3A |  | SWEETWN3_WND3A | NOLAN | WIND-O | WEST | 2011 | 33.6
625 | SWEETWATER WIND 3B |  | SWEETWN3_WND3B | NOLAN | WIND-O | WEST | 2011 | 118.6
626 | SWEETWATER WIND 4-5 |  | SWEETWN5_WND5 | NOLAN | WIND-O | WEST | 2007 | 85
627 | SWEETWATER WIND 4-4B |  | SWEETWN4_WND4B | NOLAN | WIND-O | WEST | 2007 | 112
628 | SWEETWATER WIND 4-4A |  | SWEETWN4_WND4A | NOLAN | WIND-O | WEST | 2007 | 125
629 | TAHOKA WIND 1 |  | TAHOKA_UNIT_1 | LYNN | WIND-O | WEST | 2019 | 150
630 | TAHOKA WIND 2 |  | TAHOKA_UNIT_2 | LYNN | WIND-O | WEST | 2019 | 150
631 | TEXAS BIG SPRING WIND A |  | SGMTN_SIGNALMT | HOWARD | WIND-O | WEST | 1999 | 27.7
632 | TEXAS BIG SPRING WIND B |  | SGMTN_SIGNALM2 | HOWARD | WIND-O | WEST | 1999 | 6.6
633 | TORRECILLAS WIND 1 |  | TORR_UNIT1_25 | WEBB | WIND-O | SOUTH | 2019 | 150
634 | TORRECILLAS WIND 2 |  | TORR_UNIT2_23 | WEBB | WIND-O | SOUTH | 2019 | 23
635 | TORRECILLAS WIND 3 |  | TORR_UNIT2_25 | WEBB | WIND-O | SOUTH | 2019 | 127.5
636 | TRENT WIND | 17INR0069 | TRENT_TRENT | NOLAN | WIND-O | WEST | 2001 | 150
637 | TRINITY HILLS WIND 1 | 20INR0019 | TRINITY_TH1_BUS1 | ARCHER | WIND-O | WEST | 2012 | 103.4
638 | TRINITY HILLS WIND 2 | 20INR0019 | TRINITY_TH1_BUS2 | ARCHER | WIND-O | WEST | 2012 | 94.6
639 | TURKEY TRACK WIND |  | TTWEC_G1 | NOLAN | WIND-O | WEST | 2008 | 169.5
640 | TYLER BLUFF WIND |  | TYLRWIND_UNIT1 | COOKE | WIND-O | NORTH | 2017 | 125.6
641 | WHITETAIL WIND |  | EXGNWTL_WIND_1 | WEBB | WIND-O | SOUTH | 2012 | 92.3
642 | WINDTHORST 2 WIND |  | WNDTHST2_UNIT1 | ARCHER | WIND-O | WEST | 2014 | 67.6
643 | WKN MOZART WIND |  | MOZART_WIND_1 | KENT | WIND-O | WEST | 2012 | 30
644 | WILLOW SPRINGS WIND A |  | SALVTION_UNIT1 | HASKELL | WIND-O | WEST | 2017 | 125
645 | WILLOW SPRINGS WIND B |  | SALVTION_UNIT2 | HASKELL | WIND-O | WEST | 2017 | 125
646 | WILSON RANCH (INFINITY LIVE OAK WIND) |  | WL_RANCH_UNIT1 | SCHLEICHER | WIND-O | WEST | 2020 | 199.5
647 | WOLF RIDGE WIND | 21INR0511 | WHTTAIL_WR1 | COOKE | WIND-O | NORTH | 2008 | 112.5
648 | TSTC WEST TEXAS WIND |  | DG_ROSC2_1UNIT | NOLAN | WIND-O | WEST | 2008 | 2
649 | Operational Capacity Total (Wind) | [6 empty] | 24962.4
650
651 | Operational Wind Capacity Sub-total (Coastal Counties) |  | WIND_OPERATIONAL_C |  |  |  |  | 3441.6
652 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PEAK_PCT_C | % |  |  |  | 64
653
654 | Operational Wind Capacity Sub-total (Panhandle Counties) |  | WIND_OPERATIONAL_P |  |  |  |  | 4408.7
655 | Wind Peak Average Capacity Percentage (Panhandle) |  | WIND_PEAK_PCT_P | % |  |  |  | 35
656
657 | Operational Wind Capacity Sub-total (Other Counties) |  | WIND_OPERATIONAL_O |  |  |  |  | 17112.1
658 | Wind Peak Average Capacity Percentage (Other) |  | WIND_PEAK_PCT_O | % |  |  |  | 34
659
660 | Operational Resources (Solar)
661 | ACACIA SOLAR |  | ACACIA_UNIT_1 | PRESIDIO | SOLAR | WEST | 2012 | 10
662 | BHE SOLAR PEARL PROJECT (SIRIUS 2) |  | SIRIUS_UNIT2 | PECOS | SOLAR | WEST | 2017 | 49.1
663 | BLUEBELL SOLAR (CAPRICORN RIDGE SOLAR) |  | CAPRIDG4_BB_PV | STERLING | SOLAR | WEST | 2019 | 30
664 | BNB LAMESA SOLAR (PHASE I) |  | LMESASLR_UNIT1 | DAWSON | SOLAR | WEST | 2018 | 101.6
665 | BNB LAMESA SOLAR (PHASE II) |  | LMESASLR_IVORY | DAWSON | SOLAR | WEST | 2018 | 50
666 | CASTLE GAP SOLAR |  | CASL_GAP_UNIT1 | UPTON | SOLAR | WEST | 2018 | 180
667 | FOWLER RANCH |  | FWLR_SLR_UNIT1 | CRANE | SOLAR | WEST | 2020 | 150
668 | FS BARILLA SOLAR-PECOS |  | HOVEY_UNIT1 | PECOS | SOLAR | WEST | 2015 | 22
669 | FS EAST PECOS SOLAR |  | BOOTLEG_UNIT1 | PECOS | SOLAR | WEST | 2017 | 121.1
670 | HOLSTEIN SOLAR 1 |  | HOLSTEIN_SOLAR1 | NOLAN | SOLAR | WEST | 2020 | 102.2
671 | HOLSTEIN SOLAR 2 |  | HOLSTEIN_SOLAR2 | NOLAN | SOLAR | WEST | 2020 | 102.3
672 | LAPETUS SOLAR |  | LAPETUS_UNIT_1 | ANDREWS | SOLAR | WEST | 2020 | 100.7
673 | OBERON SOLAR |  | OBERON_UNIT_1 | ECTOR | SOLAR | WEST | 2020 | 180
674 | OCI ALAMO 1 SOLAR |  | OCI_ALM1_UNIT1 | BEXAR | SOLAR | SOUTH | 2013 | 39.2
675 | OCI ALAMO 4 SOLAR-BRACKETVILLE |  | ECLIPSE_UNIT1 | KINNEY | SOLAR | SOUTH | 2014 | 37.6
676 | OCI ALAMO 5 (DOWNIE RANCH) |  | HELIOS_UNIT1 | UVALDE | SOLAR | SOUTH | 2015 | 100
677 | OCI ALAMO 6 (SIRIUS/WEST TEXAS) |  | SIRIUS_UNIT1 | PECOS | SOLAR | WEST | 2017 | 110.2
678 | OCI ALAMO 7 (PAINT CREEK) |  | SOLARA_UNIT1 | HASKELL | SOLAR | WEST | 2016 | 112
679 | PHOEBE SOLAR 1 |  | PHOEBE_UNIT1 | WINKLER | SOLAR | WEST | 2019 | 125.1
680 | PHOEBE SOLAR 2 |  | PHOEBE_UNIT2 | WINKLER | SOLAR | WEST | 2019 | 128.1
681 | PROSPERO SOLAR 1 |  | PROSPERO_UNIT1 | ANDREWS | SOLAR | WEST | 2020 | 153.6
682 | PROSPERO SOLAR 2 |  | PROSPERO_UNIT2 | ANDREWS | SOLAR | WEST | 2020 | 150
683 | QUEEN SOLAR PHASE I |  | QUEEN_SL_SOLAR1 | UPTON | SOLAR | WEST | 2020 | 102.5
684 | QUEEN SOLAR PHASE I |  | QUEEN_SL_SOLAR2 | UPTON | SOLAR | WEST | 2020 | 102.5
685 | QUEEN SOLAR PHASE II |  | QUEEEN_SL_SOLAR3 | UPTON | SOLAR | WEST | 2020 | 97.5
686 | QUEEN SOLAR PHASE II |  | QUEEEN_SL_SOLAR4 | UPTON | SOLAR | WEST | 2020 | 107.5
687 | RAMBLER SOLAR |  | RAMBLER_UNIT1 | TOM GREEN | SOLAR | WEST | 2020 | 200
688 | RE ROSEROCK SOLAR 1 |  | REROCK_UNIT1 | PECOS | SOLAR | WEST | 2016 | 78.8
689 | RE ROSEROCK SOLAR 2 |  | REROCK_UNIT2 | PECOS | SOLAR | WEST | 2016 | 78.8
690 | RIGGINS (SE BUCKTHORN WESTEX SOLAR) |  | RIGGINS_UNIT1 | PECOS | SOLAR | WEST | 2018 | 150
691 | SOLAIREHOLMAN 1 |  | LASSO_UNIT1 | BREWSTER | SOLAR | WEST | 2018 | 50
692 | SP-TX-12-PHASE B |  | SPTX12B_UNIT1 | UPTON | SOLAR | WEST | 2017 | 157.5
693 | WAYMARK SOLAR |  | WAYMARK_UNIT1 | UPTON | SOLAR | WEST | 2018 | 182
694 | WEBBERVILLE SOLAR |  | WEBBER_S_WSP1 | TRAVIS | SOLAR | SOUTH | 2011 | 26.7
695 | WEST OF PECOS SOLAR |  | W_PECOS_UNIT1 | REEVES | SOLAR | WEST | 2019 | 101
696 | ALEXIS SOLAR |  | DG_ALEXIS_ALEXIS | BROOKS | SOLAR | SOUTH | 2019 | 10
697 | BECK 1 |  | DG_CECSOLAR_DG_BECK1 | BEXAR | SOLAR | SOUTH | 2016 | 1
698 | BLUE WING 1 SOLAR |  | DG_BROOK_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.6
699 | BLUE WING 2 SOLAR |  | DG_ELMEN_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.3
700 | BOVINE SOLAR LLC |  | DG_BOVINE_BOVINE | AUSTIN | SOLAR | SOUTH | 2018 | 5
701 | BOVINE SOLAR LLC |  | DG_BOVINE2_BOVINE2 | AUSTIN | SOLAR | SOUTH | 2018 | 5
702 | BRONSON SOLAR I |  | DG_BRNSN_BRNSN | FORT BEND | SOLAR | HOUSTON | 2018 | 5
703 | BRONSON SOLAR II |  | DG_BRNSN2_BRNSN2 | FORT BEND | SOLAR | HOUSTON | 2018 | 5
704 | CASCADE SOLAR I |  | DG_CASCADE_CASCADE | WHARTON | SOLAR | SOUTH | 2018 | 5
705 | CASCADE SOLAR II |  | DG_CASCADE2_CASCADE2 | WHARTON | SOLAR | SOUTH | 2018 | 5
706 | CATAN SOLAR |  | DG_CS10_CATAN | KARNES | SOLAR | SOUTH | 2020 | 10
707 | CHISUM SOLAR |  | DG_CHISUM_CHISUM | LAMAR | SOLAR | NORTH | 2018 | 10
708 | COMMERCE_SOLAR |  | DG_ X443PV1_SWRI_PV1 | BEXAR | SOLAR | SOUTH | 2019 | 5
709 | EDDY SOLAR II |  | DG_EDDYII_EDDYII | MCLENNAN | SOLAR | NORTH | 2018 | 10
710 | FIFTH GENERATION SOLAR 1 |  | DG_FIFTHGS1_FGSOLAR1 | TRAVIS | SOLAR | SOUTH | 2016 | 1.6
711 | GRIFFIN SOLAR |  | DG_GRIFFIN_GRIFFIN | MCLENNAN | SOLAR | NORTH | 2019 | 5
712 | HIGHWAY 56 |  | DG_HWY56_HWY56 | GRAYSON | SOLAR | NORTH | 2017 | 5.3
713 | HM SEALY SOLAR 1 |  | DG_SEALY_1UNIT | AUSTIN | SOLAR | SOUTH | 2015 | 1.6
714 | LAMPWICK SOLAR |  | DG_LAMPWICK_LAMPWICK | MENARD | SOLAR | WEST | 2019 | 7.5
715 | LEON |  | DG_LEON_LEON | HUNT | SOLAR | NORTH | 2017 | 10
716 | MARLIN |  | DG_MARLIN_MARLIN | FALLS | SOLAR | NORTH | 2017 | 5.3
717 | MARS SOLAR (DG) |  | DG_MARS_MARS | WEBB | SOLAR | SOUTH | 2019 | 10
718 | NORTH GAINESVILLE |  | DG_NGNSVL_NGAINESV | COOKE | SOLAR | NORTH | 2017 | 5.2
719 | OCI ALAMO 2 SOLAR-ST. HEDWIG |  | DG_STHWG_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 4.4
720 | OCI ALAMO 3-WALZEM SOLAR |  | DG_WALZM_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 5.5
721 | POWERFIN KINGSBERY |  | DG_PFK_PFKPV | TRAVIS | SOLAR | SOUTH | 2017 | 2.6
722 | RENEWABLE ENERGY ALTERNATIVES-CCS1 |  | DG_COSERVSS_CSS1 | DENTON | SOLAR | NORTH | 2015 | 2
723 | STERLING |  | DG_STRLING_STRLING | HUNT | SOLAR | NORTH | 2018 | 10
724 | SUNEDISON RABEL ROAD SOLAR |  | DG_VALL1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9
725 | SUNEDISON VALLEY ROAD SOLAR |  | DG_VALL2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9
726 | SUNEDISON CPS3 SOMERSET 1 SOLAR |  | DG_SOME1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5.6
727 | SUNEDISON SOMERSET 2 SOLAR |  | DG_SOME2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5
728 | WALNUT SPRINGS |  | DG_WLNTSPRG_1UNIT | BOSQUE | SOLAR | NORTH | 2016 | 10
729 | WEST MOORE II |  | DG_WMOOREII_WMOOREII | GRAYSON | SOLAR | NORTH | 2018 | 5
730 | WHITESBORO |  | DG_WBORO_WHTSBORO | GRAYSON | SOLAR | NORTH | 2017 | 5
731 | WHITESBORO II |  | DG_WBOROII_WHBOROII | GRAYSON | SOLAR | NORTH | 2017 | 5
732 | WHITEWRIGHT |  | DG_WHTRT_WHTRGHT | FANNIN | SOLAR | NORTH | 2017 | 10
733 | WHITNEY SOLAR |  | DG_WHITNEY_SOLAR1 | BOSQUE | SOLAR | NORTH | 2017 | 10
734 | YELLOW JACKET SOLAR |  | DG_YLWJACKET_YLWJACKET | BOSQUE | SOLAR | NORTH | 2018 | 5
735 | Operational Capacity Total (Solar) | [6 empty] | 3836.9
736 | Solar Peak Average Capacity Percentage |  | SOLAR_PEAK_PCT | % |  |  |  | 65
737
738 | Operational Resources (Storage)
739 | BLUE SUMMIT BATTERY |  | BLSUMMIT_BATTERY | WILBARGER | STORAGE | WEST | 2017 | 30
740 | BRP ALVIN (DGR) |  | BRPALVIN_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2020 | 10
741 | BRP ODESSA SW (DGR) |  | BRPODESA_UNIT1 | ECTOR | STORAGE | WEST | 2020 | 10
742 | CASTLE GAP BATTERY |  | CASL_GAP_BATTERY1 | UPTON | STORAGE | WEST | 2019 | 9.9
743 | COMMERCE ST ESS (DGR) |  | X443ESS1_SWRI | BEXAR | STORAGE | SOUTH | 2020 | 10
744 | FLAT TOP BATTERY (DGR) |  | FLTBES_BESS1 | REEVES | STORAGE | WEST | 2020 | 9.9
745 | INADALE ESS |  | INDL_ESS | NOLAN | STORAGE | WEST | 2018 | 9.9
746 | JOHNSON CITY BESS (DGR) |  | JC_BAT_UNIT_1 | BLANCO | STORAGE | SOUTH | 2020 | 2.3
747 | NOTREES BATTERY FACILITY |  | NWF_NBS | WINKLER | STORAGE | WEST | 2013 | 33.7
748 | OCI ALAMO 1 |  | OCI_ALM1_ASTRO1 | BEXAR | STORAGE | SOUTH | 2016 | 1
749 | PORT LAVACA BATTERY (DGR) |  | PTLBES_BESS1 | CALHOUN | STORAGE | COASTAL | 2019 | 9.9
750 | PROSPECT STORAGE (DGR) |  | WCOLLDG_BSS_U1 | BRAZORIA | STORAGE | COASTAL | 2019 | 9.9
751 | PYRON ESS |  | PYR_ESS | SCURRY | STORAGE | WEST | 2018 | 9.9
752 | RABBIT HILL ENERGY STORAGE PROJECT (DGR) |  | RHESS2_ESS_1 | WILLIAMSON | STORAGE | SOUTH | 2020 | 9.9
753 | TOS BATTERY STORAGE (DGR) |  | TOSBATT_UNIT1 | MIDLAND | STORAGE | WEST | 2017 | 2
754 | WORSHAM BATTERY (DGR) |  | WRSBES_BESS1 | REEVES | STORAGE | WEST | 2020 | 9.9
755 | KINGSBERY ENERGY STORAGE SYSTEM |  | DG_KB_ESS_KB_ESS | TRAVIS | STORAGE | SOUTH | 2017 | 1.5
756 | MU ENERGY STORAGE SYSTEM |  | DG_MU_ESS_MU_ESS | TRAVIS | STORAGE | SOUTH | 2018 | 1.5
757 | YOUNICOS FACILITY |  | DG_YOUNICOS_YINC1_1 | TRAVIS | STORAGE | SOUTH | 2015 | 2
758 | Operational Capacity Total (Storage) | [6 empty] | 183.2
759 | Storage Peak Average Capacity Percentage |  | STORAGE_PEAK_PCT | % |  |  |  | 0
760
761 | Reliability Must-Run (RMR) Capacity |  | RMR_CAP_CONT |  | GAS |  |  | 0
762
763 | Capacity Pending Retirement |  | PENDRETIRE_CAP |  |  |  |  | 0
764
765 | Non-Synchronous Tie Resources
766 | EAST TIE |  | DC_E | FANNIN | OTHER | NORTH |  | 600
767 | NORTH TIE |  | DC_N | WILBARGER | OTHER | WEST |  | 220
768 | LAREDO VFT TIE |  | DC_L | WEBB | OTHER | SOUTH |  | 100
769 | SHARYLAND RAILROAD TIE |  | DC_R | HIDALGO | OTHER | SOUTH |  | 300
770 | Non-Synchronous Ties Total | [6 empty] | 1220
771 | Non-Synchronous Ties Peak Average Capacity Percentage |  | DCTIE_PEAK_PCT | % |  |  |  | 68.65
772
773 | Planned Thermal Resources with Executed SGIA, Air Permit, GHG Permit and Proof of Adequate Water Supplies
774 | AIR PRODUCTS GCA | 21INR0012 |  | GALVESTON | GAS-ST | HOUSTON | 2022 | 0
775 | MIRAGE | 17INR0022 |  | HARRIS | GAS-GT | HOUSTON | 2021 | 0
776 | PROENERGY SOUTH 1 (PES1) | 20INR0206 |  | HARRIS | GAS-GT | HOUSTON | 2020 | 306
777 | TOPAZ POWER PLANT | 20INR0231 |  | GALVESTON | GAS-GT | HOUSTON | 2021 | 0
778 | Planned Capacity Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 306
779
780 | Planned Wind Resources with Executed SGIA
781 | CHALUPA WIND | 20INR0042 |  | CAMERON | WIND-C | COASTAL | 2020 | 174
782 | CRANEL WIND | 19INR0112 |  | REFUGIO | WIND-C | COASTAL | 2020 | 220
783 | EAST RAYMOND WIND | 18INR0059 |  | WILLACY | WIND-C | COASTAL | 2021 | 201.6
784 | EL ALGODON ALTO W | 15INR0034 |  | SAN PATRICIO | WIND-C | COASTAL | 2021 | 0
785 | ESPIRITU WIND | 17INR0031 |  | CAMERON | WIND-C | COASTAL | 2020 | 25.2
786 | LAS MAJADAS WIND | 17INR0035 |  | WILLACY | WIND-C | COASTAL | 2020 | 272.6
787 | MONTE ALTO I | 19INR0022 |  | WILLACY | WIND-C | COASTAL | 2021 | 0
788 | PALMAS ALTAS WIND | 17INR0037 |  | CAMERON | WIND-C | COASTAL | 2020 | 144.9
789 | SHAFFER (PATRIOT WIND/PETRONILLA) | 11INR0062 |  | NUECES | WIND-C | COASTAL | 2020 | 226
790 | WEST RAYMOND (EL TRUENO) WIND | 20INR0088 |  | WILLACY | WIND-C | COASTAL | 2021 | 0
791 | CAROL WIND | 20INR0217 |  | POTTER | WIND-P | PANHANDLE | 2021 | 0
792 | HART WIND | 16INR0033 |  | CASTRO | WIND-P | PANHANDLE | 2022 | 0
793 | AJAX WIND | 20INR0142 |  | WILBARGER | WIND-O | WEST | 2021 | 0
794 | APOGEE WIND | 21INR0467 |  | HASKELL | WIND-O | WEST | 2021 | 0
795 | AQUILLA LAKE WIND | 19INR0145 |  | HILL | WIND-O | NORTH | 2021 | 0
796 | AQUILLA LAKE 2 WIND | 20INR0256 |  | HILL | WIND-O | NORTH | 2021 | 0
797 | AVIATOR WIND | 19INR0156 |  | COKE | WIND-O | WEST | 2020 | 525
798 | BAIRD NORTH WIND | 20INR0083 |  | CALLAHAN | WIND-O | WEST | 2021 | 0
799 | BAIRD NORTH II WIND | 21INR0498 |  | CALLAHAN | WIND-O | WEST | 2021 | 0
800 | BARROW RANCH (JUMBO HILL WIND) | 18INR0038 |  | ANDREWS | WIND-O | WEST | 2020 | 160
801 | BIG SAMPSON WIND | 16INR0104 |  | CROCKETT | WIND-O | WEST | 2022 | 0
802 | BLACKJACK CREEK WIND | 20INR0068 |  | BEE | WIND-O | SOUTH | 2021 | 0
803 | CACTUS FLATS WIND | 16INR0086 |  | CONCHO | WIND-O | WEST | 2020 | 148.4
804 | CANYON WIND | 18INR0030 |  | SCURRY | WIND-O | WEST | 2022 | 0
805 | COYOTE WIND | 17INR0027b |  | SCURRY | WIND-O | WEST | 2020 | 242.6
806 | EDMONDSON RANCH WIND | 18INR0043 |  | GLASSCOCK | WIND-O | WEST | 2021 | 0
807 | FOXTROT WIND | 20INR0129 |  | KARNES | WIND-O | SOUTH | 2022 | 0
808 | GRIFFIN TRAIL WIND | 20INR0052 |  | KNOX | WIND-O | WEST | 2021 | 0
809 | HARALD (BEARKAT WIND B) | 15INR0064b |  | GLASSCOCK | WIND-O | WEST | 2020 | 162.1
810 | HIDALGO II WIND | 19INR0053 |  | HIDALGO | WIND-O | SOUTH | 2020 | 51
811 | HIGH LONESOME W | 19INR0038 |  | CROCKETT | WIND-O | WEST | 2021 | 449.5
812 | HIGH LONESOME WIND PHASE II | 20INR0262 |  | CROCKETT | WIND-O | WEST | 2021 | 50.6
813 | HUTT WIND | 21INR0005 |  | MIDLAND | WIND-O | WEST | 2021 | 0
814 | KONTIKI 1 WIND (ERIK) | 19INR0099a |  | GLASSCOCK | WIND-O | WEST | 2023 | 0
815 | KONTIKI 2 WIND (ERNEST) | 19INR0099b |  | GLASSCOCK | WIND-O | WEST | 2023 | 0
816 | VENADO WIND | 16INR0111 |  | STARR | WIND-O | SOUTH | 2020 | 201.6
817 | LORAINE WINDPARK PHASE III | 18INR0068 |  | MITCHELL | WIND-O | WEST | 2022 | 0
818 | MARYNEAL WINDPOWER | 18INR0031 |  | NOLAN | WIND-O | WEST | 2021 | 0
819 | MAVERICK CREEK I | 20INR0045 |  | CONCHO | WIND-O | WEST | 2020 | 373.2
820 | MAVERICK CREEK II | 20INR0046 |  | CONCHO | WIND-O | WEST | 2021 | 0
821 | MESTENO WIND | 16INR0081 |  | STARR | WIND-O | SOUTH | 2020 | 201.6
822 | MONARCH CREEK WIND | 21INR0263 |  | THROCKMORTON | WIND-O | WEST | 2021 | 0
823 | OVEJA WIND | 18INR0033 |  | IRION | WIND-O | WEST | 2020 | 300
824 | PRAIRIE HILL WIND | 19INR0100 |  | MCLENNAN | WIND-O | NORTH | 2020 | 300
825 | PRIDDY WIND | 16INR0085 |  | MILLS | WIND-O | NORTH | 2021 | 0
826 | RELOJ DEL SOL WIND | 17INR0025 |  | ZAPATA | WIND-O | SOUTH | 2021 | 209.4
827 | ROADRUNNER CROSSING WIND 1 | 19INR0117 |  | EASTLAND | WIND-O | NORTH | 2021 | 0
828 | RTS 2 WIND (HEART OF TEXAS WIND) | 18INR0016 |  | MCCULLOCH | WIND-O | SOUTH | 2020 | 179.9
829 | SAGE DRAW WIND | 19INR0163 |  | LYNN | WIND-O | WEST | 2020 | 338
830 | TG EAST WIND | 19INR0052 |  | KNOX | WIND-O | WEST | 2021 | 0
831 | VERA WIND | 19INR0051 |  | KNOX | WIND-O | WEST | 2020 | 208.8
832 | VERA WIND V110 | 20INR0305 |  | KNOX | WIND-O | WEST | 2020 | 34
833 | WHITE MESA WIND | 19INR0128 |  | CROCKETT | WIND-O | WEST | 2021 | 0
834 | WHITEHORSE WIND | 19INR0080 |  | FISHER | WIND-O | WEST | 2020 | 418.9
835 | WILDWIND | 20INR0033 |  | COOKE | WIND-O | NORTH | 2021 | 0
836 | WKN AMADEUS WIND | 14INR0009 |  | FISHER | WIND-O | WEST | 2021 | 250.1
837 | Planned Capacity Total (Wind) | [6 empty] | 6069
838
839 | Planned Wind Capacity Sub-total (Coastal Counties) |  | WIND_PLANNED_C |  |  |  |  | 1264.3
840 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PL_PEAK_PCT_C | % |  |  |  | 64
841
842 | Planned Wind Capacity Sub-total (Panhandle Counties) |  | WIND_PLANNED_P |  |  |  |  | 0
843 | Wind Peak Average Capacity Percentage (Panhandle) |  | WIND_PL_PEAK_PCT_P | % |  |  |  | 35
844
845 | Planned Wind Capacity Sub-total (Other counties) |  | WIND_PLANNED_O |  |  |  |  | 4804.7
846 | Wind Peak Average Capacity Percentage (Other) |  | WIND_PL_PEAK_PCT_O | % |  |  |  | 34
847
848 | Planned Solar Resources with Executed SGIA
849 | 7V SOLAR | 21INR0351 |  | FAYETTE | SOLAR | SOUTH | 2022 | 0
850 | ANSON SOLAR | 19INR0081 |  | JONES | SOLAR | WEST | 2021 | 201.5
851 | ARAGORN SOLAR | 19INR0088 |  | CULBERSON | SOLAR | WEST | 2021 | 0
852 | AZURE SKY SOLAR | 21INR0477 |  | HASKELL | SOLAR | WEST | 2021 | 0
853 | BLUE JAY SOLAR | 19INR0085 |  | GRIMES | SOLAR | NORTH | 2021 | 0
854 | BLUEBELL SOLAR II | 20INR0204 |  | STERLING | SOLAR | WEST | 2020 | 115
855 | BRAVEPOST SOLAR | 20INR0053 |  | TOM GREEN | SOLAR | WEST | 2022 | 0
856 | BRIGHTSIDE SOLAR | 18INR0060 |  | BEE | SOLAR | SOUTH | 2021 | 0
857 | CAROL SOLAR | 21INR0274 |  | POTTER | SOLAR | PANHANDLE | 2021 | 0
858 | CONCHO VALLEY SOLAR | 21INR0384 |  | TOM GREEN | SOLAR | WEST | 2022 | 0
859 | CONIGLIO SOLAR | 20INR0037 |  | FANNIN | SOLAR | NORTH | 2021 | 125.7
860 | CORAZON SOLAR PHASE I | 15INR0044 |  | WEBB | SOLAR | SOUTH | 2021 | 0
861 | CORAZON SOLAR PHASE II | 22INR0257 |  | WEBB | SOLAR | SOUTH | 2022 | 0
862 | COTTONWOOD BAYOU | 19INR0134 |  | BRAZORIA | SOLAR | COASTAL | 2022 | 0
863 | CROWDED STAR SOLAR | 20INR0241 |  | JONES | SOLAR | WEST | 2022 | 0
864 | CROWDED STAR SOLAR II | 22INR0274 |  | JONES | SOLAR | WEST | 2022 | 0
865 | CUTLASS SOLAR | 19INR0131 |  | FORT BEND | SOLAR | HOUSTON | 2022 | 0
866 | DANCIGER SOLAR | 20INR0098 |  | BRAZORIA | SOLAR | COASTAL | 2022 | 0
867 | DANISH FIELDS SOLAR I | 20INR0069 |  | WHARTON | SOLAR | SOUTH | 2022 | 0
868 | DANISH FIELDS SOLAR II | 21INR0016 |  | WHARTON | SOLAR | SOUTH | 2022 | 0
869 | DANISH FIELDS SOLAR III | 21INR0017 |  | WHARTON | SOLAR | SOUTH | 2022 | 0
870 | DELILAH SOLAR 1 | 21INR0221 |  | LAMAR | SOLAR | NORTH | 2021 | 0
871 | DELILAH SOLAR 1A | 21INR0490 |  | LAMAR | SOLAR | NORTH | 2023 | 0
872 | DELILAH SOLAR 1B | 21INR0491 |  | LAMAR | SOLAR | NORTH | 2021 | 0
873 | ELARA SOLAR | 21INR0276 |  | FRIO | SOLAR | SOUTH | 2021 | 0
874 | EMERALD GROVE SOLAR (PECOS SOLAR POWER I) | 15INR0059 |  | PECOS | SOLAR | WEST | 2021 | 0
875 | EUNICE SOLAR | 20INR0219 |  | ANDREWS | SOLAR | WEST | 2021 | 426.7
876 | FIGHTING JAYS SOLAR | 21INR0278 |  | FORT BEND | SOLAR | HOUSTON | 2022 | 0
877 | FORT BEND SOLAR | 18INR0053 |  | FORT BEND | SOLAR | HOUSTON | 2021 | 0
878 | GALLOWAY 1 SOLAR | 19INR0121 |  | CONCHO | SOLAR | WEST | 2021 | 0
879 | GALLOWAY 2 SOLAR | 21INR0431 |  | CONCHO | SOLAR | WEST | 2022 | 0
880 | GARNET SOLAR | 20INR0021 |  | WILLIAMSON | SOLAR | SOUTH | 2020 | 20
881 | GREASEWOOD SOLAR | 19INR0034 |  | PECOS | SOLAR | WEST | 2020 | 255
882 | GREEN HOLLY SOLAR | 21INR0021 |  | DAWSON | SOLAR | WEST | 2022 | 0
883 | HORIZON SOLAR | 21INR0261 |  | FRIO | SOLAR | SOUTH | 2022 | 0
884 | HOVEY (BARILLA SOLAR 1B) | 12INR0059b |  | PECOS | SOLAR | WEST | 2020 | 7.4
885 | IMPACT SOLAR | 19INR0151 |  | LAMAR | SOLAR | NORTH | 2020 | 198.6
886 | INDIGO SOLAR | 21INR0031 |  | FISHER | SOLAR | WEST | 2021 | 0
887 | IP TITAN | 20INR0032 |  | CULBERSON | SOLAR | WEST | 2021 | 0
888 | JUNO SOLAR PHASE I | 21INR0026 |  | BORDEN | SOLAR | WEST | 2021 | 0
889 | JUNO SOLAR PHASE II | 21INR0501 |  | BORDEN | SOLAR | WEST | 2021 | 0
890 | KELLAM SOLAR | 20INR0261 |  | VAN ZANDT | SOLAR | NORTH | 2020 | 59.8
891 | LILY SOLAR | 19INR0044 |  | KAUFMAN | SOLAR | NORTH | 2021 | 0
892 | LONG DRAW SOLAR | 18INR0055 |  | BORDEN | SOLAR | WEST | 2020 | 226.7
893 | LONG POINT SOLAR | 19INR0042 |  | BRAZORIA | SOLAR | COASTAL | 2021 | 0
894 | MISAE SOLAR | 18INR0045 |  | CHILDRESS | SOLAR | PANHANDLE | 2020 | 240.8
895 | MISAE SOLAR II | 20INR0091 |  | CHILDRESS | SOLAR | PANHANDLE | 2022 | 0
896 | MORROW LAKE SOLAR | 19INR0155 |  | FRIO | SOLAR | SOUTH | 2022 | 0
897 | MUSTANG CREEK SOLAR | 18INR0050 |  | JACKSON | SOLAR | SOUTH | 2022 | 0
898 | MYRTLE SOLAR | 19INR0041 |  | BRAZORIA | SOLAR | COASTAL | 2022 | 0
899 | NAZARETH SOLAR | 16INR0049 |  | CASTRO | SOLAR | PANHANDLE | 2023 | 0
900 | NOBLE SOLAR | 20INR0214 |  | DENTON | SOLAR | NORTH | 2022 | 0
901 | NORTON SOLAR | 19INR0035 |  | RUNNELS | SOLAR | WEST | 2022 | 0
902 | OLD 300 SOLAR CENTER | 21INR0406 |  | FORT BEND | SOLAR | HOUSTON | 2021 | 0
903 | OLD HICKORY SOLAR | 20INR0236 |  | JACKSON | SOLAR | SOUTH | 2022 | 0
904 | OXY SOLAR | 19INR0184 |  | ECTOR | SOLAR | WEST | 2020 | 16.2
905 | PFLUGERVILLE SOLAR | 15INR0090 |  | TRAVIS | SOLAR | SOUTH | 2021 | 0
906 | PHOENIX SOLAR | 19INR0091 |  | FANNIN | SOLAR | NORTH | 2021 | 0
907 | PINE FOREST SOLAR | 20INR0203 |  | HOPKINS | SOLAR | NORTH | 2022 | 0
908 | PROSPERO SOLAR II | 21INR0229 |  | ANDREWS | SOLAR | WEST | 2021 | 0
909 | RAMSEY SOLAR | 20INR0130 |  | WHARTON | SOLAR | SOUTH | 2021 | 0
910 | RAYOS DEL SOL | 19INR0045 |  | CAMERON | SOLAR | COASTAL | 2021 | 0
911 | RE MAPLEWOOD 2A SOLAR | 17INR0020a |  | PECOS | SOLAR | WEST | 2021 | 0
912 | RE MAPLEWOOD 2B SOLAR | 17INR0020b |  | PECOS | SOLAR | WEST | 2021 | 0
913 | RED HOLLY SOLAR | 21INR0022 |  | DAWSON | SOLAR | WEST | 2022 | 0
914 | RED-TAILED HAWK SOLAR | 21INR0389 |  | WHARTON | SOLAR | SOUTH | 2021 | 0
915 | RIPPEY SOLAR | 20INR0031 |  | COOKE | SOLAR | NORTH | 2020 | 59.8
916 | RODEO SOLAR | 19INR0103 |  | ANDREWS | SOLAR | WEST | 2021 | 0
917 | RUETER SOLAR | 20INR0202 |  | BOSQUE | SOLAR | NORTH | 2022 | 0
918 | SBRANCH SOLAR PROJECT | 22INR0205 |  | WHARTON | SOLAR | SOUTH | 2022 | 0
919 | SECOND DIVISION SOLAR | 20INR0248 |  | BRAZORIA | SOLAR | COASTAL | 2022 | 0
920 | SHAKES SOLAR | 19INR0073 |  | ZAVALA | SOLAR | SOUTH | 2021 | 0
921 | SODA LAKE SOLAR 2 | 20INR0143 |  | CRANE | SOLAR | WEST | 2022 | 0
922 | SOLEMIO | 19INR0093 |  | HOPKINS | SOLAR | NORTH | 2021 | 0
923 | SPARTA SOLAR | 22INR0352 |  | BEE | SOLAR | SOUTH | 2022 | 0
924 | STARR SOLAR RANCH | 20INR0216 |  | STARR | SOLAR | SOUTH | 2021 | 0
925 | STRATEGIC SOLAR 1 | 20INR0081 |  | ELLIS | SOLAR | NORTH | 2021 | 0
926 | SUN VALLEY | 19INR0169 |  | HILL | SOLAR | NORTH | 2022 | 0
927 | TAYGETE II SOLAR | 21INR0233 |  | PECOS | SOLAR | WEST | 2021 | 0
928 | TAYGETE SOLAR | 20INR0054 |  | PECOS | SOLAR | WEST | 2021 | 255.1
929 | TEXAS SOLAR NOVA | 19INR0001 |  | KENT | SOLAR | WEST | 2022 | 0
930 | TIMBERWOLF POI A | 20INR0226 |  | UPTON | SOLAR | WEST | 2022 | 0
931 | TRES BAHIAS SOLAR | 20INR0266 |  | CALHOUN | SOLAR | COASTAL | 2021 | 0
932 | TYSON NICK SOLAR | 20INR0222 |  | LAMAR | SOLAR | NORTH | 2021 | 0
933 | UPTON SOLAR | 16INR0114 |  | UPTON | SOLAR | WEST | 2021 | 0
934 | VANCOURT SOLAR | 21INR0213 |  | CAMERON | SOLAR | COASTAL | 2021 | 0
935 | VISION SOLAR 1 | 20INR0082 |  | NAVARRO | SOLAR | NORTH | 2021 | 0
936 | WAGYU SOLAR | 18INR0062 |  | BRAZORIA | SOLAR | COASTAL | 2020 | 120
937 | WESTORIA SOLAR | 20INR0101 |  | BRAZORIA | SOLAR | COASTAL | 2021 | 0
938 | Planned Capacity Total (Solar) | [6 empty] | 2328.3
939 | Solar Peak Average Capacity Percentage |  | SOLAR_PL_PEAK_PCT | % |  |  |  | 65
940
941 | Planned Storage Resources with Executed SGIA
942 | AZURE SKY BESS | 21INR0476 |  | HASKELL | STORAGE | WEST | 2021 | 0
943 | BAT CAVE | 21INR0365 |  | MASON | STORAGE | SOUTH | 2021 | 0
944 | CHISHOLM GRID | 20INR0089 |  | TARRANT | STORAGE | NORTH | 2021 | 0
945 | CROSSETT POWER BATT | 21INR0510 |  | CRANE | STORAGE | WEST | 2021 | 0
946 | EUNICE STORAGE | 20INR0220 |  | ANDREWS | STORAGE | WEST | 2021 | 40.3
947 | GAMBIT | 21INR0364 |  | BRAZORIA | STORAGE | COASTAL | 2021 | 0
948 | GREEN HOLLY STORAGE | 21INR0029 |  | DAWSON | STORAGE | WEST | 2021 | 0
949 | HIGH LONESOME BESS | 20INR0280 |  | CROCKETT | STORAGE | WEST | 2022 | 0
950 | IGNACIO GRID | 21INR0522 |  | HIDALGO | STORAGE | SOUTH | 2021 | 0
951 | LILY STORAGE | 20INR0294 |  | KAUFMAN | STORAGE | NORTH | 2021 | 0
952 | MADERO GRID | 21INR0244 |  | HIDALGO | STORAGE | SOUTH | 2021 | 0
953 | NORTH FORK | 20INR0276 |  | WILLIAMSON | STORAGE | SOUTH | 2021 | 0
954 | QUEEN BESS | 20INR0281 |  | UPTON | STORAGE | WEST | 2022 | 0
955 | ROUGHNECK STORAGE | 19INR0176 |  | BRAZORIA | STORAGE | COASTAL | 2021 | 0
956 | SILICON HILL STORAGE | 20INR0291 |  | TRAVIS | STORAGE | SOUTH | 2021 | 0
957 | SP TX-12B BESS | 21INR0357 |  | UPTON | STORAGE | WEST | 2021 | 0
958 | BRP ANGELTON (DGR) |  | BRPANGLE_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2020 | 10
959 | BRP BRAZORIA (DGR) |  | BRP_BRAZ_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2020 | 10
960 | BRP DICKINSON (DGR) |  | BRP_DIKN_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2020 | 10
961 | BRP HEIGHTS (DGR) |  | BRHEIGHT_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2020 | 10
962 | BRP LOOP 463 (DGR) |  | BRP_LOOP_UNIT1 | VICTORIA | STORAGE | SOUTH | 2020 | 10
963 | BRP MAGNOLIA (DGR) |  | BRPMAGNO_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2020 | 10
964 | BRP PUEBLO I (DGR) |  | BRP_PBL1_UNIT1 | MAVERICK | STORAGE | SOUTH | 2020 | 5
965 | BRP PUEBLO II (DGR) |  | BRP_PBL2_UNIT1 | MAVERICK | STORAGE | SOUTH | 2020 | 10
966 | BRP RANCHTOWN (DGR) |  | BRP_RNCH_UNIT1 | BEXAR | STORAGE | SOUTH | 2020 | 10
967 | BRP SEMINOLE (DGR) |  | BRP_SEMI_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2020 | 10
968 | BRP SWEENY (DGR) |  | BRP_SWNY_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2020 | 10
969 | BRP ZAPATA I (DGR) |  | BRP_ZPT1_UNIT1 | ZAPATA | STORAGE | SOUTH | 2020 | 10
970 | BRP ZAPATA II (DGR) |  | BRP_ZPT2_UNIT1 | ZAPATA | STORAGE | SOUTH | 2020 | 5
971 | FLOWER VALLEY BATTERY (DGR) |  | FLVABES1_FLATU1 | REEVES | STORAGE | WEST | 2020 | 9.9
972 | HOEFSROAD BESS (DGR) |  | HRBESS_BESS | REEVES | STORAGE | WEST | 2020 | 2
973 | SWOOSE BATTERY (DGR) |  | SWOOSE1_SWOOSEU1 | WARD | STORAGE | WEST | 2020 | 9.9
974 | TRIPLE BUTTE (DGR) |  | TRIPBUT1_BELU1 | PECOS | STORAGE | WEST | 2021 | 7.5
975 | Planned Capacity Total (Storage) | [6 empty] | 189.6
976 | Storage Peak Average Capacity Percentage |  | STORAGE_PL_PEAK_PCT | % |  |  |  | 0
977
978 | Inactive Planned Resources
979 | HALYARD WHARTON ENERGY CENTER | 16INR0044 |  | WHARTON | GAS-GT | SOUTH | 2021 | 0
980 | CHOCOLATE BAYOU W | 16INR0074 |  | BRAZORIA | WIND-C | COASTAL | 2022 | 0
981 | GOODNIGHT WIND | 14INR0033 |  | ARMSTRONG | WIND-P | PANHANDLE | 2022 | 0
982 | MARIAH DEL ESTE | 13INR0010a |  | PARMER | WIND-P | PANHANDLE | 2020 | 152.5
983 | NORTHDRAW WIND | 13INR0025 |  | RANDALL | WIND-P | PANHANDLE | 2020 | 150
984 | PANHANDLE WIND 3 | 14INR0030c |  | CARSON | WIND-P | PANHANDLE | 2022 | 0
985 | WILDROSE WIND (SWISHER WIND) | 13INR0038 |  | SWISHER | WIND-P | PANHANDLE | 2021 | 0
986 | LOMA PINTA WIND | 16INR0112 |  | LA SALLE | WIND-O | SOUTH | 2021 | 0
987 | AGATE SOLAR | 20INR0023 |  | ELLIS | SOLAR | NORTH | 2020 | 60
988 | SPINEL SOLAR | 20INR0025 |  | MEDINA | SOLAR | SOUTH | 2020 | 30
989 | Inactive Planned Capacity Total | [6 empty] | 392.5
990
991 | Seasonal Mothballed Resources
992 | GREGORY POWER PARTNERS GT1 (AS OF 10/17/2019, AVAILABLE 5/1 THROUGH 9/30) |  | LGE_LGE_GT1 | SAN PATRICIO | GAS-CC | COASTAL | 2000 | 152
993 | GREGORY POWER PARTNERS GT2 (AS OF 10/17/2019, AVAILABLE 5/1 THROUGH 9/30) |  | LGE_LGE_GT2 | SAN PATRICIO | GAS-CC | COASTAL | 2000 | 151
994 | GREGORY POWER PARTNERS STG (AS OF 10/17/2019,AVAILABLE 5/1 THROUGH 9/30) |  | LGE_LGE_STG | SAN PATRICIO | GAS-CC | COASTAL | 2000 | 75
995 | SPENCER STG U4 (AS OF 10/3/2018, AVAILABLE 5/20 THROUGH 10/10) |  | SPNCER_SPNCE_4 | DENTON | GAS-ST | NORTH | 1966 | 57
996 | SPENCER STG U5 (AS OF 10/3/2018, AVAILABLE 5/20 THROUGH 10/10) |  | SPNCER_SPNCE_5 | DENTON | GAS-ST | NORTH | 1973 | 61
997 | NACOGDOCHES POWER (AS OF 10/16/2020, AVAILABLE 5/15 THROUGH 10/15) |  | NACPW_UNIT1 | NACOGDOCHES | BIOMASS | NORTH | 2012 | 105
998 | Total Seasonal Mothballed Capacity | [6 empty] | 601
999
1000 | Mothballed Resources
1001 | J T DEELY U1 (AS OF 12/31/2018) |  | CALAVERS_JTD1_M | BEXAR | COAL | SOUTH | 1977 | 430
1002 | J T DEELY U2 (AS OF 12/31/2018) |  | CALAVERS_JTD2_M | BEXAR | COAL | SOUTH | 1978 | 420
1003 | Total Mothballed Capacity | [6 empty] | 850
1004
1005 | Retiring Resources Unavailable to ERCOT (since last CDR/SARA)
1006 | SAM RAYBURN POWER CTG 1 (RETIRING ON 02/28/2021) |  | RAYBURN_RAYBURG1 | VICTORIA | GAS-GT | SOUTH | 1963 | 13.5
1007 | SAM RAYBURN POWER CTG 2 (RETIRING ON 02/28/2021) |  | RAYBURN_RAYBURG2 | VICTORIA | GAS-GT | SOUTH | 1963 | 13.5
1008 | Total Retiring Capacity | [6 empty] | 27
Notes:
Capacity changes due to planned repower/upgrade projects are reflected in the operational units' ratings upon receipt and ERCOT approval of a new Resource Asset Registration Form (RARF). Interconnection requests for existing resources that involve MW capacity changes are indicated with a code in the “Generation Interconnection Project Code” column.
Although seasonal capacity ratings for battery energy storage systems are reported above, the ratings are not included in the operational/planned capacity formulae. These resources are assumed to provide regulation reserves rather than sustained capacity available to meet system peak loads.
Unit Names with a (DGR) suffix are Distribution Generation Resources. A DGR fully participates in ERCOT's markets, but is connected to the Distribution System and is currently not required to go through the GINR application process.
Note on I391: Units unavailable for season: DG_LKWDT_2UNITS (-2.4 MW) DG_SCHUM_2UNITS (-3.6 MW)

## Background
Release Date: November 5, 2020
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Background
The Seasonal Assessment of Resource Adequacy (SARA) report is a deterministic approach to considering the impact of potential variables that may affect the sufficiency of installed resources to meet the peak electrical demand on the ERCOT System during a particular season.
The standard approach to assessing resource adequacy for one or more years into the future is to account for projected load and resources on a normalized basis and to require sufficient reserves (resources in excess of peak demand, on this normalized basis) to cover the uncertainty in peak demand and resource availability to meet a probabilistic reliability standard.
For seasonal assessments that look ahead less than a year, specific information may be available (such as seasonal climate forecasts or anticipated common-mode events such as drought) which can be used to consider the range of resource adequacy in a more deterministic manner.
The SARA report focuses on the availability of sufficient operating reserves to avoid emergency actions such as deployment of voluntary load reduction resources. It uses an operating reserve threshold of 2,300 MW to indicate the risk that an Energy Emergency Alert Level 1 (EEA1) may be triggered during the time of the forecasted seasonal peak load. This threshold level is intended to be roughly analogous to the 2,300 MW Physical Responsive Capability (PRC) threshold for EEA1. However, PRC is a real-time capability measure for Resources that can quickly respond to system disturbances. In contrast, the SARA operating reserve reflects additional capability assumed to be available before energy emergency procedures are initiated, such as from Resources qualified to provide non-spinning reserves. Additionally, the amount of operating reserves available may increase relative to what is included in the SARA report due to the market responding to wholesale market price increases and anticipated capacity scarcity conditions. Given these considerations, ERCOT believes that the 2,300 MW reserve capacity threshold is a reasonable indicator for the risk of Energy Emergency Alerts given the uncertainties in predicting system conditions months in advance.
The SARA report is intended to illustrate the range of resource adequacy outcomes that might occur. It serves as a situational awareness tool for ERCOT operational planning purposes, and helps fulfill the "extreme weather" resource adequacy assessment requirement per Public Utility Commission of Texas rule 25.362(i)(2)(H). In addition to a base scenario, several other scenarios are developed by varying the value of load forecast and resource availability parameters. The variation in these parameters is based on historic ranges of the parameter values or known changes expected in the near-term. The SARA report is not intended to indicate the likelihood of any of these scenario outcomes.